{"text_format":"2","workbook":"xlsx","n_sheets":47,"sheets":["Main","List","Base","主CPU","从CPU","L201","L101","L202","L102","L203","L103","L204","L104","L205","L105","L206","L106","L207","L107","L208","L108","L301","L401","L508","L302","L402","L509","L303","L403","L507","L304","L404","L510","L305","L503","L504","L306","L406","L501","L601","L307","L407","L502","L308","L408","L505","L506"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":4,"defined_names":131,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Main","index":0,"n_rows":50,"n_cols":4,"rows_kept":50,"cut":false,"hidden":false,"merged":[]}
[]
["日期","版本号","编制记录","编制人"]
[20190721,2,"初始化建立","姚立"]
[20170722,2.1,"增加插入VB控件","姚立"]
[20190723,2.1,"完善设备列表","戚如钢"]
[20190723,2.2,"修正BUG，增加基础变量","姚立"]
[20190723,2.3,"VB编写错误修改","姚立"]
[20190723,2.4,"修正写入BUG","姚立"]
[20190724,2.5,"增加变量修正BUG","姚立"]
[20190808,2.6,"修正显示问题","姚立"]
[20190812,2.7,"修正现场发现的问题","姚立"]
[20190820,2.8,"增加功能，调整错误","姚立"]
[null,null,"增加电源模板"]
[null,null,"增加前端接线自动检索生成公式，并自动附加前缀"]
[null,null,"增加DDC箱体名称"]
[null,null,"调整偏置格式"]
[null,null,"4种点位模块，颜色区分"]
[null,null,"增加页眉页码"]
[null,null,"调整偏置格式"]
[null,null,"检查BASE模板内字体格式，字体大小"]
[20190820,2.9,"修正BUG，增加基础变量","姚立"]
[20190821,2.91,"补充吾悦专用变量","姚立"]
[20190903,2.92,"优化声明生成公式（结构整理）","姚立"]
[20190904,2.93,"修正1601R与0801R的声明表地址错误问题","戚如钢"]
[20190905,2.94,"修正1601R与0801R的声明表地址另一错误问题","戚如钢"]
[20191003,2.95,"加入主CPU/从CPU/OPCDA声明，适配injoydemov2.0","姚立"]
[20191004,2.96,"优化OPCDA区程序声明备注","姚立"]
[20191006,2.97,"优化OPCDA区数据类型地址自动累加方式","姚立"]
[null,null,"增加OPCDA区数据类型整除性验证行"]
[null,null,"增加主CPU/从CPU接收发送对应地址计算"]
[null,null,"增加OPCDA区非直接声明变量自动生成列"]
[20191008,2.98,"增加从CPU接收主CPU心跳数据","姚立"]
[20191009,2.99,"匹配","姚立"]
[20200509,3.1,"增加EXC6000接线表，增加程序中间变量声明，主从CPU修改变量","戴锦豪"]
[20200509,3.11,"增加冷机声明示例，增加EXC61610进入插入脚本","姚立"]
[20200618,3.2,"增加程序中间变量声明，主从CPU修改变量，Bsae结构整理变大","戴锦豪"]
[20210202,3.3,"增加程序中间变量声明，主从CPU修改变量，Bsae结构整理变大","戴锦豪"]
[20210819,3.4,"修复了表格中声明间隙；EXC61610modbus地址调整；其他编写bug调整","潘平"]
[20211203,3.5,"增加EXC-61608-BT模块声明，应用于蓝牙功能，点位变量调整为中间变量，增加赋值公式","潘平"]
[20211217,3.51,"增加EXC-61610-BT模块声明，应用于蓝牙功能，点位变量调整为中间变量，增加赋值公式","潘平"]
[20220507,3.6,"增加CPU及电源模块样例，完善调试信息图","潘平"]
[null,null,"拓展设备点位处数据验证长度"]
[null,null,"增加EXC-61610-BT模块施工段做白处理，减少现场误解"]
[null,null,"增加IOM 0401U E5模块声明"]
[20221202,3.61,"增加EXC-60006模块声明","潘平"]
[20221206,3.62,"修复了表格中EXC6000模块modbus地址错误问题","潘平"]
[20221222,3.63,"增加EXC-61610 C8、EXC-61610 D8模块","潘平"]
[null,null,"调整内容：为模拟量端子增设DC24V电源输出，原向下版本暂不删除，用以过渡项目"]
[20230524,3.64,"增加9键面板模块","戴锦豪"]
[20240812,4,"大改，根据软件部改写变量，中间变量全部加入"]

{"sheet":"List","index":1,"n_rows":295,"n_cols":17,"rows_kept":295,"cut":false,"hidden":false,"merged":[[0,1,0,3],[0,4,0,5],[0,6,0,7],[0,8,0,9],[0,10,0,12],[0,14,0,16],[158,4,158,5],[158,6,158,7],[158,8,158,9]]}
["序号","设备缩写",null,null,"楼层",null,"箱子编号",null,"设备数量",null,"功能名",null,null,null,"接线备注"]
[null,"<空调系统>>",null,null,"地下三层","B3","1#","A",1,"01","<空调功能>",null,null,null,"功能名","端子编号","线色备注"]
[1,"F新风机组","FAU","Fresh air unit","地下二层","B2","2#","B",2,"02","运行状态","R","Run"]
[2,"P新风机组","PAU","术语备选","地下一层","B1","3#","C",3,"03","故障状态","F","Fault"]
[3,"M新风机组","MAU","术语备选","夹层","BM","4#","D",4,"04","自动状态","A","Auto"]
[4,"全热交换机组","HEU","Heat exchange unit","一层","01","5#","E",5,"05","启停控制","C","Control"]
[5,"风机盘管","FCU","Fan Coil Units","二层","02","6#","F",6,"06","变频器运行","VR","VFD run"]
[6,"空调机组","AHU","Air handling unit","三层","03","7#","G",7,"07","变频器故障","VF","VFD fault"]
[null,"<吾悦特殊机组>",null,null,"四层","04","8#","H",8,"08","变频器启停","VC","VFD control"]
[7,"吊顶式空调机组","AHU","Fresh air unit","五层","05","9#","I",9,"09","变频器频率控制","VFC","VFD frequency control"]
[7,"风幕机","AC","air curtain",null,"···",null,"···",null,"···","变频器频率反馈","VFB","VFD frequency feedback"]
[7,"水幕机","WAC","Water air curtain","屋面","RF","26#","Z",null,"99","送风机运行状态","SR","Run"]
[5,"风机盘管电磁阀","FCUV",{"$nulls":7},"送风机故障状态","SF","Fault"]
[null,"遮阳帘","SSC",{"$nulls":7},"送风机自动状态","SA","Auto"]
[{"$nulls":10},"送风机启停控制","SC","Control"]
[{"$nulls":10},"送风机变频器频率控制","SVFC","VFD frequency control"]
[{"$nulls":10},"送风机变频器频率反馈","SVFB","VFD frequency feedback"]
[{"$nulls":10},"排风机运行状态","ER","Run"]
[{"$nulls":10},"排风机故障状态","EF","Fault"]
[{"$nulls":10},"排风机自动状态","EA","Auto"]
[{"$nulls":10},"排风机启停控制","EC","Control"]
[{"$nulls":10},"排风机变频器频率控制","EVFC","VFD frequency control"]
[{"$nulls":10},"排风机变频器频率反馈","EVFB","VFD frequency feedback"]
[{"$nulls":10},"风机压差","FPS","Fan Differential Pressure Switch"]
[{"$nulls":10},"初效滤网压差","IPS","initial effect Differential Pressure Switch"]
[{"$nulls":10},"中效滤网压差","MPS","Medium effect Differential Pressure Switch"]
[{"$nulls":10},"高效滤网压差","HPS","High effect Differential Pressure Switch"]
[{"$nulls":10},"低温断路开关","AFS","Antifreeze switch"]
[{"$nulls":10},"送风温度","ST","Supply air Temperature"]
[{"$nulls":10},"回风温度","RT","Return air Temperature"]
[{"$nulls":10},"排风温度","ET","Exhaust air Temperature"]
[{"$nulls":10},"新风温度","FT","Fresh air Temperature"]
[{"$nulls":10},"送风湿度","SH","Supply air Humidity"]
[{"$nulls":10},"回风湿度","RH","Return air Humidity"]
[{"$nulls":10},"排风湿度","EH","Exhaust air Humidity"]
[{"$nulls":10},"新风湿度","FH","Fresh air Humidity"]
[{"$nulls":10},"送风压力","SP","Supply pressure"]
[{"$nulls":10},"送风风速","SWS","Supply wind speed"]
[{"$nulls":10},"回风二氧化碳","RCO2","Return CO2"]
[{"$nulls":10},"露点温度","DPT","Dew point temperature"]
[{"$nulls":10},"送风阀开状态","SDOB","Supply air Damper open feedback"]
[{"$nulls":10},"送风阀关状态","SDSB","Supply air Damper shut feedback"]
[{"$nulls":10},"送风阀开控制","SDOC","Supply air Damper open control"]
[{"$nulls":10},"送风阀关控制","SDSC","Supply air Damper shut control"]
[{"$nulls":10},"回风阀开状态","RDOB","Return air Damper open feedback"]
[{"$nulls":10},"回风阀关状态","RDSB","Return air Damper shut feedback"]
[{"$nulls":10},"回风阀开控制","RDOC","Return air Damper open control"]
[{"$nulls":10},"回风阀关控制","RDSC","Return air Damper shut control"]
[{"$nulls":10},"排风阀开状态","EDOB","Exhaust air Damper open feedback"]
[{"$nulls":10},"排风阀关状态","EDSB","Exhaust air Damper shut feedback"]
[{"$nulls":10},"排风阀开控制","EDOC","Exhaust air Damper open control"]
[{"$nulls":10},"排风阀关控制","EDSC","Exhaust air Damper shut control"]
[{"$nulls":10},"新风阀开状态","FDOB","Fresh air Damper open feedback"]
[{"$nulls":10},"新风阀关状态","FDSB","Fresh air Damper shut feedback"]
[{"$nulls":10},"新风阀开控制","FDOC","Fresh air Damper open control"]
[{"$nulls":10},"新风阀关控制","FDSC","Fresh air Damper shut control"]
[{"$nulls":10},"送风阀控制","SDC","Supply air Damper regulation control"]
[{"$nulls":10},"送风阀反馈","SDB","Supply air Damper regulation feedback"]
[{"$nulls":10},"回风阀控制","RDC","Return air Damper regulation control"]
[{"$nulls":10},"回风阀反馈","RDB","Return air Damper regulation feedback"]
[{"$nulls":10},"排风阀控制","EDC","Exhaust air Damper regulation control"]
[{"$nulls":10},"排风阀反馈","EDB","Exhaust air Damper regulation feedback"]
[{"$nulls":10},"新风阀控制","FDC","Fresh air Damper regulation control"]
[{"$nulls":10},"新风阀反馈","FDB","Fresh air Damper regulation feedback"]
[{"$nulls":10},"加湿器开反馈","HFOB","Humidifier open feedback"]
[{"$nulls":10},"加湿器关反馈","HFSB","Humidifier shut feedback"]
[{"$nulls":10},"加湿器开控制","HFOC","Humidifier open control"]
[{"$nulls":10},"加湿器关控制","HFSC","Humidifier shut control"]
[{"$nulls":10},"加湿器控制","HFC","Humidifier control"]
[{"$nulls":10},"加湿器反馈","HFB","Humidifier Feedback"]
[{"$nulls":10},"水阀控制","WVC","Water Valve control"]
[{"$nulls":10},"水阀反馈","WVB","Water Valve Feedback"]
[{"$nulls":10},"水阀开反馈","WVOB","Water Valve open Feedback"]
[{"$nulls":10},"水阀关反馈","WVSB","Water Valve shut Feedback"]
[{"$nulls":10},"水阀开控制","WVOC","Water Valve open control"]
[{"$nulls":10},"水阀关控制","WVSC","Water Valve shut control"]
[{"$nulls":10},"<吾悦特殊功能>"]
[{"$nulls":10},"电磁阀开启状态","EVR","Electromagnetic valve run"]
[{"$nulls":10},"电磁阀自动状态","EVA","Electromagnetic valve auto"]
[{"$nulls":10},"电磁阀开关控制","EVC","Electromagnetic valve control"]
[null,"<送排风系统>>",{"$nulls":8},"<送排风功能>"]
[1,"送风机","SAF","Supply fan",{"$nulls":6},"运行状态","R","Run"]
[2,"排风机","EAF","Air exhaust fan",{"$nulls":6},"故障状态","F","Fault"]
[3,"排烟机","ESF","Somke exhaust fan",{"$nulls":6},"自动状态","A","Auto"]
[4,"双速风机","EMF","Multipurpose exhaust fan",{"$nulls":6},"启停控制","C","Control"]
[null,"<给排水系统>",{"$nulls":8},"<给排水功能>"]
[1,"潜污泵井","SWP","Submersible sewage pump/sump ",{"$nulls":6},"泵1运行状态","R1"]
[2,"生活水泵","LWP","Life Water pump",{"$nulls":6},"泵1故障状态","F1"]
[3,"消防水泵","FWP","Fire water pump",{"$nulls":6},"泵1启停控制","C1"]
[4,"生活水箱","LWT","Life water tank",{"$nulls":6},"泵2运行状态","R2"]
[5,"消防水箱","FWT","Fire water tank",{"$nulls":6},"泵2故障状态","F2"]
[6,"其它水箱","OWT","Other water tank",{"$nulls":6},"泵2启停控制","C2"]
[7,"隔油池","OST","oil separator",{"$nulls":6},"泵3运行状态","R3"]
[8,"污水提升","SST","Sewage lifting",{"$nulls":6},"泵3故障状态","F3"]
[9,"膨胀水箱","EWT","Swell water tank",{"$nulls":6},"泵3启停控制","C3"]
[10,"生活水系统","DWS","domestic water system",{"$nulls":6},"超高液位","SHL","Super high level"]
[{"$nulls":10},"高液位","HL","High level"]
[{"$nulls":10},"低液位","LL","Low level"]
[{"$nulls":10},"超低液位","SLL","Super low level"]
[{"$nulls":10},"液位高度","LLH","Liquid level height"]
[null,"<电梯系统>",{"$nulls":8},"<电梯功能>"]
[1,"扶梯","LET","level Escalator",{"$nulls":6},"上行状态","US","Upward state"]
[2,"垂直电梯","VET","Vertical elevator",{"$nulls":6},"下行状态","DS","Downward state"]
[{"$nulls":10},"楼层","FL"]
[{"$nulls":10},"运行状态","R"]
[{"$nulls":10},"故障状态","F"]
[{"$nulls":10},"门状态","DR","DOOR"]
[null,"<环境监测系统>",{"$nulls":8},"<环境功能>"]
[1,"室内环境状态","IES","Indoor environmental state",{"$nulls":6},"照度状态","I","Illumination"]
[2,"室外环境状态","OES","Outdoor environmental state",{"$nulls":6},"温度状态","T","Temperature"]
[{"$nulls":10},"湿度状态","H","Humidity"]
[{"$nulls":10},"露点温度","DPT","Dew point temperature"]
[{"$nulls":10},"静压状态","SPT","Static Pressure Transducer"]
[{"$nulls":10},"一氧化碳浓度状态","CO"]
[{"$nulls":10},"二氧化碳浓度状态","CO2"]
[{"$nulls":10},"甲烷浓度状态","CH4"]
[{"$nulls":10},"氧气浓度状态","O2"]
[{"$nulls":10},"氨气浓度状态","NH4"]
[{"$nulls":10},"可吸入颗粒物2.5状态","PM25","ug/m3"]
[{"$nulls":10},"可吸入颗粒物10状态","PM10","ug/m3"]
[{"$nulls":10},"可挥发气体状态","VOC","ug/m3"]
[{"$nulls":10},"可吸入颗粒物1状态","PM1","ug/m3"]
[{"$nulls":10},"甲醛浓度状态","CH2O","ug/m3"]
[null,"<冷热源系统>",{"$nulls":8},"<冷热源功能>"]
[1,"冷水机组","CHR","CHILLER",{"$nulls":6},"运行状态","R","Run"]
[2,"风冷热泵机组","ACHP","Air-cooled heat pump",{"$nulls":6},"故障状态","F","Fault"]
[3,"水源热泵机组","CHR","按冷机缩写命名",{"$nulls":6},"自动状态","A","Auto"]
[4,"地源热泵机组","CHR","按冷机缩写命名",{"$nulls":6},"启停控制","C","Control"]
[5,"冷冻水泵","CHP","Chilled water pump",{"$nulls":6},"变频器频率控制","VFC","VFD frequency control"]
[6,"冷却水泵","CLP","Cooling water pump",{"$nulls":6},"变频器频率反馈","VFB","VFD frequency feedback"]
[7,"冷却塔","CLT","Cooling water tower",{"$nulls":6},"水流开关","FS","Flow switch"]
[8,"蝶阀","BFV","Butterfly valve",{"$nulls":6},"供水温度","ST","Supply water temperature"]
[9,"旁通阀","BPV","Bypass valve",{"$nulls":6},"回水温度","RT","Return water temperature"]
[10,"冷冻水回路","CHS","Chilled water system",{"$nulls":6},"供水压力","SP","Supply water Pressure"]
[11,"冷却水回路","CLS","Cooling water system",{"$nulls":6},"回水压力","RP","Return water Pressure"]
[12,"一次侧热水回路","PHS","Primary hot water system",{"$nulls":6},"供水流量","SF","Supply water flow"]
[13,"二次侧热水回路","SHS","Secondary hot water system",{"$nulls":6},"回水流量","RF","Return water flow"]
[14,"锅炉","BLR","Boiler",{"$nulls":6},"水阀控制","WVC","Water Valve control"]
[15,"热水循环泵","BFP","Boiler feed water pump",{"$nulls":6},"水阀反馈","WVB","Water Valve Feedback"]
[16,"板式换热器","HEX","Heat exchanger",{"$nulls":6},"供水阀开状态","SOB"]
[17,"补水泵","RWP","Replenishing water pump",{"$nulls":6},"供水阀关状态","SSB"]
[18,"分集水器","D","distributor",{"$nulls":6},"回水阀开状态","ROB"]
[{"$nulls":10},"回水阀关状态","RSB"]
[{"$nulls":10},"供水阀开控制","SOC"]
[{"$nulls":10},"供水阀关控制","SSC"]
[{"$nulls":10},"回水阀开控制","ROC"]
[{"$nulls":10},"回水阀关控制","RSC"]
[{"$nulls":10},"<冷却塔功能>"]
[{"$nulls":10},"高速运行状态","R1"]
[{"$nulls":10},"高速故障状态","F1"]
[{"$nulls":10},"高速启停控制","C1"]
[{"$nulls":10},"低速运行状态","R2"]
[{"$nulls":10},"低速故障状态","F2"]
[{"$nulls":10},"低速启停控制","C2"]
[{"$nulls":10},"<锅炉功能>"]
[{"$nulls":10},"大火","HF","High fire"]
[{"$nulls":10},"中火","MF","Middle fire"]
[{"$nulls":10},"小火","LF","Low fire"]
[null,"<照明系统>",null,null,"楼层",null,"箱子编号",null,"回路数量",null,"<照明功能>"]
[1,"照明控制箱","LCB","Lighting control box","地下三层","B3","1#","A",1,"01","回路开关","C","Control"]
[2,"照明调光箱","LDB","Lighting dimming zone","地下二层","B2","2#","B",2,"02","场景反馈","SF","Scene feedback"]
[3,"照明面板","LCP","Smart lighting panel","地下一层","B1","3#","C",3,"03","场景控制","SC","Scene Control"]
[{"$nulls":4},"夹层","BM","4#","D",4,"04","电流检测值","CD","Current detection"]
[{"$nulls":4},"一层","01","5#","E",5,"05","人体感应开关","MIS","Mobile induction switch"]
[{"$nulls":4},"二层","02","6#","F",6,"06","照度","I","illumination"]
[{"$nulls":5},"···",null,"···",null,"···","回路调节","D","Dimming"]
[{"$nulls":4},"屋面","RF","26#","Z",99,"99"]
[{"$nulls":6},"27#","1"]
[{"$nulls":6},"28#","2"]
[{"$nulls":7},"···"]
[{"$nulls":6},"35#","9"]
[null,"<能耗系统>",{"$nulls":8},"<电表>"]
[1,"电表","EM","electricity meter",{"$nulls":6},"用户电能","AE"]
[2,"水表","WM","water meter",{"$nulls":6},"A相电压","UA"]
[3,"预付费电表","PEM","Prepaid electricity meter",{"$nulls":6},"B相电压","UB"]
[4,"预付费水表","PWM","Prepaid water meter",{"$nulls":6},"C相电压","UC"]
[5,"热表","HM","heat meter",{"$nulls":6},"AB相电压","UAB"]
[{"$nulls":10},"BC相电压","UBC"]
[{"$nulls":10},"CA相电压","UCA"]
[{"$nulls":10},"A相电流","IA"]
[{"$nulls":10},"B相电流","IB"]
[{"$nulls":10},"C相电流","IC"]
[{"$nulls":10},"总有功功率","AP"]
[{"$nulls":10},"预付费电表继电器控制","RC"]
[{"$nulls":10},"仪表清零","MC"]
[{"$nulls":10},"<水表>"]
[{"$nulls":10},"用水总量","TWC"]
[{"$nulls":10},"阀门状态","VS"]
[{"$nulls":10},"阀门开关控制","VS"]
[null,"<系统基础>>",{"$nulls":8},"<中间变量>>"]
[1,"控制箱","BOX",{"$nulls":7},"模块地址状态","DS","Device Status"]
[2,"控制器","DEV","Device",{"$nulls":6},"模块在线比例","OR","Online Ratio"]
[3,"AI通道","Device",{"$nulls":7},"硬件总点位","THB","Total hardware bit"]
[4,"命令","CMD",{"$nulls":7},"设定温度值","TSET","Temperature Set"]
[5,"高压综合主开关柜","HVM","High voltage main switchgear",{"$nulls":6},"季节模式","SM","Season Mode"]
[6,"高压综合备开关柜","HVS","High voltage standby switchgear",{"$nulls":6},"水阀反馈换算值","WVBS","Water Vavle Feedback Switch"]
[7,"低压综合主配电柜","LVM","Low voltage main switchgear",{"$nulls":6},"水阀手动控制","WVMC","Water Vavle Manual Control"]
[8,"低压综合备配电柜","LVS","Low voltage standby switchgear",{"$nulls":6},"水阀手动控制值","WVMV","Water Vavle Manual Value"]
[null,"系统","SYS",{"$nulls":7},"回风温度换算值","RTS","Return Temperature Switch"]
[{"$nulls":10},"运行时间累积重置","RST","Runtime Reset"]
[{"$nulls":10},"运行时间累积重置值","RSTV","Runtime Reset Value"]
[{"$nulls":10},"运行时间累积值","RH","Runtime Hour"]
[{"$nulls":10},"隔离开关1","ISO1","Isolation Switch1"]
[{"$nulls":10},"隔离开关2","ISO2","Isolation Switch2"]
[{"$nulls":10},"隔离开关3","ISO3","Isolation Switch3"]
[{"$nulls":10},"P调节参数","VP","Value Proportion "]
[{"$nulls":10},"I调节参数","VI","Value Integration"]
[{"$nulls":10},"设备状态代码","SN","Status Number"]
[{"$nulls":10},"水阀控制转换值","WVCS","Water Vavle Control Switch"]
[{"$nulls":10},"室内温度转换值","TS","Temperature Switch"]
[{"$nulls":10},"程序控制","PC","Program Control"]
[{"$nulls":10},"新云模式","CM"]
[{"$nulls":10},"运行模式","RM"]
[{"$nulls":10},"温度换算值","TS","Temperature Switch"]
[{"$nulls":10},"电磁阀手动控制","EVMC"]
[{"$nulls":10},"电磁阀手动控制值","EVMV"]
[{"$nulls":10},"心跳值","DHV","Device Heart Vavle"]
[{"$nulls":10},"照度状态换算值","IS","Illumination Switch"]
[{"$nulls":10},"温度状态换算值","TS","Temperature Switch"]
[{"$nulls":10},"湿度状态换算值","HS","Humidity Switch"]
[{"$nulls":10},"定时控制","TC"]
[{"$nulls":10},"定时模式","TM"]
[{"$nulls":10},"心跳值返回","DHR"]
[{"$nulls":10},"送风温度换算值","STS"]
[{"$nulls":10},"变频手动控制值","VFMV"]
[{"$nulls":10},"低温断路报警隔离","ISO3"]
[{"$nulls":10},"变频器频率控制值","VFCS"]
[{"$nulls":10},"变频器频率反馈值","VFBS"]
[{"$nulls":10},"联动模式","LM"]
[{"$nulls":10},"定时控制","TC"]
[{"$nulls":10},"定时模式","TM"]
[{"$nulls":10},"全天候模式","DM"]
[{"$nulls":10},"CO2设定值","CO2SET"]
[{"$nulls":10},"CO设定值","COSET"]
[{"$nulls":10},"CO2换算值","CO2S"]
[{"$nulls":10},"CO换算值","COS"]
[{"$nulls":10},"烟雾浓度状态","SR"]
[{"$nulls":10},"AI1配置","MO1"]
[{"$nulls":10},"AI2配置","MO2"]
[{"$nulls":10},"AI3配置","MO3"]
[{"$nulls":10},"AI4配置","MO4"]
[{"$nulls":10},"AI5配置","MO5"]
[{"$nulls":10},"AI6配置","MO6"]
[{"$nulls":10},"控制模式","CM","Control mode"]
[{"$nulls":10},"使能输入","CI","Control Input"]
[{"$nulls":10},"冷冻出水温度设定","TSET","evaporimeter; Set"]
[{"$nulls":10},"工况模式","RM","Running Mode"]
[{"$nulls":10},"蒸发器进水温度","CHRT","冷冻Evaporimeter Return Water Temperature"]
[{"$nulls":10},"蒸发器出水温度","CHST","冷冻Evaporimeter Supply Water Temperature"]
[{"$nulls":10},"冷凝器进水温度","CLRT","冷却Condenser Return Water Temperature"]
[{"$nulls":10},"冷凝器出水温度","CLST","冷却Condenser Supply Water Temperature"]
[{"$nulls":10},"压缩机出水温度","CPST","Compressor Supply Water Temperature"]
[{"$nulls":10},"压缩机吸气温度","CPRT","Compressor Return Air Temperature"]
[{"$nulls":10},"压缩机排气温度","CPET","Compressor Exhaust Air Temperature"]
[{"$nulls":10},"蒸发器饱和温度","EST","Evaporimeter Saturation Temperature"]
[{"$nulls":10},"蒸发器蒸发压力","EP","Evaporimeter Pressure"]
[{"$nulls":10},"蒸发器水流量","EF","Evaporimeter Flow"]
[{"$nulls":10},"冷凝器饱和温度","CST","Condenser Saturation Temperature"]
[{"$nulls":10},"冷凝器压力","CP","Condenser Pressure"]
[{"$nulls":10},"冷凝器水流量","CF","Condenser Flow"]
[{"$nulls":10},"电流百分比","AC","Current Per"]
[{"$nulls":10},"油槽压力","OGP","Oil Groove Pressure"]
[{"$nulls":10},"油槽温度","OGT","Oil Groove Temperature"]
[{"$nulls":10},"压缩机启动次数","CRN","Compressor RunNum"]
[{"$nulls":10},"压缩机运行时间","CPRH","Compressor Runtime"]
[{"$nulls":10},"蒸发器运行时间","ERH","Evaporimeter Runtime"]
[{"$nulls":10},"冷凝器运行时间","CRH","Condenser Runtime"]
[{"$nulls":10},"工作日开启小时","WOH"]
[{"$nulls":10},"工作日开启分钟","WOM"]
[{"$nulls":10},"工作日关闭小时","WCH"]
[{"$nulls":10},"工作日关闭分钟","WCM"]
[{"$nulls":10},"节假日开启小时","HOH"]
[{"$nulls":10},"节假日开启分钟","HOM"]
[{"$nulls":10},"节假日关闭小时","HCH"]
[{"$nulls":10},"节假日关闭分钟","HCM"]
[{"$nulls":10},"运行时间累积重置1","RST1","Runtime Reset"]
[{"$nulls":10},"运行时间累积重置值1","RSTV1","Runtime Reset Value"]
[{"$nulls":10},"运行时间累积值1","RH1","Runtime Hour"]
[{"$nulls":10},"运行时间累积重置2","RST2","Runtime Reset"]
[{"$nulls":10},"运行时间累积重置值2","RSTV2","Runtime Reset Value"]
[{"$nulls":10},"运行时间累积值2","RH2","Runtime Hour"]
[{"$nulls":10},"运行时间累积重置3","RST3","Runtime Reset"]
[{"$nulls":10},"运行时间累积重置值3","RSTV3","Runtime Reset Value"]
[{"$nulls":10},"运行时间累积值3","RH3","Runtime Hour"]
[{"$nulls":10},"风阀联动模式","FM"]
[{"$nulls":10},"回风阀控制换算值","RDCS"]
[{"$nulls":10},"回风阀反馈换算值","RDBS"]
[{"$nulls":10},"新风阀控制换算值","FDCS"]
[{"$nulls":10},"新风阀反馈换算值","FDBS"]
[{"$nulls":10},"回风阀手动控制值","RDMV"]
[{"$nulls":10},"新风阀手动控制值","FDMV"]
[{"$nulls":10},"闪存写入次数","WriteNum"]
[{"$nulls":10},"闪存写入成功标记","Write_Flag"]
[{"$nulls":10},"闪存读取成功标记","Read_Flag"]
[{"$nulls":10},"变化判断变量","Judge_Num"]

{"sheet":"Base","index":2,"n_rows":508,"n_cols":45,"rows_kept":508,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,2,4,4],[4,27,4,28],[6,1,6,25],[7,1,7,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[41,5,41,6],[41,9,41,25],[42,5,42,6],[42,9,42,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[75,5,75,6],[75,9,75,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[84,5,84,6],[84,9,84,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[88,9,88,25],[89,9,89,25],[90,9,90,25],[91,9,91,25],[92,9,92,25],[93,9,93,25],[94,9,94,25],[95,9,95,25],[96,9,96,25],[97,9,97,25],[99,9,99,25],[100,9,100,25],[101,9,101,25],[102,9,102,25],[103,9,103,25],[104,9,104,25],[105,9,105,25],[106,9,106,25],[107,9,107,25],[108,9,108,25],[110,5,110,6],[110,9,110,25],[111,5,111,6],[111,9,111,25],[112,5,112,6],[112,9,112,25],[113,5,113,6],[113,9,113,25],[114,5,114,6],[114,9,114,25],[115,5,115,6],[115,9,115,25],[116,5,116,6],[116,9,116,25],[117,5,117,6],[117,9,117,25],[118,5,118,6],[118,9,118,25],[119,5,119,6],[119,9,119,25],[120,5,120,6],[120,9,120,25],[121,5,121,6],[121,9,121,25],[122,5,122,6],[122,9,122,25],[123,5,123,6],[123,9,123,25],[124,5,124,6],[124,9,124,25],[125,5,125,6],[125,9,125,25],[126,5,126,6],[126,9,126,25],[127,5,127,6],[127,9,127,25],[128,5,128,6],[128,9,128,25],[129,5,129,6],[129,9,129,25],[130,5,130,6],[130,9,130,25],[131,5,131,6],[131,9,131,25],[132,5,132,6],[132,9,132,25],[133,5,133,6],[133,9,133,25],[134,5,134,6],[134,9,134,25],[135,5,135,6],[135,9,135,25],[136,5,136,6],[136,9,136,25],[137,5,137,6],[137,9,137,25],[138,5,138,6],[138,9,138,25],[139,5,139,6],[139,9,139,25],[140,5,140,6],[140,9,140,25],[141,5,141,6],[141,9,141,25],[142,5,142,6],[142,9,142,25],[143,5,143,6],[143,9,143,25],[145,5,145,6],[145,9,145,25],[146,5,146,6],[146,9,146,25],[147,5,147,6],[147,9,147,25],[148,5,148,6],[148,9,148,25],[149,5,149,6],[149,9,149,25],[150,5,150,6],[150,9,150,25],[151,5,151,6],[151,9,151,25],[152,5,152,6],[152,9,152,25],[153,5,153,6],[153,9,153,25],[154,5,154,6],[154,9,154,25],[155,5,155,6],[155,9,155,25],[156,5,156,6],[156,9,156,25],[157,5,157,6],[157,9,157,25],[158,5,158,6],[158,9,158,25],[159,5,159,6],[159,9,159,25],[160,5,160,6],[160,9,160,25],[161,5,161,6],[161,9,161,25],[162,5,162,6],[162,9,162,25],[163,5,163,6],[163,9,163,25],[164,5,164,6],[164,9,164,25],[165,5,165,6],[165,9,165,25],[166,5,166,6],[166,9,166,25],[167,5,167,6],[167,9,167,25],[168,5,168,6],[168,9,168,25],[169,5,169,6],[169,9,169,25],[170,5,170,6],[170,9,170,25],[171,5,171,6],[171,9,171,25],[172,5,172,6],[172,9,172,25],[173,5,173,6],[173,9,173,25],[174,5,174,6],[174,9,174,25],[175,5,175,6],[175,9,175,25],[176,5,176,6],[176,9,176,25],[177,5,177,6],[177,9,177,25],[178,5,178,6],[178,9,178,25],[180,5,180,6],[180,9,180,25],[181,5,181,6],[181,9,181,25],[182,5,182,6],[182,9,182,25],[183,5,183,6],[183,9,183,25],[184,5,184,6],[184,9,184,25],[185,5,185,6],[185,9,185,25],[186,5,186,6],[186,9,186,25],[187,5,187,6],[187,9,187,25],[188,5,188,6],[188,9,188,25],[189,5,189,6],[189,9,189,25],[190,5,190,6],[190,9,190,25],[191,5,191,6],[191,9,191,25],[192,5,192,6],[192,9,192,25],[193,5,193,6],[193,9,193,25],[194,5,194,6],[194,9,194,25],[195,5,195,6],[195,9,195,25],[196,5,196,6],[196,9,196,25],[197,5,197,6],[197,9,197,25],[198,5,198,6],[198,9,198,25],[199,5,199,6],[199,9,199,25],[200,5,200,6],[200,9,200,25],[201,5,201,6],[201,9,201,25],[202,5,202,6],[202,9,202,25],[203,5,203,6],[203,9,203,25],[204,5,204,6],[204,9,204,25],[205,5,205,6],[205,9,205,25],[206,5,206,6],[206,9,206,25],[207,5,207,6],[207,9,207,25],[208,5,208,6],[208,9,208,25],[210,5,210,6],[210,9,210,25],[211,5,211,6],[211,9,211,25],[212,5,212,6],[212,9,212,25],[213,5,213,6],[213,9,213,25],[214,5,214,6],[214,9,214,25],[215,5,215,6],[215,9,215,25],[216,5,216,6],[216,9,216,25],[217,5,217,6],[217,9,217,25],[218,5,218,6],[218,9,218,25],[219,5,219,6],[219,9,219,25],[220,5,220,6],[220,9,220,25],[221,5,221,6],[221,9,221,25],[222,5,222,6],[222,9,222,25],[223,5,223,6],[223,9,223,25],[224,5,224,6],[224,9,224,25],[225,5,225,6],[225,9,225,25],[226,5,226,6],[226,9,226,25],[227,5,227,6],[227,9,227,25],[228,5,228,6],[228,9,228,25],[229,5,229,6],[229,9,229,25],[230,5,230,6],[230,9,230,25],[231,5,231,6],[231,9,231,25],[232,5,232,6],[232,9,232,25],[233,5,233,6],[233,9,233,25],[234,5,234,6],[234,9,234,25],[235,5,235,6],[235,9,235,25],[236,5,236,6],[236,9,236,25],[237,5,237,6],[237,9,237,25],[238,5,238,6],[238,9,238,25],[240,5,240,6],[240,9,240,25],[241,5,241,6],[241,9,241,25],[242,5,242,6],[242,9,242,25],[243,5,243,6],[243,9,243,25],[244,5,244,6],[244,9,244,25],[245,5,245,6],[245,9,245,25],[247,5,247,6],[247,9,247,25],[248,5,248,6],[248,9,248,25],[249,5,249,6],[249,9,249,25],[250,5,250,6],[250,9,250,25],[252,5,252,6],[252,9,252,25],[253,5,253,6],[253,9,253,25],[254,5,254,6],[254,9,254,25],[255,5,255,6],[255,9,255,25],[256,5,256,6],[256,9,256,25],[257,5,257,6],[257,9,257,25],[258,5,258,6],[258,9,258,25],[259,5,259,6],[259,9,259,25],[261,5,261,6],[261,9,261,25],[262,5,262,6],[262,9,262,25],[263,5,263,6],[263,9,263,25],[264,5,264,6],[264,9,264,25],[265,5,265,6],[265,9,265,25],[266,5,266,6],[266,9,266,25],[267,5,267,6],[267,9,267,25],[268,5,268,6],[268,9,268,25],[269,5,269,6],[269,9,269,25],[270,5,270,6],[270,9,270,25],[271,5,271,6],[271,9,271,25],[272,5,272,6],[272,9,272,25],[274,5,274,6],[274,9,274,25],[275,5,275,6],[275,9,275,25],[276,5,276,6],[276,9,276,25],[277,5,277,6],[277,9,277,25],[278,5,278,6],[278,9,278,25],[279,5,279,6],[279,9,279,25],[280,5,280,6],[280,9,280,25],[282,9,282,25],[283,9,283,25],[284,9,284,25],[285,9,285,25],[286,9,286,25],[287,9,287,25],[289,9,289,25],[290,9,290,25],[291,9,291,25],[292,9,292,25],[293,9,293,25],[294,9,294,25],[295,9,295,25],[296,9,296,25],[297,9,297,25],[299,9,299,25],[300,9,300,25],[301,9,301,25],[302,9,302,25],[303,9,303,25],[304,9,304,25],[305,9,305,25],[306,9,306,25],[307,9,307,25],[309,2,309,5],[309,6,309,8],[309,9,309,25],[310,2,310,5],[310,6,310,8],[310,9,310,25],[311,2,311,5],[311,6,311,8],[311,9,311,25],[312,2,312,5],[312,6,312,8],[312,9,312,25],[313,2,313,5],[313,6,313,8],[313,9,313,25],[314,2,314,5],[314,6,314,8],[314,9,314,25],[315,2,315,5],[315,6,315,8],[315,9,315,25],[316,2,316,5],[316,6,316,8],[316,9,316,25],[317,2,317,5],[317,6,317,8],[317,9,317,25],[318,2,318,5],[318,6,318,8],[318,9,318,25],[319,2,319,5],[319,6,319,8],[319,9,319,25],[321,2,321,5],[321,6,321,8],[321,9,321,25],[322,2,322,5],[322,6,322,8],[322,9,322,25],[323,2,323,5],[323,6,323,8],[323,9,323,25],[324,2,324,5],[324,6,324,8],[324,9,324,25],[325,2,325,5],[325,6,325,8],[325,9,325,25],[326,2,326,5],[326,6,326,8],[326,9,326,25],[327,2,327,5],[327,6,327,8],[327,9,327,25],[328,2,328,5],[328,6,328,8],[328,9,328,25],[329,2,329,5],[329,6,329,8],[329,9,329,25],[330,2,330,5],[330,6,330,8],[330,9,330,25],[331,2,331,5],[331,6,331,8],[331,9,331,25],[332,2,332,5],[332,6,332,8],[332,9,332,25],[333,2,333,5],[333,6,333,8],[333,9,333,25],[334,2,334,5],[334,6,334,8],[334,9,334,25],[335,2,335,5],[335,6,335,8],[335,9,335,25],[336,2,336,5],[336,6,336,8],[336,9,336,25],[337,2,337,5],[337,6,337,8],[337,9,337,25],[338,2,338,5],[338,6,338,8],[338,9,338,25],[339,2,339,5],[339,6,339,8],[339,9,339,25],[340,2,340,5],[340,6,340,8],[340,9,340,25],[341,2,341,5],[341,6,341,8],[341,9,341,25],[342,2,342,5],[342,6,342,8],[342,9,342,25],[343,2,343,5],[343,6,343,8],[343,9,343,25],[344,2,344,5],[344,6,344,8],[344,9,344,25],[345,2,345,5],[345,6,345,8],[345,9,345,25],[346,2,346,5],[346,6,346,8],[346,9,346,25],[347,2,347,5],[347,6,347,8],[347,9,347,25],[348,2,348,5],[348,6,348,8],[348,9,348,25],[349,2,349,5],[349,6,349,8],[349,9,349,25],[351,2,351,5],[351,6,351,8],[351,9,351,25],[352,2,352,5],[352,6,352,8],[352,9,352,25],[353,2,353,5],[353,6,353,8],[353,9,353,25],[354,2,354,5],[354,6,354,8],[354,9,354,25],[355,2,355,5],[355,6,355,8],[355,9,355,25],[356,2,356,5],[356,6,356,8],[356,9,356,25],[357,2,357,5],[357,6,357,8],[357,9,357,25],[358,2,358,5],[358,6,358,8],[358,9,358,25],[359,2,359,5],[359,6,359,8],[359,9,359,25],[360,2,360,5],[360,6,360,8],[360,9,360,25],[361,2,361,5],[361,6,361,8],[361,9,361,25],[362,2,362,5],[362,6,362,8],[362,9,362,25],[363,2,363,5],[363,6,363,8],[363,9,363,25],[364,2,364,5],[364,6,364,8],[364,9,364,25],[365,2,365,5],[365,6,365,8],[365,9,365,25],[366,2,366,5],[366,6,366,8],[366,9,366,25],[367,2,367,5],[367,6,367,8],[367,9,367,25],[368,2,368,5],[368,6,368,8],[368,9,368,25],[369,2,369,5],[369,6,369,8],[369,9,369,25],[370,2,370,5],[370,6,370,8],[370,9,370,25],[371,2,371,5],[371,6,371,8],[371,9,371,25],[372,2,372,5],[372,6,372,8],[372,9,372,25],[373,2,373,5],[373,6,373,8],[373,9,373,25],[374,2,374,5],[374,6,374,8],[374,9,374,25],[376,2,376,5],[376,6,376,8],[376,9,376,25],[377,2,377,5],[377,6,377,8],[377,9,377,25],[378,2,378,5],[378,6,378,8],[378,9,378,25],[379,2,379,5],[379,6,379,8],[379,9,379,25],[380,2,380,5],[380,6,380,8],[380,9,380,25],[381,2,381,5],[381,6,381,8],[381,9,381,25],[382,2,382,5],[382,6,382,8],[382,9,382,25],[383,2,383,5],[383,6,383,8],[383,9,383,25],[384,2,384,5],[384,6,384,8],[384,9,384,25],[385,2,385,5],[385,6,385,8],[385,9,385,25],[386,2,386,5],[386,6,386,8],[386,9,386,25],[387,2,387,5],[387,6,387,8],[387,9,387,25],[388,2,388,5],[388,6,388,8],[388,9,388,25],[389,2,389,5],[389,6,389,8],[389,9,389,25],[390,2,390,5],[390,6,390,8],[390,9,390,25],[391,2,391,5],[391,6,391,8],[391,9,391,25],[392,2,392,5],[392,6,392,8],[392,9,392,25],[393,2,393,5],[393,6,393,8],[393,9,393,25],[394,2,394,5],[394,6,394,8],[394,9,394,25],[395,2,395,5],[395,6,395,8],[395,9,395,25],[396,2,396,5],[396,6,396,8],[396,9,396,25],[397,2,397,5],[397,6,397,8],[397,9,397,25],[398,2,398,5],[398,6,398,8],[398,9,398,25],[399,2,399,5],[399,6,399,8],[399,9,399,25],[400,2,400,5],[400,6,400,8],[400,9,400,25],[401,2,401,5],[401,6,401,8],[401,9,401,25],[402,2,402,5],[402,6,402,8],[402,9,402,25],[403,2,403,5],[403,6,403,8],[403,9,403,25],[404,2,404,5],[404,6,404,8],[404,9,404,25],[405,2,405,5],[405,6,405,8],[405,9,405,25],[406,2,406,5],[406,6,406,8],[406,9,406,25],[407,2,407,5],[407,6,407,8],[407,9,407,25],[408,2,408,5],[408,6,408,8],[408,9,408,25],[409,2,409,5],[409,6,409,8],[409,9,409,25],[410,2,410,5],[410,6,410,8],[410,9,410,25],[411,2,411,5],[411,6,411,8],[411,9,411,25],[413,2,413,5],[413,6,413,8],[413,9,413,25],[415,2,415,5],[415,6,415,8],[415,9,415,25],[416,2,416,5],[416,6,416,8],[416,9,416,25],[417,2,417,5],[417,6,417,8],[417,9,417,25],[418,2,418,5],[418,6,418,8],[418,9,418,25],[419,2,419,5],[419,6,419,8],[419,9,419,25],[420,2,420,5],[420,6,420,8],[420,9,420,25],[421,2,421,5],[421,6,421,8],[421,9,421,25],[422,2,422,5],[422,6,422,8],[422,9,422,25],[423,2,423,5],[423,6,423,8],[423,9,423,25],[424,2,424,5],[424,6,424,8],[424,9,424,25],[425,2,425,5],[425,6,425,8],[425,9,425,25],[426,2,426,5],[426,6,426,8],[426,9,426,25],[427,2,427,5],[427,6,427,8],[427,9,427,25],[428,2,428,5],[428,6,428,8],[428,9,428,25],[429,2,429,5],[429,6,429,8],[429,9,429,25],[430,2,430,5],[430,6,430,8],[430,9,430,25],[431,2,431,5],[431,6,431,8],[431,9,431,25],[432,2,432,5],[432,6,432,8],[432,9,432,25],[433,2,433,5],[433,6,433,8],[433,9,433,25],[434,2,434,5],[434,6,434,8],[434,9,434,25],[436,2,436,5],[436,6,436,8],[436,9,436,25],[437,2,437,5],[437,6,437,8],[437,9,437,25],[438,2,438,5],[438,6,438,8],[438,9,438,25],[439,2,439,5],[439,6,439,8],[439,9,439,25],[440,2,440,5],[440,6,440,8],[440,9,440,25],[441,2,441,5],[441,6,441,8],[441,9,441,25],[442,2,442,5],[442,6,442,8],[442,9,442,25],[443,2,443,5],[443,6,443,8],[443,9,443,25],[444,2,444,5],[444,6,444,8],[444,9,444,25],[446,2,446,5],[446,6,446,8],[446,9,446,25],[447,2,447,5],[447,6,447,8],[447,9,447,25],[448,2,448,5],[448,6,448,8],[448,9,448,25],[449,2,449,5],[449,6,449,8],[449,9,449,25],[450,2,450,5],[450,6,450,8],[450,9,450,25],[451,2,451,5],[451,6,451,8],[451,9,451,25],[452,2,452,5],[452,6,452,8],[452,9,452,25],[453,2,453,5],[453,6,453,8],[453,9,453,25],[454,2,454,5],[454,6,454,8],[454,9,454,25],[455,2,455,5],[455,6,455,8],[455,9,455,25],[456,2,456,5],[456,6,456,8],[456,9,456,25],[457,2,457,5],[457,6,457,8],[457,9,457,25],[458,2,458,5],[458,6,458,8],[458,9,458,25],[459,2,459,5],[459,6,459,8],[459,9,459,25],[460,2,460,5],[460,6,460,8],[460,9,460,25],[462,2,462,5],[462,6,462,8],[462,9,462,25],[463,2,463,5],[463,6,463,8],[463,9,463,25],[464,2,464,5],[464,6,464,8],[464,9,464,25],[465,2,465,5],[465,6,465,8],[465,9,465,25],[466,2,466,5],[466,6,466,8],[466,9,466,25],[467,2,467,5],[467,6,467,8],[467,9,467,25],[468,2,468,5],[468,6,468,8],[468,9,468,25],[469,2,469,5],[469,6,469,8],[469,9,469,25],[470,2,470,5],[470,6,470,8],[470,9,470,25],[471,2,471,5],[471,6,471,8],[471,9,471,25],[472,2,472,5],[472,6,472,8],[472,9,472,25],[473,2,473,5],[473,6,473,8],[473,9,473,25],[474,2,474,5],[474,6,474,8],[474,9,474,25],[475,2,475,5],[475,6,475,8],[475,9,475,25]],"merged_total":1177,"flags":["merged_cut"]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,null,"X","X","X","X"]
[12,null,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,null,null,"of","on",{"$nulls":22},"端子编号","线色备注"]
[null,"PM.25D"]
[null,"EXC-1000"]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B14&\"地址: \"&B11&\" *)\"","v":"(* IOM 0801R 地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B11),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B11),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH10&AA10&\"-\"&AK10","v":"潜污泵井SUMP-01-泵1运行状态"},{"$nulls":16},{"$f":"IF(AI10=\"\",\"\",AI10)","v":"SUMP-01"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"潜污泵井","SUMP-01","B1A01","泵1运行状态",{"$f":"AH10&\"-\"&AK10","v":"潜污泵井-泵1运行状态"},{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_R1"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B11*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LSWPB1A01_R1 AT%I32.0 :BOOL; (*潜污泵井SUMP-01-泵1运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN10,SEARCH(\"AT%\",AN10),,REPT(\" \",25-SEARCH(\"AT%\",AN10))),SEARCH(\":\",REPLACE(AN10,SEARCH(\"AT%\",AN10),,REPT(\" \",25-SEARCH(\"AT%\",AN10)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN10,SEARCH(\"AT%\",AN10),,REPT(\" \",25-SEARCH(\"AT%\",AN10)))))),\" \")","v":"LSWPB1A01_R1            AT%I32.0       :BOOL; (*潜污泵井SUMP-01-泵1运行状态*)"},null,{"$f":"AM10","v":"SWPB1A01_R1"},{"$f":"J10","v":"潜污泵井SUMP-01-泵1运行状态"},{"$f":"10000+($B11*16*8+F10-1)","v":10256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B11),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B11),REPT(0,5))),4,1))","v":1},2,null,2,"C",{"$f":"AH11&AA11&\"-\"&AK11","v":"潜污泵井SUMP-01-泵1故障状态"},{"$nulls":16},{"$f":"IF(AI11=\"\",\"\",AI11)","v":"SUMP-01"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"潜污泵井","SUMP-01","B1A01","泵1故障状态",{"$f":"AH11&\"-\"&AK11","v":"潜污泵井-泵1故障状态"},{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_F1"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B11*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LSWPB1A01_F1 AT%I32.1 :BOOL; (*潜污泵井SUMP-01-泵1故障状态*)"},"LSWPB1A01_F1            AT%I32.1       :BOOL; (*潜污泵井SUMP-01-泵1故障状态*)",null,{"$f":"AM11","v":"SWPB1A01_F1"},{"$f":"J11","v":"潜污泵井SUMP-01-泵1故障状态"},{"$f":"AS10+1","v":10257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B11),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B11),REPT(0,5))),3,1))","v":0},3,null,3,"C",{"$f":"AH12&AA12&\"-\"&AK12","v":"潜污泵井SUMP-01-泵2运行状态"},{"$nulls":16},"SUMP-01",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"潜污泵井","SUMP-01","B1A01","泵2运行状态","潜污泵井-泵2运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_R2"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B11*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LSWPB1A01_R2 AT%I32.2 :BOOL; (*潜污泵井SUMP-01-泵2运行状态*)"},"LSWPB1A01_R2            AT%I32.2       :BOOL; (*潜污泵井SUMP-01-泵2运行状态*)",null,"SWPB1A01_R2","潜污泵井SUMP-01-泵2运行状态",{"$f":"AS11+1","v":10258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B11),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B11),REPT(0,5))),2,1))","v":0},4,null,4,"C",{"$f":"AH13&AA13&\"-\"&AK13","v":"潜污泵井SUMP-01-泵2故障状态"},{"$nulls":16},"SUMP-01",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"潜污泵井","SUMP-01","B1A01","泵2故障状态","潜污泵井-泵2故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_F2"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B11*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LSWPB1A01_F2 AT%I32.3 :BOOL; (*潜污泵井SUMP-01-泵2故障状态*)"},"LSWPB1A01_F2            AT%I32.3       :BOOL; (*潜污泵井SUMP-01-泵2故障状态*)",null,"SWPB1A01_F2","潜污泵井SUMP-01-泵2故障状态",10259]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B11),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B11),REPT(0,5))),1,1))","v":0},5,null,5,"C","潜污泵井SUMP-01-泵3运行状态",{"$nulls":16},"SUMP-01",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"潜污泵井","SUMP-01","B1A01","泵3运行状态","潜污泵井-泵3运行状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_R3"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B11*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LSWPB1A01_R3 AT%I32.4 :BOOL; (*潜污泵井SUMP-01-泵3运行状态*)"},"LSWPB1A01_R3            AT%I32.4       :BOOL; (*潜污泵井SUMP-01-泵3运行状态*)",null,"SWPB1A01_R3","潜污泵井SUMP-01-泵3运行状态",10260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B13=20,1,IF(B13=50,10,IF(B13=125,11,IF(B13=250,100,IF(B13=500,101,IF(B13=800,110,IF(B13=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B13=20,1,IF(B13=50,10,IF(B13=125,11,IF(B13=250,100,IF(B13=500,101,IF(B13=800,110,IF(B13=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","潜污泵井SUMP-01-泵3故障状态",{"$nulls":16},"SUMP-01",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"潜污泵井","SUMP-01","B1A01","泵3故障状态","潜污泵井-泵3故障状态",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_F3"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B11*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LSWPB1A01_F3 AT%I32.5 :BOOL; (*潜污泵井SUMP-01-泵3故障状态*)"},"LSWPB1A01_F3            AT%I32.5       :BOOL; (*潜污泵井SUMP-01-泵3故障状态*)",null,"SWPB1A01_F3","潜污泵井SUMP-01-泵3故障状态",10261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B13=20,1,IF(B13=50,10,IF(B13=125,11,IF(B13=250,100,IF(B13=500,101,IF(B13=800,110,IF(B13=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B13=20,1,IF(B13=50,10,IF(B13=125,11,IF(B13=250,100,IF(B13=500,101,IF(B13=800,110,IF(B13=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","潜污泵井SUMP-01-高液位",{"$nulls":16},"SUMP-01",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"潜污泵井","SUMP-01","B1A01","高液位","潜污泵井-高液位",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_HL"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B11*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LSWPB1A01_HL AT%I32.6 :BOOL; (*潜污泵井SUMP-01-高液位*)"},"LSWPB1A01_HL            AT%I32.6       :BOOL; (*潜污泵井SUMP-01-高液位*)",null,"SWPB1A01_HL","潜污泵井SUMP-01-高液位",10262]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B13=20,1,IF(B13=50,10,IF(B13=125,11,IF(B13=250,100,IF(B13=500,101,IF(B13=800,110,IF(B13=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B13=20,1,IF(B13=50,10,IF(B13=125,11,IF(B13=250,100,IF(B13=500,101,IF(B13=800,110,IF(B13=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","潜污泵井SUMP-01-低液位",{"$nulls":16},"SUMP-01",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"潜污泵井","SUMP-01","B1A01","低液位","潜污泵井-低液位",{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_LL"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B11*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LSWPB1A01_LL AT%I32.7 :BOOL; (*潜污泵井SUMP-01-低液位*)"},"LSWPB1A01_LL            AT%I32.7       :BOOL; (*潜污泵井SUMP-01-低液位*)",null,"SWPB1A01_LL","潜污泵井SUMP-01-低液位",10263]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B23&\"地址: \"&B20&\" *)\"","v":"(* IOM 1601R 地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B20),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B20),REPT(0,5))),5,1))","v":1},1,null,1,"C",{"$f":"AH19&AA19&\"-\"&AK19","v":"空调机组BXJ-1AP(KT)1-1-运行状态"},{"$nulls":16},{"$f":"IF(AI19=\"\",\"\",AI19)","v":"BXJ-1AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","BXJ-1AP(KT)1-1","01A01","运行状态",{"$f":"AH19&\"-\"&AK19","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B20*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU01A01_R AT%I48.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN19,SEARCH(\"AT%\",AN19),,REPT(\" \",25-SEARCH(\"AT%\",AN19))),SEARCH(\":\",REPLACE(AN19,SEARCH(\"AT%\",AN19),,REPT(\" \",25-SEARCH(\"AT%\",AN19)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN19,SEARCH(\"AT%\",AN19),,REPT(\" \",25-SEARCH(\"AT%\",AN19)))))),\" \")","v":"LAHU01A01_R             AT%I48.0       :BOOL; (*空调机组BXJ-1AP(KT)1-1-运行状态*)"},null,"AHU01A01_R",{"$f":"J19","v":"空调机组BXJ-1AP(KT)1-1-运行状态"},{"$f":"10000+($B20*16*8+F19-1)","v":10384}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B20),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B20),REPT(0,5))),4,1))","v":1},2,null,2,"C","空调机组BXJ-1AP(KT)1-1-故障状态",{"$nulls":16},{"$f":"IF(AI20=\"\",\"\",AI20)","v":"BXJ-1AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","BXJ-1AP(KT)1-1","01A01","故障状态",{"$f":"AH20&\"-\"&AK20","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B20*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU01A01_F AT%I48.1 :BOOL; (*空调机组BXJ-1AP(KT)1-1-故障状态*)"},"LAHU01A01_F             AT%I48.1       :BOOL; (*空调机组BXJ-1AP(KT)1-1-故障状态*)",null,"AHU01A01_F",{"$f":"J20","v":"空调机组BXJ-1AP(KT)1-1-故障状态"},{"$f":"AS19+1","v":10385}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B20),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B20),REPT(0,5))),3,1))","v":0},3,null,3,"C","空调机组BXJ-1AP(KT)1-1-自动状态",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","BXJ-1AP(KT)1-1","01A01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B20*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU01A01_A AT%I48.2 :BOOL; (*空调机组BXJ-1AP(KT)1-1-自动状态*)"},"LAHU01A01_A             AT%I48.2       :BOOL; (*空调机组BXJ-1AP(KT)1-1-自动状态*)",null,"AHU01A01_A","空调机组BXJ-1AP(KT)1-1-自动状态",{"$f":"AS20+1","v":10386}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B20),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B20),REPT(0,5))),2,1))","v":0},4,null,4,"C","空调机组BXJ-1AP(KT)1-1-风机压差",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","BXJ-1AP(KT)1-1","01A01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B20*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU01A01_FPS AT%I48.3 :BOOL; (*空调机组BXJ-1AP(KT)1-1-风机压差*)"},"LAHU01A01_FPS           AT%I48.3       :BOOL; (*空调机组BXJ-1AP(KT)1-1-风机压差*)",null,"AHU01A01_FPS","空调机组BXJ-1AP(KT)1-1-风机压差",10387]
[null,"IOM 1601R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B20),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B20),REPT(0,5))),1,1))","v":0},5,null,5,"C","空调机组BXJ-1AP(KT)1-1-初效滤网压差",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","BXJ-1AP(KT)1-1","01A01","初效滤网压差","空调机组-初效滤网压差",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_IPS"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B20*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU01A01_IPS AT%I48.4 :BOOL; (*空调机组BXJ-1AP(KT)1-1-初效滤网压差*)"},"LAHU01A01_IPS           AT%I48.4       :BOOL; (*空调机组BXJ-1AP(KT)1-1-初效滤网压差*)",null,"AHU01A01_IPS","空调机组BXJ-1AP(KT)1-1-初效滤网压差",10388]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B22=20,1,IF(B22=50,10,IF(B22=125,11,IF(B22=250,100,IF(B22=500,101,IF(B22=800,110,IF(B22=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B22=20,1,IF(B22=50,10,IF(B22=125,11,IF(B22=250,100,IF(B22=500,101,IF(B22=800,110,IF(B22=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","空调机组BXJ-1AP(KT)1-1-低温断路开关",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","BXJ-1AP(KT)1-1","01A01","低温断路开关","空调机组-低温断路开关",{"$f":"VLOOKUP(AH24,List!$B$3:$D$445,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_AFS"},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%I\"&B20*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":"LAHU01A01_AFS AT%I48.5 :BOOL; (*空调机组BXJ-1AP(KT)1-1-低温断路开关*)"},"LAHU01A01_AFS           AT%I48.5       :BOOL; (*空调机组BXJ-1AP(KT)1-1-低温断路开关*)",null,"AHU01A01_AFS","空调机组BXJ-1AP(KT)1-1-低温断路开关",10389]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B22=20,1,IF(B22=50,10,IF(B22=125,11,IF(B22=250,100,IF(B22=500,101,IF(B22=800,110,IF(B22=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B22=20,1,IF(B22=50,10,IF(B22=125,11,IF(B22=250,100,IF(B22=500,101,IF(B22=800,110,IF(B22=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","风机盘管BXJ-1AP(KT)1-7-运行状态",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"风机盘管","BXJ-1AP(KT)1-7","01A07","运行状态","风机盘管-运行状态",{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"FCU01A07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B20*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LFCU01A07_R AT%I48.6 :BOOL; (*风机盘管BXJ-1AP(KT)1-7-运行状态*)"},"LFCU01A07_R             AT%I48.6       :BOOL; (*风机盘管BXJ-1AP(KT)1-7-运行状态*)",null,"FCU01A07_R","风机盘管BXJ-1AP(KT)1-7-运行状态",10390]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B22=20,1,IF(B22=50,10,IF(B22=125,11,IF(B22=250,100,IF(B22=500,101,IF(B22=800,110,IF(B22=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B22=20,1,IF(B22=50,10,IF(B22=125,11,IF(B22=250,100,IF(B22=500,101,IF(B22=800,110,IF(B22=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","风机盘管BXJ-1AP(KT)1-7-自动状态",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"风机盘管","BXJ-1AP(KT)1-7","01A07","自动状态","风机盘管-自动状态",{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"FCU01A07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B20*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LFCU01A07_A AT%I48.7 :BOOL; (*风机盘管BXJ-1AP(KT)1-7-自动状态*)"},"LFCU01A07_A             AT%I48.7       :BOOL; (*风机盘管BXJ-1AP(KT)1-7-自动状态*)",null,"FCU01A07_A","风机盘管BXJ-1AP(KT)1-7-自动状态",10391]
[{"$nulls":5},9,null,9,"C","风机盘管BXJ-1AP(KT)1-7-电磁阀开启状态",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"风机盘管","BXJ-1AP(KT)1-7","01A07","电磁阀开启状态","风机盘管-电磁阀开启状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"FCU01A07_EVR"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B20*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LFCU01A07_EVR AT%I49.0 :BOOL; (*风机盘管BXJ-1AP(KT)1-7-电磁阀开启状态*)"},"LFCU01A07_EVR           AT%I49.0       :BOOL; (*风机盘管BXJ-1AP(KT)1-7-电磁阀开启状态*)",null,"FCU01A07_EVR","风机盘管BXJ-1AP(KT)1-7-电磁阀开启状态",10392]
[{"$nulls":5},10,null,10,"C","风机盘管BXJ-1AP(KT)1-7-电磁阀自动状态",{"$nulls":16},{"$f":"IF(AI28=\"\",\"\",AI28)","v":"BXJ-1AP(KT)1-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"风机盘管","BXJ-1AP(KT)1-7","01A07","电磁阀自动状态",{"$f":"AH28&\"-\"&AK28","v":"风机盘管-电磁阀自动状态"},{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"FCU01A07_EVA"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B20*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LFCU01A07_EVA AT%I49.1 :BOOL; (*风机盘管BXJ-1AP(KT)1-7-电磁阀自动状态*)"},"LFCU01A07_EVA           AT%I49.1       :BOOL; (*风机盘管BXJ-1AP(KT)1-7-电磁阀自动状态*)",null,"FCU01A07_EVA",{"$f":"J28","v":"风机盘管BXJ-1AP(KT)1-7-电磁阀自动状态"},10393]
[{"$nulls":5},11,null,11,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B20*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10394]
[{"$nulls":5},12,null,12,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B20*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10395]
[{"$nulls":5},13,null,13,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B20*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10396]
[{"$nulls":5},14,null,14,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B20*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10397]
[{"$nulls":5},15,null,15,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B20*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10398]
[".",{"$nulls":4},16,null,16,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B20*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10399]
[null,"IOM 0801D",{"$nulls":38},{"$f":"\"(* \"&B40&\"地址: \"&B37&\" *)\"","v":"(* IOM 0801D地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B37),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B37),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH36&AA36&\"-\"&AK36","v":"空调机组BXJ-1AP(KT)1-1-启停控制"},{"$nulls":16},{"$f":"IF(AI36=\"\",\"\",AI36)","v":"BXJ-1AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","BXJ-1AP(KT)1-1","01A01","启停控制",{"$f":"AH36&\"-\"&AK36","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%Q\"&B37*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU01A01_C AT%Q64.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN36,SEARCH(\"AT%\",AN36),,REPT(\" \",25-SEARCH(\"AT%\",AN36))),SEARCH(\":\",REPLACE(AN36,SEARCH(\"AT%\",AN36),,REPT(\" \",25-SEARCH(\"AT%\",AN36)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN36,SEARCH(\"AT%\",AN36),,REPT(\" \",25-SEARCH(\"AT%\",AN36)))))),\" \")","v":"LAHU01A01_C             AT%Q64.0       :BOOL; (*空调机组BXJ-1AP(KT)1-1-启停控制*)"},null,"AHU01A01_C",{"$f":"J36","v":"空调机组BXJ-1AP(KT)1-1-启停控制"},{"$f":"($B37*16*8+F36-1)","v":512}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B37),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B37),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","风机盘管BXJ-1AP(KT)1-7-启停控制",{"$nulls":16},{"$f":"IF(AI37=\"\",\"\",AI37)","v":"BXJ-1AP(KT)1-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"风机盘管","BXJ-1AP(KT)1-7","01A07","启停控制",{"$f":"AH37&\"-\"&AK37","v":"风机盘管-启停控制"},{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"FCU01A07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%Q\"&B37*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LFCU01A07_C AT%Q64.1 :BOOL; (*风机盘管BXJ-1AP(KT)1-7-启停控制*)"},"LFCU01A07_C             AT%Q64.1       :BOOL; (*风机盘管BXJ-1AP(KT)1-7-启停控制*)",null,"FCU01A07_C",{"$f":"J37","v":"风机盘管BXJ-1AP(KT)1-7-启停控制"},{"$f":"AS36+1","v":513}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B37),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B37),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","风机盘管BXJ-1AP(KT)1-7-电磁阀开关控制",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"风机盘管","BXJ-1AP(KT)1-7","01A07","电磁阀开关控制","风机盘管-电磁阀开关控制",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"FCU01A07_EVC"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%Q\"&B37*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LFCU01A07_EVC AT%Q64.2 :BOOL; (*风机盘管BXJ-1AP(KT)1-7-电磁阀开关控制*)"},"LFCU01A07_EVC           AT%Q64.2       :BOOL; (*风机盘管BXJ-1AP(KT)1-7-电磁阀开关控制*)",null,"FCU01A07_EVC","风机盘管BXJ-1AP(KT)1-7-电磁阀开关控制",{"$f":"AS37+1","v":514}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B37),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B37),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%Q\"&B37*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",515]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B37),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B37),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%Q\"&B37*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",516]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B39=20,1,IF(B39=50,10,IF(B39=125,11,IF(B39=250,100,IF(B39=500,101,IF(B39=800,110,IF(B39=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B39=20,1,IF(B39=50,10,IF(B39=125,11,IF(B39=250,100,IF(B39=500,101,IF(B39=800,110,IF(B39=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%Q\"&B37*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",517]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B39=20,1,IF(B39=50,10,IF(B39=125,11,IF(B39=250,100,IF(B39=500,101,IF(B39=800,110,IF(B39=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B39=20,1,IF(B39=50,10,IF(B39=125,11,IF(B39=250,100,IF(B39=500,101,IF(B39=800,110,IF(B39=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%Q\"&B37*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",518]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B39=20,1,IF(B39=50,10,IF(B39=125,11,IF(B39=250,100,IF(B39=500,101,IF(B39=800,110,IF(B39=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B39=20,1,IF(B39=50,10,IF(B39=125,11,IF(B39=250,100,IF(B39=500,101,IF(B39=800,110,IF(B39=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%Q\"&B37*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",519]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B49&\"地址: \"&B46&\" *)\"","v":"(* IOM 1601D地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B46),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B46),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH45&AA45&\"-\"&AK45","v":"-"},{"$nulls":16},{"$f":"IF(AI45=\"\",\"\",AI45)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH45&\"-\"&AK45","v":"-"},{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%Q\"&B46*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN45,SEARCH(\"AT%\",AN45),,REPT(\" \",25-SEARCH(\"AT%\",AN45))),SEARCH(\":\",REPLACE(AN45,SEARCH(\"AT%\",AN45),,REPT(\" \",25-SEARCH(\"AT%\",AN45)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN45,SEARCH(\"AT%\",AN45),,REPT(\" \",25-SEARCH(\"AT%\",AN45)))))),\" \")","v":" "},null,{"$error":"#N/A"},{"$f":"J45","v":"-"},{"$f":"($B46*16*8+F45-1)","v":384}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B46),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B46),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","-",{"$nulls":16},{"$f":"IF(AI46=\"\",\"\",AI46)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH46&\"-\"&AK46","v":"-"},{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%Q\"&B46*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J46","v":"-"},{"$f":"AS45+1","v":385}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B46),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B46),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%Q\"&B46*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS46+1","v":386}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B46),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B46),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%Q\"&B46*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",387]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B46),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B46),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%Q\"&B46*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",388]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B48=20,1,IF(B48=50,10,IF(B48=125,11,IF(B48=250,100,IF(B48=500,101,IF(B48=800,110,IF(B48=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B48=20,1,IF(B48=50,10,IF(B48=125,11,IF(B48=250,100,IF(B48=500,101,IF(B48=800,110,IF(B48=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%Q\"&B46*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",389]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B48=20,1,IF(B48=50,10,IF(B48=125,11,IF(B48=250,100,IF(B48=500,101,IF(B48=800,110,IF(B48=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B48=20,1,IF(B48=50,10,IF(B48=125,11,IF(B48=250,100,IF(B48=500,101,IF(B48=800,110,IF(B48=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%Q\"&B46*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",390]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B48=20,1,IF(B48=50,10,IF(B48=125,11,IF(B48=250,100,IF(B48=500,101,IF(B48=800,110,IF(B48=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B48=20,1,IF(B48=50,10,IF(B48=125,11,IF(B48=250,100,IF(B48=500,101,IF(B48=800,110,IF(B48=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%Q\"&B46*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",391]
[{"$nulls":5},9,null,"9+","9-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%Q\"&B46*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",392]
[{"$nulls":5},10,null,"10+","10-","-",{"$nulls":16},{"$f":"IF(AI54=\"\",\"\",AI54)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH54&\"-\"&AK54","v":"-"},{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%Q\"&B46*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J54","v":"-"},393]
[{"$nulls":5},11,null,"11+","11-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%Q\"&B46*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",394]
[{"$nulls":5},12,null,"12+","12-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%Q\"&B46*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",395]
[{"$nulls":5},13,null,"13+","13-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%Q\"&B46*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",396]
[{"$nulls":5},14,null,"14+","14-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%Q\"&B46*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",397]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH59,List!$B$3:$D$445,2,FALSE)&AJ59&\"_\"&VLOOKUP(AK59,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM59&\" \"&\"AT%Q\"&B46*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J59&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",398]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%Q\"&B46*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",399]
[null,{"$f":"B66","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B66&\"地址: \"&B63&\" *)\"","v":"(* IOM 0801U地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B63),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B63),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH62&AA62&\"-\"&AK62","v":"空调机组BXJ-1AP(KT)1-1-回风温度"},{"$nulls":16},{"$f":"IF(AI62=\"\",\"\",AI62)","v":"BXJ-1AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","BXJ-1AP(KT)1-1","01A01","回风温度",{"$f":"AH62&\"-\"&AK62","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B63*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LAHU01A01_RT AT%I80.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN62,SEARCH(\"AT%\",AN62),,REPT(\" \",25-SEARCH(\"AT%\",AN62))),SEARCH(\":\",REPLACE(AN62,SEARCH(\"AT%\",AN62),,REPT(\" \",25-SEARCH(\"AT%\",AN62)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN62,SEARCH(\"AT%\",AN62),,REPT(\" \",25-SEARCH(\"AT%\",AN62)))))),\" \")","v":"LAHU01A01_RT            AT%I80.0       :INT ; (*空调机组BXJ-1AP(KT)1-1-回风温度*)"},null,"AHU01A01_RT",{"$f":"J62","v":"空调机组BXJ-1AP(KT)1-1-回风温度"},{"$f":"30000+($B63*8+F62-1)","v":30040}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B63),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B63),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组BXJ-1AP(KT)1-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI63=\"\",\"\",AI63)","v":"BXJ-1AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","BXJ-1AP(KT)1-1","01A01","水阀反馈",{"$f":"AH63&\"-\"&AK63","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B63*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LAHU01A01_WVB AT%I82.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-水阀反馈*)"},"LAHU01A01_WVB           AT%I82.0       :INT ; (*空调机组BXJ-1AP(KT)1-1-水阀反馈*)",null,"AHU01A01_WVB",{"$f":"J63","v":"空调机组BXJ-1AP(KT)1-1-水阀反馈"},{"$f":"AS62+1","v":30041}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B63),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B63),REPT(0,5))),3,1))","v":1},3,null,3,"0V","风机盘管BXJ-1AP(KT)1-7-温度状态",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"风机盘管","BXJ-1AP(KT)1-7","01A07","温度状态","风机盘管-温度状态",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"FCU01A07_T"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B63*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LFCU01A07_T AT%I84.0 :INT ; (*风机盘管BXJ-1AP(KT)1-7-温度状态*)"},"LFCU01A07_T             AT%I84.0       :INT ; (*风机盘管BXJ-1AP(KT)1-7-温度状态*)",null,"FCU01A07_T","风机盘管BXJ-1AP(KT)1-7-温度状态",{"$f":"AS63+1","v":30042}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B63),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B63),REPT(0,5))),2,1))","v":0},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B63*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30043]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B63),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B63),REPT(0,5))),1,1))","v":0},5,null,5,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B63*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30044]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B65=20,1,IF(B65=50,10,IF(B65=125,11,IF(B65=250,100,IF(B65=500,101,IF(B65=800,110,IF(B65=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B65=20,1,IF(B65=50,10,IF(B65=125,11,IF(B65=250,100,IF(B65=500,101,IF(B65=800,110,IF(B65=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","-",{"$nulls":16},{"$f":"IF(AI67=\"\",\"\",AI67)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%I\"&B63*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J67","v":"-"},30045]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B65=20,1,IF(B65=50,10,IF(B65=125,11,IF(B65=250,100,IF(B65=500,101,IF(B65=800,110,IF(B65=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B65=20,1,IF(B65=50,10,IF(B65=125,11,IF(B65=250,100,IF(B65=500,101,IF(B65=800,110,IF(B65=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%I\"&B63*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30046]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B65=20,1,IF(B65=50,10,IF(B65=125,11,IF(B65=250,100,IF(B65=500,101,IF(B65=800,110,IF(B65=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B65=20,1,IF(B65=50,10,IF(B65=125,11,IF(B65=250,100,IF(B65=500,101,IF(B65=800,110,IF(B65=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%I\"&B63*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30047]
[null,{"$f":"B75","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B75&\"地址: \"&B72&\" *)\"","v":"(* IOM 0401U地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B72),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B72),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH71&AA71&\"-\"&AK71","v":"-"},{"$nulls":16},{"$f":"IF(AI71=\"\",\"\",AI71)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH71&\"-\"&AK71","v":"-"},{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%I\"&B72*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN71,SEARCH(\"AT%\",AN71),,REPT(\" \",25-SEARCH(\"AT%\",AN71))),SEARCH(\":\",REPLACE(AN71,SEARCH(\"AT%\",AN71),,REPT(\" \",25-SEARCH(\"AT%\",AN71)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN71,SEARCH(\"AT%\",AN71),,REPT(\" \",25-SEARCH(\"AT%\",AN71)))))),\" \")","v":" "},null,{"$error":"#N/A"},{"$f":"J71","v":"-"},{"$f":"30000+($B72*8+F71-1)","v":30040}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B72),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B72),REPT(0,5))),4,1))","v":0},2,null,2,"0V","-",{"$nulls":16},{"$f":"IF(AI72=\"\",\"\",AI72)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH72&\"-\"&AK72","v":"-"},{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%I\"&B72*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J72","v":"-"},{"$f":"AS71+1","v":30041}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B72),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B72),REPT(0,5))),3,1))","v":1},3,null,3,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%I\"&B72*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS72+1","v":30042}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B72),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B72),REPT(0,5))),2,1))","v":0},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%I\"&B72*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30043]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B72),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B72),REPT(0,5))),1,1))","v":0}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B74=20,1,IF(B74=50,10,IF(B74=125,11,IF(B74=250,100,IF(B74=500,101,IF(B74=800,110,IF(B74=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B74=20,1,IF(B74=50,10,IF(B74=125,11,IF(B74=250,100,IF(B74=500,101,IF(B74=800,110,IF(B74=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B74=20,1,IF(B74=50,10,IF(B74=125,11,IF(B74=250,100,IF(B74=500,101,IF(B74=800,110,IF(B74=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B74=20,1,IF(B74=50,10,IF(B74=125,11,IF(B74=250,100,IF(B74=500,101,IF(B74=800,110,IF(B74=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B74=20,1,IF(B74=50,10,IF(B74=125,11,IF(B74=250,100,IF(B74=500,101,IF(B74=800,110,IF(B74=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B74=20,1,IF(B74=50,10,IF(B74=125,11,IF(B74=250,100,IF(B74=500,101,IF(B74=800,110,IF(B74=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B84","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B84&\"地址: \"&B81&\" *)\"","v":"(* IOM 0401A地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B81),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B81),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH80&AA80&\"-\"&AK80","v":"空调机组BXJ-1AP(KT)1-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI80=\"\",\"\",AI80)","v":"BXJ-1AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","BXJ-1AP(KT)1-1","01A01","水阀控制",{"$f":"AH80&\"-\"&AK80","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B81*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU01A01_WVC AT%Q96.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN80,SEARCH(\"AT%\",AN80),,REPT(\" \",25-SEARCH(\"AT%\",AN80))),SEARCH(\":\",REPLACE(AN80,SEARCH(\"AT%\",AN80),,REPT(\" \",25-SEARCH(\"AT%\",AN80)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN80,SEARCH(\"AT%\",AN80),,REPT(\" \",25-SEARCH(\"AT%\",AN80)))))),\" \")","v":"LAHU01A01_WVC           AT%Q96.0       :INT ; (*空调机组BXJ-1AP(KT)1-1-水阀控制*)"},null,{"$f":"AM80","v":"AHU01A01_WVC"},{"$f":"J80","v":"空调机组BXJ-1AP(KT)1-1-水阀控制"},{"$f":"40000+($B81*8+F80-1)","v":40048}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B81),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B81),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH81&AA81&\"-\"&AK81","v":"-"},{"$nulls":16},{"$f":"IF(AI81=\"\",\"\",AI81)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH81&\"-\"&AK81","v":"-"},{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%Q\"&B81*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J81","v":"-"},{"$f":"AS80+1","v":40049}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B81),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B81),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH82&AA82&\"-\"&AK82","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%Q\"&B81*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS81+1","v":40050}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B81),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B81),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH83&AA83&\"-\"&AK83","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%Q\"&B81*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40051]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B81),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B81),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B83=20,1,IF(B83=50,10,IF(B83=125,11,IF(B83=250,100,IF(B83=500,101,IF(B83=800,110,IF(B83=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B83=20,1,IF(B83=50,10,IF(B83=125,11,IF(B83=250,100,IF(B83=500,101,IF(B83=800,110,IF(B83=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B83=20,1,IF(B83=50,10,IF(B83=125,11,IF(B83=250,100,IF(B83=500,101,IF(B83=800,110,IF(B83=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B83=20,1,IF(B83=50,10,IF(B83=125,11,IF(B83=250,100,IF(B83=500,101,IF(B83=800,110,IF(B83=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B83=20,1,IF(B83=50,10,IF(B83=125,11,IF(B83=250,100,IF(B83=500,101,IF(B83=800,110,IF(B83=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B83=20,1,IF(B83=50,10,IF(B83=125,11,IF(B83=250,100,IF(B83=500,101,IF(B83=800,110,IF(B83=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,"DC24V"]
[null,"DC24V\n电源",{"$nulls":5},"+","-",{"$nulls":17},{"$f":"IF(AI89=\"\",\"\",AI89)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(J89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[{"$nulls":7},"+","-",{"$nulls":17},{"$f":"IF(AI90=\"\",\"\",AI90)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(J90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[{"$nulls":7},"+","-",{"$nulls":17},"",{"$f":"_xlfn.IFNA(VLOOKUP(J91,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J91,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[{"$nulls":7},"+","-",{"$nulls":17},"",{"$f":"_xlfn.IFNA(VLOOKUP(J92,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J92,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[{"$nulls":7},"+","-",{"$nulls":17},"",{"$f":"_xlfn.IFNA(VLOOKUP(J93,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J93,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[{"$nulls":7},"+","-",{"$nulls":17},{"$f":"IF(AI94=\"\",\"\",AI94)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(J94,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J94,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[{"$nulls":7},"+","-",{"$nulls":17},"",{"$f":"_xlfn.IFNA(VLOOKUP(J95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[{"$nulls":7},"+","-",{"$nulls":17},"",{"$f":"_xlfn.IFNA(VLOOKUP(J96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[{"$nulls":7},"+","-",{"$nulls":17},"",{"$f":"_xlfn.IFNA(VLOOKUP(J97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[".",{"$nulls":6},"+","-",{"$nulls":17},{"$f":"IF(AI98=\"\",\"\",AI98)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(J98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[null,"AC24V"]
[null,"AC24V\n电源",{"$nulls":5},"L","N",{"$nulls":17},{"$f":"IF(AI100=\"\",\"\",AI100)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(J100,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J100,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[{"$nulls":7},"L","N",{"$nulls":17},{"$f":"IF(AI101=\"\",\"\",AI101)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(J101,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J101,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[{"$nulls":7},"L","N",{"$nulls":17},"",{"$f":"_xlfn.IFNA(VLOOKUP(J102,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J102,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[{"$nulls":7},"L","N",{"$nulls":17},"",{"$f":"_xlfn.IFNA(VLOOKUP(J103,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J103,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[{"$nulls":7},"L","N",{"$nulls":17},"",{"$f":"_xlfn.IFNA(VLOOKUP(J104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[{"$nulls":7},"L","N",{"$nulls":17},{"$f":"IF(AI105=\"\",\"\",AI105)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(J105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[{"$nulls":7},"L","N",{"$nulls":17},"",{"$f":"_xlfn.IFNA(VLOOKUP(J106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[{"$nulls":7},"L","N",{"$nulls":17},"",{"$f":"_xlfn.IFNA(VLOOKUP(J107,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J107,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[{"$nulls":7},"L","N",{"$nulls":17},"",{"$f":"_xlfn.IFNA(VLOOKUP(J108,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J108,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[".",{"$nulls":6},"L","N",{"$nulls":17},{"$f":"IF(AI109=\"\",\"\",AI109)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(J109,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(J109,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"}]
[null,"EXC-61610",{"$nulls":38},{"$f":"\"(* \"&B110&\"地址: \"&B112&\" *)\"","v":"(* EXC-61610地址: 0 *)"}]
[null,"addr",{"$f":"B110","v":"EXC-61610"},null,null,"DI1",null,1,"COM",{"$f":"AH111&AA111&\"-\"&AK111","v":"P新风机组BXJ-1AP(KT)1-2-运行状态"},{"$nulls":16},{"$f":"IF(AI111=\"\",\"\",AI111)","v":"BXJ-1AP(KT)1-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL111,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL111,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"P新风机组","BXJ-1AP(KT)1-2","01A02","运行状态",{"$f":"AH111&\"-\"&AK111","v":"P新风机组-运行状态"},{"$f":"VLOOKUP(AH111,List!$B$3:$D$445,2,FALSE)&AJ111&\"_\"&VLOOKUP(AK111,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM111&\" \"&\"AT%I0.0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J111&\"*)\",\" \")","v":"LPAU01A02_R AT%I0.0 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN111,SEARCH(\"AT%\",AN111),,REPT(\" \",25-SEARCH(\"AT%\",AN111))),SEARCH(\":\",REPLACE(AN111,SEARCH(\"AT%\",AN111),,REPT(\" \",25-SEARCH(\"AT%\",AN111)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN111,SEARCH(\"AT%\",AN111),,REPT(\" \",25-SEARCH(\"AT%\",AN111)))))),\" \")","v":"LPAU01A02_R             AT%I0.0        :BOOL; (*P新风机组BXJ-1AP(KT)1-2-运行状态*)"},null,{"$f":"AM111","v":"PAU01A02_R"},{"$f":"J111","v":"P新风机组BXJ-1AP(KT)1-2-运行状态"},{"$f":"10000+($B112*16*8+H111-1)","v":10000}]
[null,0,null,null,null,"DI2",null,2,null,"P新风机组BXJ-1AP(KT)1-2-故障状态",{"$nulls":16},{"$f":"IF(AI112=\"\",\"\",AI112)","v":"BXJ-1AP(KT)1-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"P新风机组","BXJ-1AP(KT)1-2","01A02","故障状态",{"$f":"AH112&\"-\"&AK112","v":"P新风机组-故障状态"},{"$f":"VLOOKUP(AH112,List!$B$3:$D$445,2,FALSE)&AJ112&\"_\"&VLOOKUP(AK112,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM112&\" \"&\"AT%I0.1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J112&\"*)\",\" \")","v":"LPAU01A02_F AT%I0.1 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-故障状态*)"},"LPAU01A02_F             AT%I0.1        :BOOL; (*P新风机组BXJ-1AP(KT)1-2-故障状态*)",null,"PAU01A02_F",{"$f":"J112","v":"P新风机组BXJ-1AP(KT)1-2-故障状态"},{"$f":"AS111+1","v":10001}]
[null,"kbs",null,null,null,"DI3",null,3,null,"P新风机组BXJ-1AP(KT)1-2-自动状态",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"P新风机组","BXJ-1AP(KT)1-2","01A02","自动状态","P新风机组-自动状态",{"$f":"VLOOKUP(AH113,List!$B$3:$D$445,2,FALSE)&AJ113&\"_\"&VLOOKUP(AK113,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM113&\" \"&\"AT%I0.2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J113&\"*)\",\" \")","v":"LPAU01A02_A AT%I0.2 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-自动状态*)"},"LPAU01A02_A             AT%I0.2        :BOOL; (*P新风机组BXJ-1AP(KT)1-2-自动状态*)",null,"PAU01A02_A","P新风机组BXJ-1AP(KT)1-2-自动状态",{"$f":"AS112+1","v":10002}]
[null,50,null,null,null,"DI4",null,4,"COM","P新风机组BXJ-1AP(KT)1-2-风机压差",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"P新风机组","BXJ-1AP(KT)1-2","01A02","风机压差","P新风机组-风机压差",{"$f":"VLOOKUP(AH114,List!$B$3:$D$445,2,FALSE)&AJ114&\"_\"&VLOOKUP(AK114,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM114&\" \"&\"AT%I0.3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J114&\"*)\",\" \")","v":"LPAU01A02_FPS AT%I0.3 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-风机压差*)"},"LPAU01A02_FPS           AT%I0.3        :BOOL; (*P新风机组BXJ-1AP(KT)1-2-风机压差*)",null,"PAU01A02_FPS","P新风机组BXJ-1AP(KT)1-2-风机压差",10003]
[null," ",null,null,null,"DI5",null,5,null,"P新风机组BXJ-1AP(KT)1-2-初效滤网压差",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"P新风机组","BXJ-1AP(KT)1-2","01A02","初效滤网压差","P新风机组-初效滤网压差",{"$f":"VLOOKUP(AH115,List!$B$3:$D$445,2,FALSE)&AJ115&\"_\"&VLOOKUP(AK115,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_IPS"},{"$f":"_xlfn.IFNA(\"L\"&AM115&\" \"&\"AT%I0.4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J115&\"*)\",\" \")","v":"LPAU01A02_IPS AT%I0.4 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-初效滤网压差*)"},"LPAU01A02_IPS           AT%I0.4        :BOOL; (*P新风机组BXJ-1AP(KT)1-2-初效滤网压差*)",null,"PAU01A02_IPS","P新风机组BXJ-1AP(KT)1-2-初效滤网压差",10004]
[{"$nulls":5},"DI6",null,6,null,"P新风机组BXJ-1AP(KT)1-2-低温断路开关",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"P新风机组","BXJ-1AP(KT)1-2","01A02","低温断路开关","P新风机组-低温断路开关",{"$f":"VLOOKUP(AH116,List!$B$3:$D$445,2,FALSE)&AJ116&\"_\"&VLOOKUP(AK116,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_AFS"},{"$f":"_xlfn.IFNA(\"L\"&AM116&\" \"&\"AT%I0.5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J116&\"*)\",\" \")","v":"LPAU01A02_AFS AT%I0.5 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-低温断路开关*)"},"LPAU01A02_AFS           AT%I0.5        :BOOL; (*P新风机组BXJ-1AP(KT)1-2-低温断路开关*)",null,"PAU01A02_AFS","P新风机组BXJ-1AP(KT)1-2-低温断路开关",10005]
[{"$nulls":5},"DI7",null,7,"COM","P新风机组BXJ-1AP(KT)1-2-新风阀开状态",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL117,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL117,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"P新风机组","BXJ-1AP(KT)1-2","01A02","新风阀开状态","P新风机组-新风阀开状态",{"$f":"VLOOKUP(AH117,List!$B$3:$D$445,2,FALSE)&AJ117&\"_\"&VLOOKUP(AK117,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_FDOB"},{"$f":"_xlfn.IFNA(\"L\"&AM117&\" \"&\"AT%I0.6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J117&\"*)\",\" \")","v":"LPAU01A02_FDOB AT%I0.6 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-新风阀开状态*)"},"LPAU01A02_FDOB          AT%I0.6        :BOOL; (*P新风机组BXJ-1AP(KT)1-2-新风阀开状态*)",null,"PAU01A02_FDOB","P新风机组BXJ-1AP(KT)1-2-新风阀开状态",10006]
[".",{"$nulls":4},"DI8",null,8,null,"P新风机组BXJ-1AP(KT)1-2-新风阀关状态",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL118,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL118,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"P新风机组","BXJ-1AP(KT)1-2","01A02","新风阀关状态","P新风机组-新风阀关状态",{"$f":"VLOOKUP(AH118,List!$B$3:$D$445,2,FALSE)&AJ118&\"_\"&VLOOKUP(AK118,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_FDSB"},{"$f":"_xlfn.IFNA(\"L\"&AM118&\" \"&\"AT%I0.7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J118&\"*)\",\" \")","v":"LPAU01A02_FDSB AT%I0.7 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-新风阀关状态*)"},"LPAU01A02_FDSB          AT%I0.7        :BOOL; (*P新风机组BXJ-1AP(KT)1-2-新风阀关状态*)",null,"PAU01A02_FDSB","P新风机组BXJ-1AP(KT)1-2-新风阀关状态",10007]
[{"$nulls":5},"DI9",null,9,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL119,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL119,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH119,List!$B$3:$D$445,2,FALSE)&AJ119&\"_\"&VLOOKUP(AK119,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM119&\" \"&\"AT%I1.0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J119&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"10000+(($B112*16+1)*8+H119-9)","v":10008}]
[{"$nulls":5},"DI10",null,10,"COM","-",{"$nulls":16},{"$f":"IF(AI120=\"\",\"\",AI120)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL120,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL120,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH120&\"-\"&AK120","v":"-"},{"$f":"VLOOKUP(AH120,List!$B$3:$D$445,2,FALSE)&AJ120&\"_\"&VLOOKUP(AK120,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM120&\" \"&\"AT%I1.1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J120&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J120","v":"-"},{"$f":"AS119+1","v":10009}]
[{"$nulls":5},"DI11",null,11,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH121,List!$B$3:$D$445,2,FALSE)&AJ121&\"_\"&VLOOKUP(AK121,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM121&\" \"&\"AT%I1.2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J121&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS120+1","v":10010}]
[{"$nulls":5},"DI12",null,12,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH122,List!$B$3:$D$445,2,FALSE)&AJ122&\"_\"&VLOOKUP(AK122,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM122&\" \"&\"AT%I1.3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J122&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10011]
[{"$nulls":5},"DO1",null,"1+","1-","P新风机组BXJ-1AP(KT)1-2-启停控制",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"P新风机组","BXJ-1AP(KT)1-2","01A02","启停控制","P新风机组-启停控制",{"$f":"VLOOKUP(AH123,List!$B$3:$D$445,2,FALSE)&AJ123&\"_\"&VLOOKUP(AK123,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM123&\" \"&\"AT%Q0.0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J123&\"*)\",\" \")","v":"LPAU01A02_C AT%Q0.0 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-启停控制*)"},"LPAU01A02_C             AT%Q0.0        :BOOL; (*P新风机组BXJ-1AP(KT)1-2-启停控制*)",null,"PAU01A02_C","P新风机组BXJ-1AP(KT)1-2-启停控制",{"$f":"($B112*16*8+LEFT(H123,1)-1)","v":0}]
[{"$nulls":5},"DO2",null,"2+","2-","P新风机组BXJ-1AP(KT)1-2-新风阀开控制",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"P新风机组","BXJ-1AP(KT)1-2","01A02","新风阀开控制","P新风机组-新风阀开控制",{"$f":"VLOOKUP(AH124,List!$B$3:$D$445,2,FALSE)&AJ124&\"_\"&VLOOKUP(AK124,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_FDOC"},{"$f":"_xlfn.IFNA(\"L\"&AM124&\" \"&\"AT%Q0.1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J124&\"*)\",\" \")","v":"LPAU01A02_FDOC AT%Q0.1 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-新风阀开控制*)"},"LPAU01A02_FDOC          AT%Q0.1        :BOOL; (*P新风机组BXJ-1AP(KT)1-2-新风阀开控制*)",null,"PAU01A02_FDOC","P新风机组BXJ-1AP(KT)1-2-新风阀开控制",1]
[{"$nulls":5},"DO3",null,"3+","3-","P新风机组BXJ-1AP(KT)1-2-新风阀关控制",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"P新风机组","BXJ-1AP(KT)1-2","01A02","新风阀关控制","P新风机组-新风阀关控制",{"$f":"VLOOKUP(AH125,List!$B$3:$D$445,2,FALSE)&AJ125&\"_\"&VLOOKUP(AK125,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_FDSC"},{"$f":"_xlfn.IFNA(\"L\"&AM125&\" \"&\"AT%Q0.2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J125&\"*)\",\" \")","v":"LPAU01A02_FDSC AT%Q0.2 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-新风阀关控制*)"},"LPAU01A02_FDSC          AT%Q0.2        :BOOL; (*P新风机组BXJ-1AP(KT)1-2-新风阀关控制*)",null,"PAU01A02_FDSC","P新风机组BXJ-1AP(KT)1-2-新风阀关控制",2]
[{"$nulls":5},"DO4",null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL126,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL126,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH126,List!$B$3:$D$445,2,FALSE)&AJ126&\"_\"&VLOOKUP(AK126,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM126&\" \"&\"AT%Q0.3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J126&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",3]
[{"$nulls":5},"DO5",null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL127,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL127,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH127,List!$B$3:$D$445,2,FALSE)&AJ127&\"_\"&VLOOKUP(AK127,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM127&\" \"&\"AT%Q0.4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J127&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",4]
[{"$nulls":5},"DO6",null,"6+","6-","-",{"$nulls":16},{"$f":"IF(AI128=\"\",\"\",AI128)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL128,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL128,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH128&\"-\"&AK128","v":"-"},{"$f":"VLOOKUP(AH128,List!$B$3:$D$445,2,FALSE)&AJ128&\"_\"&VLOOKUP(AK128,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM128&\" \"&\"AT%Q0.5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J128&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J128","v":"-"},5]
[{"$nulls":5},"AI1",null,1,"0\nV","P新风机组BXJ-1AP(KT)1-2-送风温度",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL129,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL129,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"P新风机组","BXJ-1AP(KT)1-2","01A02","送风温度","P新风机组-送风温度",{"$f":"VLOOKUP(AH129,List!$B$3:$D$445,2,FALSE)&AJ129&\"_\"&VLOOKUP(AK129,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_ST"},{"$f":"_xlfn.IFNA(\"L\"&AM129&\" \"&\"AT%I2.0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J129&\"*)\",\" \")","v":"LPAU01A02_ST AT%I2.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-送风温度*)"},"LPAU01A02_ST            AT%I2.0        :INT ; (*P新风机组BXJ-1AP(KT)1-2-送风温度*)",null,"PAU01A02_ST","P新风机组BXJ-1AP(KT)1-2-送风温度",{"$f":"30000+($B112*8+LEFT(H129,1))","v":30001}]
[{"$nulls":5},"AI2",null,2,null,"P新风机组BXJ-1AP(KT)1-2-水阀反馈",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL130,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL130,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"P新风机组","BXJ-1AP(KT)1-2","01A02","水阀反馈","P新风机组-水阀反馈",{"$f":"VLOOKUP(AH130,List!$B$3:$D$445,2,FALSE)&AJ130&\"_\"&VLOOKUP(AK130,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM130&\" \"&\"AT%I4.0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J130&\"*)\",\" \")","v":"LPAU01A02_WVB AT%I4.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-水阀反馈*)"},"LPAU01A02_WVB           AT%I4.0        :INT ; (*P新风机组BXJ-1AP(KT)1-2-水阀反馈*)",null,"PAU01A02_WVB","P新风机组BXJ-1AP(KT)1-2-水阀反馈",30002]
[{"$nulls":5},"AI3",null,3,"0\nV","P新风机组BXJ-1AP(KT)1-2-变频器频率反馈",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL131,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL131,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"P新风机组","BXJ-1AP(KT)1-2","01A02","变频器频率反馈","P新风机组-变频器频率反馈",{"$f":"VLOOKUP(AH131,List!$B$3:$D$445,2,FALSE)&AJ131&\"_\"&VLOOKUP(AK131,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_VFB"},{"$f":"_xlfn.IFNA(\"L\"&AM131&\" \"&\"AT%I6.0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J131&\"*)\",\" \")","v":"LPAU01A02_VFB AT%I6.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-变频器频率反馈*)"},"LPAU01A02_VFB           AT%I6.0        :INT ; (*P新风机组BXJ-1AP(KT)1-2-变频器频率反馈*)",null,"PAU01A02_VFB","P新风机组BXJ-1AP(KT)1-2-变频器频率反馈",30003]
[{"$nulls":5},"AI4",null,4,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL132,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL132,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH132,List!$B$3:$D$445,2,FALSE)&AJ132&\"_\"&VLOOKUP(AK132,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM132&\" \"&\"AT%I8.0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J132&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30004]
[{"$nulls":5},"AI5",null,5,"0\nV","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL133,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL133,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH133,List!$B$3:$D$445,2,FALSE)&AJ133&\"_\"&VLOOKUP(AK133,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM133&\" \"&\"AT%I10.0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J133&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30005]
[".",{"$nulls":4},"AI6",null,6,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL134,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL134,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH134,List!$B$3:$D$445,2,FALSE)&AJ134&\"_\"&VLOOKUP(AK134,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM134&\" \"&\"AT%I12.0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J134&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30006]
[{"$nulls":5},"AO1",null,"1+","1-","P新风机组BXJ-1AP(KT)1-2-水阀控制",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL135,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL135,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"P新风机组","BXJ-1AP(KT)1-2","01A02","水阀控制","P新风机组-水阀控制",{"$f":"VLOOKUP(AH135,List!$B$3:$D$445,2,FALSE)&AJ135&\"_\"&VLOOKUP(AK135,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM135&\" \"&\"AT%Q8.0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J135&\"*)\",\" \")","v":"LPAU01A02_WVC AT%Q8.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-水阀控制*)"},"LPAU01A02_WVC           AT%Q8.0        :INT ; (*P新风机组BXJ-1AP(KT)1-2-水阀控制*)",null,"PAU01A02_WVC","P新风机组BXJ-1AP(KT)1-2-水阀控制",{"$f":"40000+($B112*8+LEFT(H135,1)+3)","v":40004}]
[{"$nulls":5},"AO2",null,"2+","2-","P新风机组BXJ-1AP(KT)1-2-变频器频率控制",{"$nulls":16},{"$f":"IF(AI136=\"\",\"\",AI136)","v":"BXJ-1AP(KT)1-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL136,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL136,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"P新风机组","BXJ-1AP(KT)1-2","01A02","变频器频率控制",{"$f":"AH136&\"-\"&AK136","v":"P新风机组-变频器频率控制"},{"$f":"VLOOKUP(AH136,List!$B$3:$D$445,2,FALSE)&AJ136&\"_\"&VLOOKUP(AK136,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_VFC"},{"$f":"_xlfn.IFNA(\"L\"&AM136&\" \"&\"AT%Q10.0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J136&\"*)\",\" \")","v":"LPAU01A02_VFC AT%Q10.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-变频器频率控制*)"},"LPAU01A02_VFC           AT%Q10.0       :INT ; (*P新风机组BXJ-1AP(KT)1-2-变频器频率控制*)",null,"PAU01A02_VFC",{"$f":"J136","v":"P新风机组BXJ-1AP(KT)1-2-变频器频率控制"},{"$f":"AS135+1","v":40005}]
[{"$nulls":5},"AO3",null,"3+","3-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL137,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL137,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH137,List!$B$3:$D$445,2,FALSE)&AJ137&\"_\"&VLOOKUP(AK137,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM137&\" \"&\"AT%Q12.0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J137&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS136+1","v":40006}]
[{"$nulls":5},"AO4",null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL138,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL138,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH138,List!$B$3:$D$445,2,FALSE)&AJ138&\"_\"&VLOOKUP(AK138,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM138&\" \"&\"AT%Q14.0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J138&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40007]
[{"$nulls":5},"AI1",null,null,null,"AI1配置",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL139,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL139,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"AI通道",null,"01","AI1配置","AI通道-AI1配置",{"$f":"VLOOKUP(AH139,List!$B$3:$D$445,2,FALSE)&AJ139&\"_\"&VLOOKUP(AK139,List!$K$2:$M$447,2,FALSE)","v":"Device01_MO1"},{"$f":"_xlfn.IFNA(\"L\"&AM139&\" \"&\"AT%Q2.0\"&\" \"&\":BYTE;\"&\" \"&\"(*\"&J139&\"*)\",\" \")","v":"LDevice01_MO1 AT%Q2.0 :BYTE; (*AI1配置*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN139,SEARCH(\"AT%\",AN139),,REPT(\" \",25-SEARCH(\"AT%\",AN139))),SEARCH(\":\",REPLACE(AN139,SEARCH(\"AT%\",AN139),,REPT(\" \",25-SEARCH(\"AT%\",AN139)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN139,SEARCH(\"AT%\",AN139),,REPT(\" \",25-SEARCH(\"AT%\",AN139)))))),\" \")","v":"LDevice01_MO1           AT%Q2.0        :BYTE; (*AI1配置*)"},null,"Device01_MO1","AI1配置",{"$f":"AS135-3","v":40001}]
[".",{"$nulls":4},"AI2",null,null,null,"AI2配置",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL140,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL140,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"AI通道",null,"01","AI2配置","AI通道-AI2配置",{"$f":"VLOOKUP(AH140,List!$B$3:$D$445,2,FALSE)&AJ140&\"_\"&VLOOKUP(AK140,List!$K$2:$M$447,2,FALSE)","v":"Device01_MO2"},{"$f":"_xlfn.IFNA(\"L\"&AM140&\" \"&\"AT%Q3.0\"&\" \"&\":BYTE;\"&\" \"&\"(*\"&J140&\"*)\",\" \")","v":"LDevice01_MO2 AT%Q3.0 :BYTE; (*AI2配置*)"},"LDevice01_MO2           AT%Q3.0        :BYTE; (*AI2配置*)",null,"Device01_MO2","AI2配置",{"$f":"AS139","v":40001}]
[{"$nulls":5},"AI3",null,null,null,"AI3配置",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL141,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL141,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"AI通道",null,"01","AI3配置","AI通道-AI3配置",{"$f":"VLOOKUP(AH141,List!$B$3:$D$445,2,FALSE)&AJ141&\"_\"&VLOOKUP(AK141,List!$K$2:$M$447,2,FALSE)","v":"Device01_MO3"},{"$f":"_xlfn.IFNA(\"L\"&AM141&\" \"&\"AT%Q4.0\"&\" \"&\":BYTE;\"&\" \"&\"(*\"&J141&\"*)\",\" \")","v":"LDevice01_MO3 AT%Q4.0 :BYTE; (*AI3配置*)"},"LDevice01_MO3           AT%Q4.0        :BYTE; (*AI3配置*)",null,"Device01_MO3","AI3配置",{"$f":"AS135-2","v":40002}]
[{"$nulls":5},"AI4",null,null,null,"AI4配置",{"$nulls":16},{"$f":"IF(AI142=\"\",\"\",AI142)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL142,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL142,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"AI通道",null,"01","AI4配置",{"$f":"AH142&\"-\"&AK142","v":"AI通道-AI4配置"},{"$f":"VLOOKUP(AH142,List!$B$3:$D$445,2,FALSE)&AJ142&\"_\"&VLOOKUP(AK142,List!$K$2:$M$447,2,FALSE)","v":"Device01_MO4"},{"$f":"_xlfn.IFNA(\"L\"&AM142&\" \"&\"AT%Q5.0\"&\" \"&\":BYTE;\"&\" \"&\"(*\"&J142&\"*)\",\" \")","v":"LDevice01_MO4 AT%Q5.0 :BYTE; (*AI4配置*)"},"LDevice01_MO4           AT%Q5.0        :BYTE; (*AI4配置*)",null,"Device01_MO4",{"$f":"J142","v":"AI4配置"},{"$f":"AS141","v":40002}]
[{"$nulls":5},"AI5",null,null,null,"AI5配置",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL143,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL143,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"AI通道",null,"01","AI5配置","AI通道-AI5配置",{"$f":"VLOOKUP(AH143,List!$B$3:$D$445,2,FALSE)&AJ143&\"_\"&VLOOKUP(AK143,List!$K$2:$M$447,2,FALSE)","v":"Device01_MO5"},{"$f":"_xlfn.IFNA(\"L\"&AM143&\" \"&\"AT%Q6.0\"&\" \"&\":BYTE;\"&\" \"&\"(*\"&J143&\"*)\",\" \")","v":"LDevice01_MO5 AT%Q6.0 :BYTE; (*AI5配置*)"},"LDevice01_MO5           AT%Q6.0        :BYTE; (*AI5配置*)",null,"Device01_MO5","AI5配置",{"$f":"AS135-1","v":40003}]
[".",{"$nulls":4},"AI6",null,null,null,"AI6配置",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL144,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL144,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"AI通道",null,"01","AI6配置","AI通道-AI6配置",{"$f":"VLOOKUP(AH144,List!$B$3:$D$445,2,FALSE)&AJ144&\"_\"&VLOOKUP(AK144,List!$K$2:$M$447,2,FALSE)","v":"Device01_MO6"},{"$f":"_xlfn.IFNA(\"L\"&AM144&\" \"&\"AT%Q7.0\"&\" \"&\":BYTE;\"&\" \"&\"(*\"&J144&\"*)\",\" \")","v":"LDevice01_MO6 AT%Q7.0 :BYTE; (*AI6配置*)"},"LDevice01_MO6           AT%Q7.0        :BYTE; (*AI6配置*)",null,"Device01_MO6","AI6配置",{"$f":"AS143","v":40003}]
[null,"EXC-61610-IO",{"$nulls":38},{"$f":"\"(* \"&B145&\"地址: \"&B147&\" *)\"","v":"(* EXC-61610-IO地址: 1 *)"}]
[null,"addr",{"$f":"B145","v":"EXC-61610-IO"},null,null,"DI1",null,1,"COM",{"$f":"AH146&AA146&\"-\"&AK146","v":"排风机EAF-B1-01-运行状态"},{"$nulls":16},{"$f":"IF(AI146=\"\",\"\",AI146)","v":"EAF-B1-01"},{"$f":"_xlfn.IFNA(VLOOKUP(AL146,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL146,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"排风机","EAF-B1-01","B1A01","运行状态",{"$f":"AH146&\"-\"&AK146","v":"排风机-运行状态"},{"$f":"VLOOKUP(AH146,List!$B$3:$D$445,2,FALSE)&AJ146&\"_\"&VLOOKUP(AK146,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM146&\" \"&\"AT%I\"&B147*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J146&\"*)\",\" \")","v":"LEAFB1A01_R AT%I16.0 :BOOL; (*排风机EAF-B1-01-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN146,SEARCH(\"AT%\",AN146),,REPT(\" \",25-SEARCH(\"AT%\",AN146))),SEARCH(\":\",REPLACE(AN146,SEARCH(\"AT%\",AN146),,REPT(\" \",25-SEARCH(\"AT%\",AN146)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN146,SEARCH(\"AT%\",AN146),,REPT(\" \",25-SEARCH(\"AT%\",AN146)))))),\" \")","v":"LEAFB1A01_R             AT%I16.0       :BOOL; (*排风机EAF-B1-01-运行状态*)"},null,"EAFB1A01_R",{"$f":"J146","v":"排风机EAF-B1-01-运行状态"},{"$f":"10000+($B147*16*8+H146-1)","v":10128}]
[null,1,null,null,null,"DI2",null,2,null,"排风机EAF-B1-01-故障状态",{"$nulls":16},{"$f":"IF(AI147=\"\",\"\",AI147)","v":"EAF-B1-01"},{"$f":"_xlfn.IFNA(VLOOKUP(AL147,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL147,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"排风机","EAF-B1-01","B1A01","故障状态",{"$f":"AH147&\"-\"&AK147","v":"排风机-故障状态"},{"$f":"VLOOKUP(AH147,List!$B$3:$D$445,2,FALSE)&AJ147&\"_\"&VLOOKUP(AK147,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM147&\" \"&\"AT%I\"&B147*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J147&\"*)\",\" \")","v":"LEAFB1A01_F AT%I16.1 :BOOL; (*排风机EAF-B1-01-故障状态*)"},"LEAFB1A01_F             AT%I16.1       :BOOL; (*排风机EAF-B1-01-故障状态*)",null,"EAFB1A01_F",{"$f":"J147","v":"排风机EAF-B1-01-故障状态"},{"$f":"AS146+1","v":10129}]
[null,"kbs",null,null,null,"DI3",null,3,null,"排风机EAF-B1-01-自动状态",{"$nulls":16},"EAF-B1-01",{"$f":"_xlfn.IFNA(VLOOKUP(AL148,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL148,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"排风机","EAF-B1-01","B1A01","自动状态","排风机-自动状态",{"$f":"VLOOKUP(AH148,List!$B$3:$D$445,2,FALSE)&AJ148&\"_\"&VLOOKUP(AK148,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM148&\" \"&\"AT%I\"&B147*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J148&\"*)\",\" \")","v":"LEAFB1A01_A AT%I16.2 :BOOL; (*排风机EAF-B1-01-自动状态*)"},"LEAFB1A01_A             AT%I16.2       :BOOL; (*排风机EAF-B1-01-自动状态*)",null,"EAFB1A01_A","排风机EAF-B1-01-自动状态",{"$f":"AS147+1","v":10130}]
[null,50,null,null,null,"DI4",null,4,"COM","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL149,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL149,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH149,List!$B$3:$D$445,2,FALSE)&AJ149&\"_\"&VLOOKUP(AK149,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM149&\" \"&\"AT%I\"&B147*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J149&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10131]
[null," ",null,null,null,"DI5",null,5,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL150,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL150,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH150,List!$B$3:$D$445,2,FALSE)&AJ150&\"_\"&VLOOKUP(AK150,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM150&\" \"&\"AT%I\"&B147*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J150&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10132]
[{"$nulls":5},"DI6",null,6,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL151,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL151,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH151,List!$B$3:$D$445,2,FALSE)&AJ151&\"_\"&VLOOKUP(AK151,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM151&\" \"&\"AT%I\"&B147*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J151&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10133]
[{"$nulls":5},"DI7",null,7,"COM","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL152,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL152,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH152,List!$B$3:$D$445,2,FALSE)&AJ152&\"_\"&VLOOKUP(AK152,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM152&\" \"&\"AT%I\"&B147*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J152&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10134]
[".",{"$nulls":4},"DI8",null,8,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL153,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL153,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH153,List!$B$3:$D$445,2,FALSE)&AJ153&\"_\"&VLOOKUP(AK153,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM153&\" \"&\"AT%I\"&B147*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J153&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10135]
[{"$nulls":5},"DI9",null,9,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL154,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL154,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH154,List!$B$3:$D$445,2,FALSE)&AJ154&\"_\"&VLOOKUP(AK154,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM154&\" \"&\"AT%I\"&(B147*16+1)&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J154&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"10000+(($B147*16+1)*8+H154-9)","v":10136}]
[{"$nulls":5},"DI10",null,10,"COM","-",{"$nulls":16},{"$f":"IF(AI155=\"\",\"\",AI155)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL155,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL155,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH155&\"-\"&AK155","v":"-"},{"$f":"VLOOKUP(AH155,List!$B$3:$D$445,2,FALSE)&AJ155&\"_\"&VLOOKUP(AK155,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM155&\" \"&\"AT%I\"&(B147*16+1)&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J155&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J155","v":"-"},{"$f":"AS154+1","v":10137}]
[{"$nulls":5},"DI11",null,11,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL156,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL156,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH156,List!$B$3:$D$445,2,FALSE)&AJ156&\"_\"&VLOOKUP(AK156,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM156&\" \"&\"AT%I\"&(B147*16+1)&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J156&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS155+1","v":10138}]
[{"$nulls":5},"DI12",null,12,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL157,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL157,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH157,List!$B$3:$D$445,2,FALSE)&AJ157&\"_\"&VLOOKUP(AK157,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM157&\" \"&\"AT%I\"&(B147*16+1)&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J157&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10139]
[{"$nulls":5},"DO1",null,"1+","1-","排风机EAF-B1-01-启停控制",{"$nulls":16},"EAF-B1-01",{"$f":"_xlfn.IFNA(VLOOKUP(AL158,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL158,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"排风机","EAF-B1-01","B1A01","启停控制","排风机-启停控制",{"$f":"VLOOKUP(AH158,List!$B$3:$D$445,2,FALSE)&AJ158&\"_\"&VLOOKUP(AK158,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM158&\" \"&\"AT%Q\"&B147*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J158&\"*)\",\" \")","v":"LEAFB1A01_C AT%Q16.0 :BOOL; (*排风机EAF-B1-01-启停控制*)"},"LEAFB1A01_C             AT%Q16.0       :BOOL; (*排风机EAF-B1-01-启停控制*)",null,"EAFB1A01_C","排风机EAF-B1-01-启停控制",{"$f":"($B147*16*8+LEFT(H158,1)-1)","v":128}]
[{"$nulls":5},"DO2",null,"2+","2-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL159,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL159,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH159,List!$B$3:$D$445,2,FALSE)&AJ159&\"_\"&VLOOKUP(AK159,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM159&\" \"&\"AT%Q\"&B147*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J159&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS158+1","v":129}]
[{"$nulls":5},"DO3",null,"3+","3-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL160,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL160,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH160,List!$B$3:$D$445,2,FALSE)&AJ160&\"_\"&VLOOKUP(AK160,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM160&\" \"&\"AT%Q\"&B147*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J160&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",130]
[{"$nulls":5},"DO4",null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL161,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL161,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH161,List!$B$3:$D$445,2,FALSE)&AJ161&\"_\"&VLOOKUP(AK161,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM161&\" \"&\"AT%Q\"&B147*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J161&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",131]
[{"$nulls":5},"DO5",null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL162,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL162,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH162,List!$B$3:$D$445,2,FALSE)&AJ162&\"_\"&VLOOKUP(AK162,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM162&\" \"&\"AT%Q\"&B147*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J162&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",132]
[{"$nulls":5},"DO6",null,"6+","6-","-",{"$nulls":16},{"$f":"IF(AI163=\"\",\"\",AI163)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL163,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL163,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH163&\"-\"&AK163","v":"-"},{"$f":"VLOOKUP(AH163,List!$B$3:$D$445,2,FALSE)&AJ163&\"_\"&VLOOKUP(AK163,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM163&\" \"&\"AT%Q\"&B147*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J163&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J163","v":"-"},133]
[{"$nulls":5},"AI1",null,1,"0\nV","室内环境状态CO-1-一氧化碳浓度状态",{"$nulls":16},"CO-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL164,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL164,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"室内环境状态","CO-1","B1A01","一氧化碳浓度状态","室内环境状态-一氧化碳浓度状态",{"$f":"VLOOKUP(AH164,List!$B$3:$D$445,2,FALSE)&AJ164&\"_\"&VLOOKUP(AK164,List!$K$2:$M$447,2,FALSE)","v":"IESB1A01_CO"},{"$f":"_xlfn.IFNA(\"L\"&AM164&\" \"&\"AT%I\"&(B147*16+2)&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J164&\"*)\",\" \")","v":"LIESB1A01_CO AT%I18.0 :INT ; (*室内环境状态CO-1-一氧化碳浓度状态*)"},"LIESB1A01_CO            AT%I18.0       :INT ; (*室内环境状态CO-1-一氧化碳浓度状态*)",null,"IESB1A01_CO","室内环境状态CO-1-一氧化碳浓度状态",{"$f":"30000+($B147*8+LEFT(H164,1))","v":30009}]
[{"$nulls":5},"AI2",null,2,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL165,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL165,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH165,List!$B$3:$D$445,2,FALSE)&AJ165&\"_\"&VLOOKUP(AK165,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM165&\" \"&\"AT%I\"&(B147*16+4)&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J165&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS164+1","v":30010}]
[{"$nulls":5},"AI3",null,3,"0\nV","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL166,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL166,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH166,List!$B$3:$D$445,2,FALSE)&AJ166&\"_\"&VLOOKUP(AK166,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM166&\" \"&\"AT%I\"&(B147*16+6)&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J166&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30011]
[{"$nulls":5},"AI4",null,4,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL167,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL167,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH167,List!$B$3:$D$445,2,FALSE)&AJ167&\"_\"&VLOOKUP(AK167,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM167&\" \"&\"AT%I\"&(B147*16+8)&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J167&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30012]
[{"$nulls":5},"AI5",null,5,"0\nV","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL168,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL168,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH168,List!$B$3:$D$445,2,FALSE)&AJ168&\"_\"&VLOOKUP(AK168,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM168&\" \"&\"AT%I\"&(B147*16+10)&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J168&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30013]
[".",{"$nulls":4},"AI6",null,6,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL169,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL169,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH169,List!$B$3:$D$445,2,FALSE)&AJ169&\"_\"&VLOOKUP(AK169,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM169&\" \"&\"AT%I\"&(B147*16+12)&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J169&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30014]
[{"$nulls":5},"AO1",null,"1+","1-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL170,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL170,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH170,List!$B$3:$D$445,2,FALSE)&AJ170&\"_\"&VLOOKUP(AK170,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM170&\" \"&\"AT%Q\"&(B147*16+8)&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J170&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"40000+($B147*8+LEFT(H170,1)+3)","v":40012}]
[{"$nulls":5},"AO2",null,"2+","2-","-",{"$nulls":16},{"$f":"IF(AI171=\"\",\"\",AI171)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL171,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL171,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH171&\"-\"&AK171","v":"-"},{"$f":"VLOOKUP(AH171,List!$B$3:$D$445,2,FALSE)&AJ171&\"_\"&VLOOKUP(AK171,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM171&\" \"&\"AT%Q\"&(B147*16+10)&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J171&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J171","v":"-"},{"$f":"AS170+1","v":40013}]
[{"$nulls":5},"AO3",null,"3+","3-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL172,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL172,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH172,List!$B$3:$D$445,2,FALSE)&AJ172&\"_\"&VLOOKUP(AK172,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM172&\" \"&\"AT%Q\"&(B147*16+12)&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J172&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS171+1","v":40014}]
[{"$nulls":5},"AO4",null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL173,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL173,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH173,List!$B$3:$D$445,2,FALSE)&AJ173&\"_\"&VLOOKUP(AK173,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM173&\" \"&\"AT%Q\"&(B147*16+14)&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J173&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40015]
[{"$nulls":5},"AI1",null,null,null,"AI1配置",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL174,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL174,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"AI通道",null,"02","AI1配置","AI通道-AI1配置",{"$f":"VLOOKUP(AH174,List!$B$3:$D$445,2,FALSE)&AJ174&\"_\"&VLOOKUP(AK174,List!$K$2:$M$447,2,FALSE)","v":"Device02_MO1"},{"$f":"_xlfn.IFNA(\"L\"&AM174&\" \"&\"AT%Q\"&(B147*16+2)&\".0\"&\" \"&\":BYTE;\"&\" \"&\"(*\"&J174&\"*)\",\" \")","v":"LDevice02_MO1 AT%Q18.0 :BYTE; (*AI1配置*)"},"LDevice02_MO1           AT%Q18.0       :BYTE; (*AI1配置*)",null,"Device02_MO1","AI1配置",{"$f":"AS170-3","v":40009}]
[".",{"$nulls":4},"AI2",null,null,null,"AI2配置",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL175,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL175,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"AI通道",null,"02","AI2配置","AI通道-AI2配置",{"$f":"VLOOKUP(AH175,List!$B$3:$D$445,2,FALSE)&AJ175&\"_\"&VLOOKUP(AK175,List!$K$2:$M$447,2,FALSE)","v":"Device02_MO2"},{"$f":"_xlfn.IFNA(\"L\"&AM175&\" \"&\"AT%Q\"&(B147*16+3)&\".0\"&\" \"&\":BYTE;\"&\" \"&\"(*\"&J175&\"*)\",\" \")","v":"LDevice02_MO2 AT%Q19.0 :BYTE; (*AI2配置*)"},"LDevice02_MO2           AT%Q19.0       :BYTE; (*AI2配置*)",null,{"$f":"AM175","v":"Device02_MO2"},"AI2配置",{"$f":"AS174","v":40009}]
[{"$nulls":5},"AI3",null,null,null,"AI3配置",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL176,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL176,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"AI通道",null,"02","AI3配置","AI通道-AI3配置",{"$f":"VLOOKUP(AH176,List!$B$3:$D$445,2,FALSE)&AJ176&\"_\"&VLOOKUP(AK176,List!$K$2:$M$447,2,FALSE)","v":"Device02_MO3"},{"$f":"_xlfn.IFNA(\"L\"&AM176&\" \"&\"AT%Q\"&(B147*16+4)&\".0\"&\" \"&\":BYTE;\"&\" \"&\"(*\"&J176&\"*)\",\" \")","v":"LDevice02_MO3 AT%Q20.0 :BYTE; (*AI3配置*)"},"LDevice02_MO3           AT%Q20.0       :BYTE; (*AI3配置*)",null,"Device02_MO3","AI3配置",{"$f":"AS170-2","v":40010}]
[{"$nulls":5},"AI4",null,null,null,"AI4配置",{"$nulls":16},{"$f":"IF(AI177=\"\",\"\",AI177)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL177,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL177,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"AI通道",null,"02","AI4配置",{"$f":"AH177&\"-\"&AK177","v":"AI通道-AI4配置"},{"$f":"VLOOKUP(AH177,List!$B$3:$D$445,2,FALSE)&AJ177&\"_\"&VLOOKUP(AK177,List!$K$2:$M$447,2,FALSE)","v":"Device02_MO4"},{"$f":"_xlfn.IFNA(\"L\"&AM177&\" \"&\"AT%Q\"&(B147*16+5)&\".0\"&\" \"&\":BYTE;\"&\" \"&\"(*\"&J177&\"*)\",\" \")","v":"LDevice02_MO4 AT%Q21.0 :BYTE; (*AI4配置*)"},"LDevice02_MO4           AT%Q21.0       :BYTE; (*AI4配置*)",null,"Device02_MO4",{"$f":"J177","v":"AI4配置"},{"$f":"AS176","v":40010}]
[{"$nulls":5},"AI5",null,null,null,"AI5配置",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL178,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL178,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"AI通道",null,"02","AI5配置","AI通道-AI5配置",{"$f":"VLOOKUP(AH178,List!$B$3:$D$445,2,FALSE)&AJ178&\"_\"&VLOOKUP(AK178,List!$K$2:$M$447,2,FALSE)","v":"Device02_MO5"},{"$f":"_xlfn.IFNA(\"L\"&AM178&\" \"&\"AT%Q\"&(B147*16+6)&\".0\"&\" \"&\":BYTE;\"&\" \"&\"(*\"&J178&\"*)\",\" \")","v":"LDevice02_MO5 AT%Q22.0 :BYTE; (*AI5配置*)"},"LDevice02_MO5           AT%Q22.0       :BYTE; (*AI5配置*)",null,"Device02_MO5","AI5配置",{"$f":"AS170-1","v":40011}]
[".",{"$nulls":4},"AI6",null,null,null,"AI6配置",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL179,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL179,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"AI通道",null,"02","AI6配置","AI通道-AI6配置",{"$f":"VLOOKUP(AH179,List!$B$3:$D$445,2,FALSE)&AJ179&\"_\"&VLOOKUP(AK179,List!$K$2:$M$447,2,FALSE)","v":"Device02_MO6"},{"$f":"_xlfn.IFNA(\"L\"&AM179&\" \"&\"AT%Q\"&(B147*16+7)&\".0\"&\" \"&\":BYTE;\"&\" \"&\"(*\"&J179&\"*)\",\" \")","v":"LDevice02_MO6 AT%Q23.0 :BYTE; (*AI6配置*)"},"LDevice02_MO6           AT%Q23.0       :BYTE; (*AI6配置*)",null,"Device02_MO6","AI6配置",{"$f":"AS178","v":40011}]
[null,"EXC-61608",{"$nulls":38},{"$f":"\"(* \"&B180&\"地址: \"&B182&\" *)\"","v":"(* EXC-61608地址: 0 *)"}]
[null,"addr",{"$f":"B180","v":"EXC-61608"},null,null,"DI1",null,1,"COM",{"$f":"AH181&AA181&\"-\"&AK181","v":"-"},{"$nulls":16},{"$f":"IF(AI181=\"\",\"\",AI181)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL181,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL181,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH181&\"-\"&AK181","v":"-"},{"$f":"VLOOKUP(AH181,List!$B$3:$D$445,2,FALSE)&AJ181&\"_\"&VLOOKUP(AK181,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM181&\" \"&\"AT%I0.0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J181&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN181,SEARCH(\"AT%\",AN181),,REPT(\" \",25-SEARCH(\"AT%\",AN181))),SEARCH(\":\",REPLACE(AN181,SEARCH(\"AT%\",AN181),,REPT(\" \",25-SEARCH(\"AT%\",AN181)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN181,SEARCH(\"AT%\",AN181),,REPT(\" \",25-SEARCH(\"AT%\",AN181)))))),\" \")","v":" "},null,{"$f":"AM181","v":{"$error":"#N/A"}},{"$f":"J181","v":"-"},{"$f":"10000+($B182*16*8+H181-1)","v":10000}]
[null,0,null,null,null,"DI2",null,2,null,"-",{"$nulls":16},{"$f":"IF(AI182=\"\",\"\",AI182)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL182,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL182,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH182,List!$B$3:$D$445,2,FALSE)&AJ182&\"_\"&VLOOKUP(AK182,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM182&\" \"&\"AT%I0.1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J182&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J182","v":"-"},{"$f":"AS181+1","v":10001}]
[null,"kbs",null,null,null,"DI3",null,3,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL183,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL183,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH183,List!$B$3:$D$445,2,FALSE)&AJ183&\"_\"&VLOOKUP(AK183,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM183&\" \"&\"AT%I0.2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J183&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS182+1","v":10002}]
[null,50,null,null,null,"DI4",null,4,"COM","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL184,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL184,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH184,List!$B$3:$D$445,2,FALSE)&AJ184&\"_\"&VLOOKUP(AK184,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM184&\" \"&\"AT%I0.3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J184&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10003]
[null," ",null,null,null,"DI5",null,5,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL185,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL185,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH185,List!$B$3:$D$445,2,FALSE)&AJ185&\"_\"&VLOOKUP(AK185,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM185&\" \"&\"AT%I0.4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J185&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10004]
[{"$nulls":5},"DI6",null,6,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL186,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL186,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH186,List!$B$3:$D$445,2,FALSE)&AJ186&\"_\"&VLOOKUP(AK186,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM186&\" \"&\"AT%I0.5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J186&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10005]
[{"$nulls":5},"DI7",null,7,"COM","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL187,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL187,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH187,List!$B$3:$D$445,2,FALSE)&AJ187&\"_\"&VLOOKUP(AK187,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM187&\" \"&\"AT%I0.6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J187&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10006]
[".",{"$nulls":4},"DI8",null,8,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL188,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL188,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH188,List!$B$3:$D$445,2,FALSE)&AJ188&\"_\"&VLOOKUP(AK188,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM188&\" \"&\"AT%I0.7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J188&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10007]
[{"$nulls":5},"DI9",null,9,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL189,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL189,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH189,List!$B$3:$D$445,2,FALSE)&AJ189&\"_\"&VLOOKUP(AK189,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM189&\" \"&\"AT%I1.0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J189&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"10000+(($B182*16+1)*8+H189-9)","v":10008}]
[{"$nulls":5},"DI10",null,10,"COM","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL190,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL190,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH190,List!$B$3:$D$445,2,FALSE)&AJ190&\"_\"&VLOOKUP(AK190,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM190&\" \"&\"AT%I1.1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J190&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS189+1","v":10009}]
[{"$nulls":5},"DI11",null,11,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL191,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL191,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH191,List!$B$3:$D$445,2,FALSE)&AJ191&\"_\"&VLOOKUP(AK191,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM191&\" \"&\"AT%I1.2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J191&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS190+1","v":10010}]
[{"$nulls":5},"DI12",null,12,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL192,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL192,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH192,List!$B$3:$D$445,2,FALSE)&AJ192&\"_\"&VLOOKUP(AK192,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM192&\" \"&\"AT%I1.3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J192&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10011]
[{"$nulls":5},"DI13",null,13,"COM","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL193,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL193,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH193,List!$B$3:$D$445,2,FALSE)&AJ193&\"_\"&VLOOKUP(AK193,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM193&\" \"&\"AT%I1.4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J193&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10012]
[{"$nulls":5},"DI14",null,14,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL194,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL194,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH194,List!$B$3:$D$445,2,FALSE)&AJ194&\"_\"&VLOOKUP(AK194,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM194&\" \"&\"AT%I1.5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J194&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10013]
[{"$nulls":5},"DI15",null,15,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL195,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL195,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH195,List!$B$3:$D$445,2,FALSE)&AJ195&\"_\"&VLOOKUP(AK195,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM195&\" \"&\"AT%I1.6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J195&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10014]
[{"$nulls":5},"DI16",null,16,"COM","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL196,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL196,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH196,List!$B$3:$D$445,2,FALSE)&AJ196&\"_\"&VLOOKUP(AK196,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM196&\" \"&\"AT%I1.7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J196&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10015]
[{"$nulls":5},"DI17",null,17,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL197,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL197,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH197,List!$B$3:$D$445,2,FALSE)&AJ197&\"_\"&VLOOKUP(AK197,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM197&\" \"&\"AT%I2.0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J197&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10016]
[{"$nulls":5},"DI18",null,18,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL198,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL198,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH198,List!$B$3:$D$445,2,FALSE)&AJ198&\"_\"&VLOOKUP(AK198,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM198&\" \"&\"AT%I2.1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J198&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10017]
[{"$nulls":5},"DI19",null,19,"COM","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL199,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL199,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH199,List!$B$3:$D$445,2,FALSE)&AJ199&\"_\"&VLOOKUP(AK199,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM199&\" \"&\"AT%I2.2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J199&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10018]
[{"$nulls":5},"DI20",null,20,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL200,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL200,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH200,List!$B$3:$D$445,2,FALSE)&AJ200&\"_\"&VLOOKUP(AK200,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM200&\" \"&\"AT%I2.3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J200&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10019]
[{"$nulls":9},"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL201,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL201,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH201,List!$B$3:$D$445,2,FALSE)&AJ201&\"_\"&VLOOKUP(AK201,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM201&\" \"&\"AT%I2.4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J201&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-"]
[{"$nulls":5},"DO1",null,"1+","1-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL202,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL202,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH202,List!$B$3:$D$445,2,FALSE)&AJ202&\"_\"&VLOOKUP(AK202,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM202&\" \"&\"AT%Q0.0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J202&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"($B191*16*8+LEFT(H202,1)-1)","v":0}]
[{"$nulls":5},"DO2",null,"2+","2-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL203,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL203,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH203,List!$B$3:$D$445,2,FALSE)&AJ203&\"_\"&VLOOKUP(AK203,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM203&\" \"&\"AT%Q0.1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J203&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS202+1","v":1}]
[{"$nulls":5},"DO3",null,"3+","3-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL204,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL204,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH204,List!$B$3:$D$445,2,FALSE)&AJ204&\"_\"&VLOOKUP(AK204,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM204&\" \"&\"AT%Q0.2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J204&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2]
[{"$nulls":5},"DO4",null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL205,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL205,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH205,List!$B$3:$D$445,2,FALSE)&AJ205&\"_\"&VLOOKUP(AK205,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM205&\" \"&\"AT%Q0.3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J205&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",3]
[{"$nulls":5},"DO5",null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL206,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL206,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH206,List!$B$3:$D$445,2,FALSE)&AJ206&\"_\"&VLOOKUP(AK206,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM206&\" \"&\"AT%Q0.4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J206&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",4]
[{"$nulls":5},"DO6",null,"6+","6-","-",{"$nulls":16},{"$f":"IF(AI207=\"\",\"\",AI207)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL207,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL207,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH207,List!$B$3:$D$445,2,FALSE)&AJ207&\"_\"&VLOOKUP(AK207,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM207&\" \"&\"AT%Q0.5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J207&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",5]
[{"$nulls":5},"DO7",null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL208,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL208,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH208,List!$B$3:$D$445,2,FALSE)&AJ208&\"_\"&VLOOKUP(AK208,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM208&\" \"&\"AT%Q0.6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J208&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",6]
[{"$nulls":5},"DO8",null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL209,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL209,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH209,List!$B$3:$D$445,2,FALSE)&AJ209&\"_\"&VLOOKUP(AK209,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM209&\" \"&\"AT%Q0.7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J209&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",7]
[null,"EXC-61608-IO",{"$nulls":38},{"$f":"\"(* \"&B210&\"地址: \"&B212&\" *)\"","v":"(* EXC-61608-IO地址: 4 *)"}]
[null,"addr",{"$f":"B210","v":"EXC-61608-IO"},null,null,"DI1",null,1,"COM",{"$f":"AH211&AA211&\"-\"&AK211","v":"-"},{"$nulls":16},{"$f":"IF(AI211=\"\",\"\",AI211)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL211,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL211,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH211&\"-\"&AK211","v":"-"},{"$f":"VLOOKUP(AH211,List!$B$3:$D$445,2,FALSE)&AJ211&\"_\"&VLOOKUP(AK211,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM211&\" \"&\"AT%I\"&B212*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J211&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN211,SEARCH(\"AT%\",AN211),,REPT(\" \",25-SEARCH(\"AT%\",AN211))),SEARCH(\":\",REPLACE(AN211,SEARCH(\"AT%\",AN211),,REPT(\" \",25-SEARCH(\"AT%\",AN211)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN211,SEARCH(\"AT%\",AN211),,REPT(\" \",25-SEARCH(\"AT%\",AN211)))))),\" \")","v":" "},null,{"$error":"#N/A"},{"$f":"J211","v":"-"},{"$f":"10000+($B212*16*8+H211-1)","v":10512}]
[null,4,null,null,null,"DI2",null,2,null,"-",{"$nulls":16},{"$f":"IF(AI212=\"\",\"\",AI212)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL212,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL212,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH212,List!$B$3:$D$445,2,FALSE)&AJ212&\"_\"&VLOOKUP(AK212,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM212&\" \"&\"AT%I\"&B212*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J212&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J212","v":"-"},{"$f":"AS211+1","v":10513}]
[null,"kbs",null,null,null,"DI3",null,3,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL213,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL213,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH213,List!$B$3:$D$445,2,FALSE)&AJ213&\"_\"&VLOOKUP(AK213,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM213&\" \"&\"AT%I\"&B212*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J213&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS212+1","v":10514}]
[null,50,null,null,null,"DI4",null,4,"COM","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL214,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL214,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH214,List!$B$3:$D$445,2,FALSE)&AJ214&\"_\"&VLOOKUP(AK214,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM214&\" \"&\"AT%I\"&B212*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J214&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10515]
[null," ",null,null,null,"DI5",null,5,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL215,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL215,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH215,List!$B$3:$D$445,2,FALSE)&AJ215&\"_\"&VLOOKUP(AK215,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM215&\" \"&\"AT%I\"&B212*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J215&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10516]
[{"$nulls":5},"DI6",null,6,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL216,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL216,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH216,List!$B$3:$D$445,2,FALSE)&AJ216&\"_\"&VLOOKUP(AK216,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM216&\" \"&\"AT%I\"&B212*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J216&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10517]
[{"$nulls":5},"DI7",null,7,"COM","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL217,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL217,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH217,List!$B$3:$D$445,2,FALSE)&AJ217&\"_\"&VLOOKUP(AK217,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM217&\" \"&\"AT%I\"&B212*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J217&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10518]
[".",{"$nulls":4},"DI8",null,8,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL218,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL218,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH218,List!$B$3:$D$445,2,FALSE)&AJ218&\"_\"&VLOOKUP(AK218,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM218&\" \"&\"AT%I\"&B212*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J218&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10519]
[{"$nulls":5},"DI9",null,9,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL219,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL219,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH219,List!$B$3:$D$445,2,FALSE)&AJ219&\"_\"&VLOOKUP(AK219,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM219&\" \"&\"AT%I\"&(B212*16+1)&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J219&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"10000+(($B212*16+1)*8+H219-9)","v":10520}]
[{"$nulls":5},"DI10",null,10,"COM","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL220,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL220,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH220,List!$B$3:$D$445,2,FALSE)&AJ220&\"_\"&VLOOKUP(AK220,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM220&\" \"&\"AT%I\"&(B212*16+1)&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J220&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS219+1","v":10521}]
[{"$nulls":5},"DI11",null,11,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL221,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL221,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH221,List!$B$3:$D$445,2,FALSE)&AJ221&\"_\"&VLOOKUP(AK221,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM221&\" \"&\"AT%I\"&(B212*16+1)&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J221&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS220+1","v":10522}]
[{"$nulls":5},"DI12",null,12,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL222,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL222,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH222,List!$B$3:$D$445,2,FALSE)&AJ222&\"_\"&VLOOKUP(AK222,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM222&\" \"&\"AT%I\"&(B212*16+1)&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J222&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10523]
[{"$nulls":5},"DI13",null,13,"COM","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL223,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL223,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH223,List!$B$3:$D$445,2,FALSE)&AJ223&\"_\"&VLOOKUP(AK223,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM223&\" \"&\"AT%I\"&(B212*16+1)&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J223&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10524]
[{"$nulls":5},"DI14",null,14,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL224,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL224,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH224,List!$B$3:$D$445,2,FALSE)&AJ224&\"_\"&VLOOKUP(AK224,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM224&\" \"&\"AT%I\"&(B212*16+1)&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J224&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10525]
[{"$nulls":5},"DI15",null,15,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL225,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL225,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH225,List!$B$3:$D$445,2,FALSE)&AJ225&\"_\"&VLOOKUP(AK225,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM225&\" \"&\"AT%I\"&(B212*16+1)&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J225&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10526]
[{"$nulls":5},"DI16",null,16,"COM","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL226,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL226,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH226,List!$B$3:$D$445,2,FALSE)&AJ226&\"_\"&VLOOKUP(AK226,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM226&\" \"&\"AT%I\"&(B212*16+1)&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J226&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10527]
[{"$nulls":5},"DI17",null,17,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL227,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL227,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH227,List!$B$3:$D$445,2,FALSE)&AJ227&\"_\"&VLOOKUP(AK227,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM227&\" \"&\"AT%I\"&(B212*16+2)&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J227&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10528]
[{"$nulls":5},"DI18",null,18,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL228,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL228,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH228,List!$B$3:$D$445,2,FALSE)&AJ228&\"_\"&VLOOKUP(AK228,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM228&\" \"&\"AT%I\"&(B212*16+2)&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J228&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10529]
[{"$nulls":5},"DI19",null,19,"COM","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL229,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL229,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH229,List!$B$3:$D$445,2,FALSE)&AJ229&\"_\"&VLOOKUP(AK229,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM229&\" \"&\"AT%I\"&(B212*16+2)&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J229&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10530]
[{"$nulls":5},"DI20",null,20,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL230,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL230,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH230,List!$B$3:$D$445,2,FALSE)&AJ230&\"_\"&VLOOKUP(AK230,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM230&\" \"&\"AT%I\"&(B212*16+2)&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J230&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10531]
[{"$nulls":9},"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL231,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL231,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH231,List!$B$3:$D$445,2,FALSE)&AJ231&\"_\"&VLOOKUP(AK231,List!$K$2:$M$447,2,0)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM231&\" \"&\"AT%I2.4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J231&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-"]
[{"$nulls":5},"DO1",null,"1+","1-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL232,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL232,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH232,List!$B$3:$D$445,2,FALSE)&AJ232&\"_\"&VLOOKUP(AK232,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM232&\" \"&\"AT%Q\"&B212*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J232&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"($B212*16*8+LEFT(H232,1)-1)","v":512}]
[{"$nulls":5},"DO2",null,"2+","2-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL233,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL233,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH233,List!$B$3:$D$445,2,FALSE)&AJ233&\"_\"&VLOOKUP(AK233,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM233&\" \"&\"AT%Q\"&B212*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J233&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS232+1","v":513}]
[{"$nulls":5},"DO3",null,"3+","3-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL234,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL234,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH234,List!$B$3:$D$445,2,FALSE)&AJ234&\"_\"&VLOOKUP(AK234,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM234&\" \"&\"AT%Q\"&B212*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J234&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",514]
[{"$nulls":5},"DO4",null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL235,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL235,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH235,List!$B$3:$D$445,2,FALSE)&AJ235&\"_\"&VLOOKUP(AK235,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM235&\" \"&\"AT%Q\"&B212*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J235&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",515]
[{"$nulls":5},"DO5",null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL236,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL236,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH236,List!$B$3:$D$445,2,FALSE)&AJ236&\"_\"&VLOOKUP(AK236,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM236&\" \"&\"AT%Q\"&B212*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J236&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",516]
[{"$nulls":5},"DO6",null,"6+","6-","-",{"$nulls":16},{"$f":"IF(AI237=\"\",\"\",AI237)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL237,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL237,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH237,List!$B$3:$D$445,2,FALSE)&AJ237&\"_\"&VLOOKUP(AK237,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM237&\" \"&\"AT%Q\"&B212*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J237&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",517]
[{"$nulls":5},"DO7",null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL238,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL238,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH238,List!$B$3:$D$445,2,FALSE)&AJ238&\"_\"&VLOOKUP(AK238,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM238&\" \"&\"AT%Q\"&B212*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J238&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",518]
[{"$nulls":5},"DO8",null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL239,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL239,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH239,List!$B$3:$D$445,2,FALSE)&AJ239&\"_\"&VLOOKUP(AK239,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM239&\" \"&\"AT%Q\"&B212*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J239&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",519]
[null,"EXC-60006",{"$nulls":38},{"$f":"\"(* \"&B240&\"地址: \"&B242&\" *)\"","v":"(* EXC-60006地址: 3 *)"}]
[null,"addr",{"$f":"B240","v":"EXC-60006"},null,null,"AI1",null,1,"0V",{"$f":"AH241&AA241&\"-\"&AK241","v":"-"},{"$nulls":16},{"$f":"IF(AI241=\"\",\"\",AI241)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL241,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL241,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH241&\"-\"&AK241","v":"-"},{"$f":"VLOOKUP(AH241,List!$B$3:$D$445,2,FALSE)&AJ241&\"_\"&VLOOKUP(AK241,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM241&\" \"&\"AT%I\"&(B242*16)&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J241&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN241,SEARCH(\"AT%\",AN241),,REPT(\" \",25-SEARCH(\"AT%\",AN241))),SEARCH(\":\",REPLACE(AN241,SEARCH(\"AT%\",AN241),,REPT(\" \",25-SEARCH(\"AT%\",AN241)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN241,SEARCH(\"AT%\",AN241),,REPT(\" \",25-SEARCH(\"AT%\",AN241)))))),\" \")","v":" "},null,{"$error":"#N/A"},{"$f":"J241","v":"-"},{"$f":"30000+(B242*8+H241-1)","v":30024}]
[null,3,null,null,null,"AI2",null,2,"0V","-",{"$nulls":16},{"$f":"IF(AI242=\"\",\"\",AI242)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL242,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL242,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH242&\"-\"&AK242","v":"-"},{"$f":"VLOOKUP(AH242,List!$B$3:$D$445,2,FALSE)&AJ242&\"_\"&VLOOKUP(AK242,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM242&\" \"&\"AT%I\"&(B242*16+2)&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J242&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J242","v":"-"},{"$f":"AS241+1","v":30025}]
[null,"kbs",null,null,null,"AI3",null,3,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL243,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL243,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH243,List!$B$3:$D$445,2,FALSE)&AJ243&\"_\"&VLOOKUP(AK243,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM243&\" \"&\"AT%I\"&(B242*16+4)&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J243&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30026]
[null,50,null,null,null,"AI4",null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL244,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL244,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH244,List!$B$3:$D$445,2,FALSE)&AJ244&\"_\"&VLOOKUP(AK244,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM244&\" \"&\"AT%I\"&(B242*16+6)&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J244&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30027]
[null," ",null,null,null,"AI5",null,5,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL245,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL245,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH245,List!$B$3:$D$445,2,FALSE)&AJ245&\"_\"&VLOOKUP(AK245,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM245&\" \"&\"AT%I\"&(B242*16+8)&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J245&\"*)\",\" \")","v":" "}," ",null,{"$f":"AM245","v":{"$error":"#N/A"}},"-",30028]
[{"$nulls":5},"AI6",null,6,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL246,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL246,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH246,List!$B$3:$D$445,2,FALSE)&AJ246&\"_\"&VLOOKUP(AK246,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM246&\" \"&\"AT%I\"&(B242*16+10)&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J246&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30029]
[null,"BRSD_0416",{"$nulls":38},{"$f":"\"(* \"&B247&\"地址: \"&B249&\" *)\"","v":"(* BRSD_0416地址: 1 *)"}]
[null,"addr",null,null,null,1,null,1,2,{"$f":"AH248&AA248&\"-\"&AK248","v":"照明控制箱ALL01-回路开关"},{"$nulls":16},{"$f":"IF(AI248=\"\",\"\",AI248)","v":"ALL01"},{"$f":"_xlfn.IFNA(VLOOKUP(AL248,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL248,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","ALL01","01A01","回路开关",{"$f":"AH248&\"-\"&AK248","v":"照明控制箱-回路开关"},{"$f":"VLOOKUP(AH248,List!$B$3:$D$445,2,FALSE)&AJ248&\"_\"&VLOOKUP(AK248,List!$K$2:$M$447,2,FALSE)","v":"LCB01A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM248&\" \"&\"AT%Q\"&B249*4&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J248&\"*)\",\" \")","v":"LLCB01A01_C AT%Q4.0 :BOOL; (*照明控制箱ALL01-回路开关*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN248,SEARCH(\"AT%\",AN248),,REPT(\" \",25-SEARCH(\"AT%\",AN248))),SEARCH(\":\",REPLACE(AN248,SEARCH(\"AT%\",AN248),,REPT(\" \",25-SEARCH(\"AT%\",AN248)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN248,SEARCH(\"AT%\",AN248),,REPT(\" \",25-SEARCH(\"AT%\",AN248)))))),\" \")","v":"LLCB01A01_C             AT%Q4.0        :BOOL; (*照明控制箱ALL01-回路开关*)"},null,{"$f":"AM248","v":"LCB01A01_C"},{"$f":"J248","v":"照明控制箱ALL01-回路开关"},{"$f":"($B249*4*8+F248-1)","v":32}]
[null,1,null,null,null,2,null,3,4,"照明控制箱ALL01-回路开关",{"$nulls":16},{"$f":"IF(AI249=\"\",\"\",AI249)","v":"ALL01"},{"$f":"_xlfn.IFNA(VLOOKUP(AL249,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL249,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","ALL01","01A02","回路开关",{"$f":"AH249&\"-\"&AK249","v":"照明控制箱-回路开关"},{"$f":"VLOOKUP(AH249,List!$B$3:$D$445,2,FALSE)&AJ249&\"_\"&VLOOKUP(AK249,List!$K$2:$M$447,2,FALSE)","v":"LCB01A02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM249&\" \"&\"AT%Q\"&B249*4&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J249&\"*)\",\" \")","v":"LLCB01A02_C AT%Q4.1 :BOOL; (*照明控制箱ALL01-回路开关*)"},"LLCB01A02_C             AT%Q4.1        :BOOL; (*照明控制箱ALL01-回路开关*)",null,"LCB01A02_C",{"$f":"J249","v":"照明控制箱ALL01-回路开关"},{"$f":"AS248+1","v":33}]
[null,"kbs",null,null,null,3,null,5,6,"照明控制箱ALL01-回路开关",{"$nulls":16},"ALL01",{"$f":"_xlfn.IFNA(VLOOKUP(AL250,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL250,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","ALL01","01A03","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH250,List!$B$3:$D$445,2,FALSE)&AJ250&\"_\"&VLOOKUP(AK250,List!$K$2:$M$447,2,FALSE)","v":"LCB01A03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM250&\" \"&\"AT%Q\"&B249*4&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J250&\"*)\",\" \")","v":"LLCB01A03_C AT%Q4.2 :BOOL; (*照明控制箱ALL01-回路开关*)"},"LLCB01A03_C             AT%Q4.2        :BOOL; (*照明控制箱ALL01-回路开关*)",null,"LCB01A03_C","照明控制箱ALL01-回路开关",{"$f":"AS249+1","v":34}]
[".",50,null,null,null,4,null,7,8,"照明控制箱ALL01-回路开关",{"$nulls":16},"ALL01",{"$f":"_xlfn.IFNA(VLOOKUP(AL251,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL251,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","ALL01","01A04","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH251,List!$B$3:$D$445,2,FALSE)&AJ251&\"_\"&VLOOKUP(AK251,List!$K$2:$M$447,2,FALSE)","v":"LCB01A04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM251&\" \"&\"AT%Q\"&B249*4&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J251&\"*)\",\" \")","v":"LLCB01A04_C AT%Q4.3 :BOOL; (*照明控制箱ALL01-回路开关*)"},"LLCB01A04_C             AT%Q4.3        :BOOL; (*照明控制箱ALL01-回路开关*)",null,"LCB01A04_C","照明控制箱ALL01-回路开关",35]
[null,"BRSD_0816",{"$nulls":38},{"$f":"\"(* \"&B252&\"地址: \"&B254&\" *)\"","v":"(* BRSD_0816地址: 2 *)"}]
[null,"addr",null,null,null,1,null,1,2,{"$f":"AH253&AA253&\"-\"&AK253","v":"照明控制箱宴会厅-回路开关"},{"$nulls":16},{"$f":"IF(AI253=\"\",\"\",AI253)","v":"宴会厅"},{"$f":"_xlfn.IFNA(VLOOKUP(AL253,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL253,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A01","回路开关",{"$f":"AH253&\"-\"&AK253","v":"照明控制箱-回路开关"},{"$f":"VLOOKUP(AH253,List!$B$3:$D$445,2,FALSE)&AJ253&\"_\"&VLOOKUP(AK253,List!$K$2:$M$447,2,FALSE)","v":"LCB01A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM253&\" \"&\"AT%Q\"&B254*4&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J253&\"*)\",\" \")","v":"LLCB01A01_C AT%Q8.0 :BOOL; (*照明控制箱宴会厅-回路开关*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN253,SEARCH(\"AT%\",AN253),,REPT(\" \",25-SEARCH(\"AT%\",AN253))),SEARCH(\":\",REPLACE(AN253,SEARCH(\"AT%\",AN253),,REPT(\" \",25-SEARCH(\"AT%\",AN253)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN253,SEARCH(\"AT%\",AN253),,REPT(\" \",25-SEARCH(\"AT%\",AN253)))))),\" \")","v":"LLCB01A01_C             AT%Q8.0        :BOOL; (*照明控制箱宴会厅-回路开关*)"},null,{"$f":"AM253","v":"LCB01A01_C"},{"$f":"J253","v":"照明控制箱宴会厅-回路开关"},{"$f":"($B254*4*8+F253-1)","v":64}]
[null,2,null,null,null,2,null,3,4,"照明控制箱宴会厅-回路开关",{"$nulls":16},{"$f":"IF(AI254=\"\",\"\",AI254)","v":"宴会厅"},{"$f":"_xlfn.IFNA(VLOOKUP(AL254,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL254,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A02","回路开关",{"$f":"AH254&\"-\"&AK254","v":"照明控制箱-回路开关"},{"$f":"VLOOKUP(AH254,List!$B$3:$D$445,2,FALSE)&AJ254&\"_\"&VLOOKUP(AK254,List!$K$2:$M$447,2,FALSE)","v":"LCB01A02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM254&\" \"&\"AT%Q\"&B254*4&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J254&\"*)\",\" \")","v":"LLCB01A02_C AT%Q8.1 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A02_C             AT%Q8.1        :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A02_C",{"$f":"J254","v":"照明控制箱宴会厅-回路开关"},{"$f":"AS253+1","v":65}]
[null,"kbs",null,null,null,3,null,5,6,"照明控制箱宴会厅-回路开关",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL255,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL255,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A03","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH255,List!$B$3:$D$445,2,FALSE)&AJ255&\"_\"&VLOOKUP(AK255,List!$K$2:$M$447,2,FALSE)","v":"LCB01A03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM255&\" \"&\"AT%Q\"&B254*4&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J255&\"*)\",\" \")","v":"LLCB01A03_C AT%Q8.2 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A03_C             AT%Q8.2        :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A03_C","照明控制箱宴会厅-回路开关",{"$f":"AS254+1","v":66}]
[null,50,null,null,null,4,null,7,8,"照明控制箱宴会厅-回路开关",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL256,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL256,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A04","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH256,List!$B$3:$D$445,2,FALSE)&AJ256&\"_\"&VLOOKUP(AK256,List!$K$2:$M$447,2,FALSE)","v":"LCB01A04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM256&\" \"&\"AT%Q\"&B254*4&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J256&\"*)\",\" \")","v":"LLCB01A04_C AT%Q8.3 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A04_C             AT%Q8.3        :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A04_C","照明控制箱宴会厅-回路开关",67]
[{"$nulls":5},5,null,9,10,"照明控制箱宴会厅-回路开关",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL257,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL257,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A05","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH257,List!$B$3:$D$445,2,FALSE)&AJ257&\"_\"&VLOOKUP(AK257,List!$K$2:$M$447,2,FALSE)","v":"LCB01A05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM257&\" \"&\"AT%Q\"&B254*4&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J257&\"*)\",\" \")","v":"LLCB01A05_C AT%Q8.4 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A05_C             AT%Q8.4        :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A05_C","照明控制箱宴会厅-回路开关",68]
[{"$nulls":5},6,null,11,12,"照明控制箱宴会厅-回路开关",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL258,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL258,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A06","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH258,List!$B$3:$D$445,2,FALSE)&AJ258&\"_\"&VLOOKUP(AK258,List!$K$2:$M$447,2,FALSE)","v":"LCB01A06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM258&\" \"&\"AT%Q\"&B254*4&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J258&\"*)\",\" \")","v":"LLCB01A06_C AT%Q8.5 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A06_C             AT%Q8.5        :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A06_C","照明控制箱宴会厅-回路开关",69]
[{"$nulls":5},7,null,13,14,"照明控制箱宴会厅-回路开关",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL259,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL259,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A07","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH259,List!$B$3:$D$445,2,FALSE)&AJ259&\"_\"&VLOOKUP(AK259,List!$K$2:$M$447,2,FALSE)","v":"LCB01A07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM259&\" \"&\"AT%Q\"&B254*4&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J259&\"*)\",\" \")","v":"LLCB01A07_C AT%Q8.6 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A07_C             AT%Q8.6        :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A07_C","照明控制箱宴会厅-回路开关",70]
[".",{"$nulls":4},8,null,15,16,"照明控制箱宴会厅-回路开关",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL260,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL260,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A08","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH260,List!$B$3:$D$445,2,FALSE)&AJ260&\"_\"&VLOOKUP(AK260,List!$K$2:$M$447,2,FALSE)","v":"LCB01A08_C"},{"$f":"_xlfn.IFNA(\"L\"&AM260&\" \"&\"AT%Q\"&B254*4&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J260&\"*)\",\" \")","v":"LLCB01A08_C AT%Q8.7 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A08_C             AT%Q8.7        :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A08_C","照明控制箱宴会厅-回路开关",71]
[null,"BRSD_1216",{"$nulls":38},{"$f":"\"(* \"&B261&\"地址: \"&B263&\" *)\"","v":"(* BRSD_1216地址: 3 *)"}]
[null,"addr",null,null,null,1,null,1,2,{"$f":"AH262&AA262&\"-\"&AK262","v":"照明控制箱宴会厅-回路开关"},{"$nulls":16},{"$f":"IF(AI262=\"\",\"\",AI262)","v":"宴会厅"},{"$f":"_xlfn.IFNA(VLOOKUP(AL262,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL262,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A09","回路开关",{"$f":"AH262&\"-\"&AK262","v":"照明控制箱-回路开关"},{"$f":"VLOOKUP(AH262,List!$B$3:$D$445,2,FALSE)&AJ262&\"_\"&VLOOKUP(AK262,List!$K$2:$M$447,2,FALSE)","v":"LCB01A09_C"},{"$f":"_xlfn.IFNA(\"L\"&AM262&\" \"&\"AT%Q\"&B263*4&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J262&\"*)\",\" \")","v":"LLCB01A09_C AT%Q12.0 :BOOL; (*照明控制箱宴会厅-回路开关*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN262,SEARCH(\"AT%\",AN262),,REPT(\" \",25-SEARCH(\"AT%\",AN262))),SEARCH(\":\",REPLACE(AN262,SEARCH(\"AT%\",AN262),,REPT(\" \",25-SEARCH(\"AT%\",AN262)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN262,SEARCH(\"AT%\",AN262),,REPT(\" \",25-SEARCH(\"AT%\",AN262)))))),\" \")","v":"LLCB01A09_C             AT%Q12.0       :BOOL; (*照明控制箱宴会厅-回路开关*)"},null,{"$f":"AM262","v":"LCB01A09_C"},{"$f":"J262","v":"照明控制箱宴会厅-回路开关"},{"$f":"($B263*4*8+F262-1)","v":96}]
[null,3,null,null,null,2,null,3,4,"照明控制箱宴会厅-回路开关",{"$nulls":16},{"$f":"IF(AI263=\"\",\"\",AI263)","v":"宴会厅"},{"$f":"_xlfn.IFNA(VLOOKUP(AL263,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL263,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A10","回路开关",{"$f":"AH263&\"-\"&AK263","v":"照明控制箱-回路开关"},{"$f":"VLOOKUP(AH263,List!$B$3:$D$445,2,FALSE)&AJ263&\"_\"&VLOOKUP(AK263,List!$K$2:$M$447,2,FALSE)","v":"LCB01A10_C"},{"$f":"_xlfn.IFNA(\"L\"&AM263&\" \"&\"AT%Q\"&B263*4&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J263&\"*)\",\" \")","v":"LLCB01A10_C AT%Q12.1 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A10_C             AT%Q12.1       :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A10_C",{"$f":"J263","v":"照明控制箱宴会厅-回路开关"},{"$f":"AS262+1","v":97}]
[null,"kbs",null,null,null,3,null,5,6,"照明控制箱宴会厅-回路开关",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL264,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL264,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A11","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH264,List!$B$3:$D$445,2,FALSE)&AJ264&\"_\"&VLOOKUP(AK264,List!$K$2:$M$447,2,FALSE)","v":"LCB01A11_C"},{"$f":"_xlfn.IFNA(\"L\"&AM264&\" \"&\"AT%Q\"&B263*4&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J264&\"*)\",\" \")","v":"LLCB01A11_C AT%Q12.2 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A11_C             AT%Q12.2       :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A11_C","照明控制箱宴会厅-回路开关",{"$f":"AS263+1","v":98}]
[null,50,null,null,null,4,null,7,8,"照明控制箱宴会厅-回路开关",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL265,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL265,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A12","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH265,List!$B$3:$D$445,2,FALSE)&AJ265&\"_\"&VLOOKUP(AK265,List!$K$2:$M$447,2,FALSE)","v":"LCB01A12_C"},{"$f":"_xlfn.IFNA(\"L\"&AM265&\" \"&\"AT%Q\"&B263*4&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J265&\"*)\",\" \")","v":"LLCB01A12_C AT%Q12.3 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A12_C             AT%Q12.3       :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A12_C","照明控制箱宴会厅-回路开关",99]
[{"$nulls":5},5,null,9,10,"照明控制箱宴会厅-回路开关",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL266,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL266,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A13","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH266,List!$B$3:$D$445,2,FALSE)&AJ266&\"_\"&VLOOKUP(AK266,List!$K$2:$M$447,2,FALSE)","v":"LCB01A13_C"},{"$f":"_xlfn.IFNA(\"L\"&AM266&\" \"&\"AT%Q\"&B263*4&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J266&\"*)\",\" \")","v":"LLCB01A13_C AT%Q12.4 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A13_C             AT%Q12.4       :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A13_C","照明控制箱宴会厅-回路开关",100]
[{"$nulls":5},6,null,11,12,"照明控制箱宴会厅-回路开关",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL267,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL267,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A14","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH267,List!$B$3:$D$445,2,FALSE)&AJ267&\"_\"&VLOOKUP(AK267,List!$K$2:$M$447,2,FALSE)","v":"LCB01A14_C"},{"$f":"_xlfn.IFNA(\"L\"&AM267&\" \"&\"AT%Q\"&B263*4&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J267&\"*)\",\" \")","v":"LLCB01A14_C AT%Q12.5 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A14_C             AT%Q12.5       :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A14_C","照明控制箱宴会厅-回路开关",101]
[{"$nulls":5},7,null,13,14,"照明控制箱宴会厅-回路开关",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL268,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL268,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A15","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH268,List!$B$3:$D$445,2,FALSE)&AJ268&\"_\"&VLOOKUP(AK268,List!$K$2:$M$447,2,FALSE)","v":"LCB01A15_C"},{"$f":"_xlfn.IFNA(\"L\"&AM268&\" \"&\"AT%Q\"&B263*4&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J268&\"*)\",\" \")","v":"LLCB01A15_C AT%Q12.6 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A15_C             AT%Q12.6       :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A15_C","照明控制箱宴会厅-回路开关",102]
[{"$nulls":5},8,null,15,16,"照明控制箱宴会厅-回路开关",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL269,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL269,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A16","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH269,List!$B$3:$D$445,2,FALSE)&AJ269&\"_\"&VLOOKUP(AK269,List!$K$2:$M$447,2,FALSE)","v":"LCB01A16_C"},{"$f":"_xlfn.IFNA(\"L\"&AM269&\" \"&\"AT%Q\"&B263*4&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J269&\"*)\",\" \")","v":"LLCB01A16_C AT%Q12.7 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A16_C             AT%Q12.7       :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A16_C","照明控制箱宴会厅-回路开关",103]
[{"$nulls":5},9,null,17,18,"照明控制箱宴会厅-回路开关",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL270,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL270,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A17","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH270,List!$B$3:$D$445,2,FALSE)&AJ270&\"_\"&VLOOKUP(AK270,List!$K$2:$M$447,2,FALSE)","v":"LCB01A17_C"},{"$f":"_xlfn.IFNA(\"L\"&AM270&\" \"&\"AT%Q\"&B263*4+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J270&\"*)\",\" \")","v":"LLCB01A17_C AT%Q13.0 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A17_C             AT%Q13.0       :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A17_C","照明控制箱宴会厅-回路开关",104]
[{"$nulls":5},10,null,19,20,"照明控制箱宴会厅-回路开关",{"$nulls":16},{"$f":"IF(AI271=\"\",\"\",AI271)","v":"宴会厅"},{"$f":"_xlfn.IFNA(VLOOKUP(AL271,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL271,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A18","回路开关",{"$f":"AH271&\"-\"&AK271","v":"照明控制箱-回路开关"},{"$f":"VLOOKUP(AH271,List!$B$3:$D$445,2,FALSE)&AJ271&\"_\"&VLOOKUP(AK271,List!$K$2:$M$447,2,FALSE)","v":"LCB01A18_C"},{"$f":"_xlfn.IFNA(\"L\"&AM271&\" \"&\"AT%Q\"&B263*4+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J271&\"*)\",\" \")","v":"LLCB01A18_C AT%Q13.1 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A18_C             AT%Q13.1       :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A18_C",{"$f":"J271","v":"照明控制箱宴会厅-回路开关"},105]
[".",{"$nulls":4},11,null,21,22,"照明控制箱宴会厅-回路开关",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL272,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL272,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A19","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH272,List!$B$3:$D$445,2,FALSE)&AJ272&\"_\"&VLOOKUP(AK272,List!$K$2:$M$447,2,FALSE)","v":"LCB01A19_C"},{"$f":"_xlfn.IFNA(\"L\"&AM272&\" \"&\"AT%Q\"&B263*4+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J272&\"*)\",\" \")","v":"LLCB01A19_C AT%Q13.2 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A19_C             AT%Q13.2       :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A19_C","照明控制箱宴会厅-回路开关",106]
[".",{"$nulls":4},12,null,23,24,"照明控制箱宴会厅-回路开关",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL273,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL273,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","宴会厅","01A20","回路开关","照明控制箱-回路开关",{"$f":"VLOOKUP(AH273,List!$B$3:$D$445,2,FALSE)&AJ273&\"_\"&VLOOKUP(AK273,List!$K$2:$M$447,2,FALSE)","v":"LCB01A20_C"},{"$f":"_xlfn.IFNA(\"L\"&AM273&\" \"&\"AT%Q\"&B263*4+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J273&\"*)\",\" \")","v":"LLCB01A20_C AT%Q13.3 :BOOL; (*照明控制箱宴会厅-回路开关*)"},"LLCB01A20_C             AT%Q13.3       :BOOL; (*照明控制箱宴会厅-回路开关*)",null,"LCB01A20_C","照明控制箱宴会厅-回路开关",107]
[null,"BRSI_0702",{"$nulls":38},{"$f":"\"(* \"&B274&\"地址: \"&B276&\" *)\"","v":"(* BRSI_0702地址: 1 *)"}]
[null,"addr",null,null,null,1,null,1,"COM",{"$f":"AH275&AA275&\"-\"&AK275","v":"-"},{"$nulls":16},{"$f":"IF(AI275=\"\",\"\",AI275)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL275,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL275,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH275&\"-\"&AK275","v":"-"},{"$f":"VLOOKUP(AH275,List!$B$3:$D$445,2,FALSE)&AJ275&\"_\"&VLOOKUP(AK275,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM275&\" \"&\"AT%I\"&B276*4&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J275&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN275,SEARCH(\"AT%\",AN275),,REPT(\" \",25-SEARCH(\"AT%\",AN275))),SEARCH(\":\",REPLACE(AN275,SEARCH(\"AT%\",AN275),,REPT(\" \",25-SEARCH(\"AT%\",AN275)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN275,SEARCH(\"AT%\",AN275),,REPT(\" \",25-SEARCH(\"AT%\",AN275)))))),\" \")","v":" "},null,{"$f":"AM275","v":{"$error":"#N/A"}},{"$f":"J275","v":"-"},{"$f":"10000+($B276*4*8+F275-1)","v":10032}]
[null,1,null,null,null,2,null,2,null,"-",{"$nulls":16},{"$f":"IF(AI276=\"\",\"\",AI276)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL276,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL276,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH276&\"-\"&AK276","v":"-"},{"$f":"VLOOKUP(AH276,List!$B$3:$D$445,2,FALSE)&AJ276&\"_\"&VLOOKUP(AK276,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM276&\" \"&\"AT%I\"&B276*4&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J276&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J276","v":"-"},{"$f":"AS275+1","v":10033}]
[null,"kbs",null,null,null,3,null,3,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL277,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL277,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH277,List!$B$3:$D$445,2,FALSE)&AJ277&\"_\"&VLOOKUP(AK277,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM277&\" \"&\"AT%I\"&B276*4&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J277&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS276+1","v":10034}]
[null,50,null,null,null,4,null,4,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL278,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL278,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH278,List!$B$3:$D$445,2,FALSE)&AJ278&\"_\"&VLOOKUP(AK278,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM278&\" \"&\"AT%I\"&B276*4&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J278&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10035]
[{"$nulls":5},5,null,5,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL279,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL279,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH279,List!$B$3:$D$445,2,FALSE)&AJ279&\"_\"&VLOOKUP(AK279,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM279&\" \"&\"AT%I\"&B276*4&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J279&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10036]
[{"$nulls":5},6,null,6,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL280,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL280,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH280,List!$B$3:$D$445,2,FALSE)&AJ280&\"_\"&VLOOKUP(AK280,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM280&\" \"&\"AT%I\"&B276*4&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J280&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10037]
[".",{"$nulls":4},7,null,7,null,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL281,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL281,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH281,List!$B$3:$D$445,2,FALSE)&AJ281&\"_\"&VLOOKUP(AK281,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM281&\" \"&\"AT%I\"&B276*4&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J281&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10038]
[null,"BRBP_0601A",{"$nulls":38},{"$f":"\"(* \"&B282&\"地址: \"&B284&\" *)\"","v":"(* BRBP_0601A地址: 4 *)"}]
[null,"addr",null,null,null,1,null,null,null,{"$f":"AH283&AA283&\"-\"&AK283","v":"照明面板ALL01-场景控制"},{"$nulls":16},{"$f":"IF(AI283=\"\",\"\",AI283)","v":"ALL01"},{"$f":"_xlfn.IFNA(VLOOKUP(AL283,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL283,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","ALL01","01A01","场景控制",{"$f":"AH283&\"-\"&AK283","v":"照明面板-场景控制"},{"$f":"VLOOKUP(AH283,List!$B$3:$D$445,2,FALSE)&AJ283&\"_\"&VLOOKUP(AK283,List!$K$2:$M$447,2,FALSE)","v":"LCP01A01_SC"},{"$f":"_xlfn.IFNA(\"L\"&AM283&\" \"&\"AT%Q\"&B284*4+512&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J283&\"*)\",\" \")","v":"LLCP01A01_SC AT%Q528.0 :BOOL; (*照明面板ALL01-场景控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN283,SEARCH(\"AT%\",AN283),,REPT(\" \",25-SEARCH(\"AT%\",AN283))),SEARCH(\":\",REPLACE(AN283,SEARCH(\"AT%\",AN283),,REPT(\" \",25-SEARCH(\"AT%\",AN283)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN283,SEARCH(\"AT%\",AN283),,REPT(\" \",25-SEARCH(\"AT%\",AN283)))))),\" \")","v":"LLCP01A01_SC            AT%Q528.0      :BOOL; (*照明面板ALL01-场景控制*)"},null,{"$f":"AM283","v":"LCP01A01_SC"},{"$f":"J283","v":"照明面板ALL01-场景控制"},{"$f":"(($B284*4+512)*8+F283-1)","v":4224}]
[null,4,null,null,null,2,null,null,null,"照明面板ALL01-场景控制",{"$nulls":16},{"$f":"IF(AI284=\"\",\"\",AI284)","v":"ALL01"},{"$f":"_xlfn.IFNA(VLOOKUP(AL284,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL284,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","ALL01","01A02","场景控制",{"$f":"AH284&\"-\"&AK284","v":"照明面板-场景控制"},{"$f":"VLOOKUP(AH284,List!$B$3:$D$445,2,FALSE)&AJ284&\"_\"&VLOOKUP(AK284,List!$K$2:$M$447,2,FALSE)","v":"LCP01A02_SC"},{"$f":"_xlfn.IFNA(\"L\"&AM284&\" \"&\"AT%Q\"&B284*4+512&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J284&\"*)\",\" \")","v":"LLCP01A02_SC AT%Q528.1 :BOOL; (*照明面板ALL01-场景控制*)"},"LLCP01A02_SC            AT%Q528.1      :BOOL; (*照明面板ALL01-场景控制*)",null,"LCP01A02_SC",{"$f":"J284","v":"照明面板ALL01-场景控制"},{"$f":"AS283+1","v":4225}]
[null,"kbs",null,null,null,3,null,null,null,"照明面板ALL01-场景控制",{"$nulls":16},"ALL01",{"$f":"_xlfn.IFNA(VLOOKUP(AL285,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL285,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","ALL01","01A03","场景控制","照明面板-场景控制",{"$f":"VLOOKUP(AH285,List!$B$3:$D$445,2,FALSE)&AJ285&\"_\"&VLOOKUP(AK285,List!$K$2:$M$447,2,FALSE)","v":"LCP01A03_SC"},{"$f":"_xlfn.IFNA(\"L\"&AM285&\" \"&\"AT%Q\"&B284*4+512&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J285&\"*)\",\" \")","v":"LLCP01A03_SC AT%Q528.2 :BOOL; (*照明面板ALL01-场景控制*)"},"LLCP01A03_SC            AT%Q528.2      :BOOL; (*照明面板ALL01-场景控制*)",null,"LCP01A03_SC","照明面板ALL01-场景控制",{"$f":"AS284+1","v":4226}]
[null,50,null,null,null,4,null,null,null,"照明面板ALL01-场景控制",{"$nulls":16},"ALL01",{"$f":"_xlfn.IFNA(VLOOKUP(AL286,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL286,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","ALL01","01A04","场景控制","照明面板-场景控制",{"$f":"VLOOKUP(AH286,List!$B$3:$D$445,2,FALSE)&AJ286&\"_\"&VLOOKUP(AK286,List!$K$2:$M$447,2,FALSE)","v":"LCP01A04_SC"},{"$f":"_xlfn.IFNA(\"L\"&AM286&\" \"&\"AT%Q\"&B284*4+512&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J286&\"*)\",\" \")","v":"LLCP01A04_SC AT%Q528.3 :BOOL; (*照明面板ALL01-场景控制*)"},"LLCP01A04_SC            AT%Q528.3      :BOOL; (*照明面板ALL01-场景控制*)",null,"LCP01A04_SC","照明面板ALL01-场景控制",4227]
[{"$nulls":5},5,null,null,null,"照明面板ALL01-场景控制",{"$nulls":16},"ALL01",{"$f":"_xlfn.IFNA(VLOOKUP(AL287,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL287,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","ALL01","01A05","场景控制","照明面板-场景控制",{"$f":"VLOOKUP(AH287,List!$B$3:$D$445,2,FALSE)&AJ287&\"_\"&VLOOKUP(AK287,List!$K$2:$M$447,2,FALSE)","v":"LCP01A05_SC"},{"$f":"_xlfn.IFNA(\"L\"&AM287&\" \"&\"AT%Q\"&B284*4+512&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J287&\"*)\",\" \")","v":"LLCP01A05_SC AT%Q528.4 :BOOL; (*照明面板ALL01-场景控制*)"},"LLCP01A05_SC            AT%Q528.4      :BOOL; (*照明面板ALL01-场景控制*)",null,"LCP01A05_SC","照明面板ALL01-场景控制",4228]
[".",{"$nulls":4},6,null,null,null,"照明面板ALL01-场景控制",{"$nulls":16},"ALL01",{"$f":"_xlfn.IFNA(VLOOKUP(AL288,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL288,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","ALL01","01A06","场景控制","照明面板-场景控制",{"$f":"VLOOKUP(AH288,List!$B$3:$D$445,2,FALSE)&AJ288&\"_\"&VLOOKUP(AK288,List!$K$2:$M$447,2,FALSE)","v":"LCP01A06_SC"},{"$f":"_xlfn.IFNA(\"L\"&AM288&\" \"&\"AT%Q\"&B284*4+512&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J288&\"*)\",\" \")","v":"LLCP01A06_SC AT%Q528.5 :BOOL; (*照明面板ALL01-场景控制*)"},"LLCP01A06_SC            AT%Q528.5      :BOOL; (*照明面板ALL01-场景控制*)",null,"LCP01A06_SC","照明面板ALL01-场景控制",4229]
[null,"BRBP_0901A",{"$nulls":38},{"$f":"\"(* \"&B289&\"地址: \"&B291&\" *)\"","v":"(* BRBP_0901A地址: 5 *)"}]
[null,"addr",null,null,null,1,null,null,null,{"$f":"AH290&AA290&\"-\"&AK290","v":"照明面板宴会厅-场景反馈"},{"$nulls":16},{"$f":"IF(AI290=\"\",\"\",AI290)","v":"宴会厅"},{"$f":"_xlfn.IFNA(VLOOKUP(AL290,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL290,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A01","场景反馈",{"$f":"AH290&\"-\"&AK290","v":"照明面板-场景反馈"},{"$f":"VLOOKUP(AH290,List!$B$3:$D$445,2,FALSE)&AJ290&\"_\"&VLOOKUP(AK290,List!$K$2:$M$447,2,FALSE)","v":"LCP01A01_SF"},{"$f":"_xlfn.IFNA(\"L\"&AM290&\" \"&\"AT%I\"&B291*4&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J290&\"*)\",\" \")","v":"LLCP01A01_SF AT%I20.0 :BOOL; (*照明面板宴会厅-场景反馈*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN290,SEARCH(\"AT%\",AN290),,REPT(\" \",25-SEARCH(\"AT%\",AN290))),SEARCH(\":\",REPLACE(AN290,SEARCH(\"AT%\",AN290),,REPT(\" \",25-SEARCH(\"AT%\",AN290)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN290,SEARCH(\"AT%\",AN290),,REPT(\" \",25-SEARCH(\"AT%\",AN290)))))),\" \")","v":"LLCP01A01_SF            AT%I20.0       :BOOL; (*照明面板宴会厅-场景反馈*)"},null,{"$f":"AM290","v":"LCP01A01_SF"},{"$f":"J290","v":"照明面板宴会厅-场景反馈"},{"$f":"(($B291*4+512)*8+F290-1)","v":4256}]
[null,5,null,null,null,2,null,null,null,{"$f":"AH291&AA291&\"-\"&AK291","v":"照明面板宴会厅-场景反馈"},{"$nulls":16},{"$f":"IF(AI291=\"\",\"\",AI291)","v":"宴会厅"},{"$f":"_xlfn.IFNA(VLOOKUP(AL291,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL291,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A02","场景反馈",{"$f":"AH291&\"-\"&AK291","v":"照明面板-场景反馈"},{"$f":"VLOOKUP(AH291,List!$B$3:$D$445,2,FALSE)&AJ291&\"_\"&VLOOKUP(AK291,List!$K$2:$M$447,2,FALSE)","v":"LCP01A02_SF"},{"$f":"_xlfn.IFNA(\"L\"&AM291&\" \"&\"AT%I\"&B291*4&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J291&\"*)\",\" \")","v":"LLCP01A02_SF AT%I20.1 :BOOL; (*照明面板宴会厅-场景反馈*)"},"LLCP01A02_SF            AT%I20.1       :BOOL; (*照明面板宴会厅-场景反馈*)",null,"LCP01A02_SF",{"$f":"J291","v":"照明面板宴会厅-场景反馈"},{"$f":"AS290+1","v":4257}]
[null,"kbs",null,null,null,3,null,null,null,"照明面板宴会厅-场景反馈",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL292,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL292,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A03","场景反馈","照明面板-场景反馈",{"$f":"VLOOKUP(AH292,List!$B$3:$D$445,2,FALSE)&AJ292&\"_\"&VLOOKUP(AK292,List!$K$2:$M$447,2,FALSE)","v":"LCP01A03_SF"},{"$f":"_xlfn.IFNA(\"L\"&AM292&\" \"&\"AT%I\"&B291*4&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J292&\"*)\",\" \")","v":"LLCP01A03_SF AT%I20.2 :BOOL; (*照明面板宴会厅-场景反馈*)"},"LLCP01A03_SF            AT%I20.2       :BOOL; (*照明面板宴会厅-场景反馈*)",null,"LCP01A03_SF","照明面板宴会厅-场景反馈",{"$f":"AS291+1","v":4258}]
[null,50,null,null,null,4,null,null,null,"照明面板宴会厅-场景反馈",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL293,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL293,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A04","场景反馈","照明面板-场景反馈",{"$f":"VLOOKUP(AH293,List!$B$3:$D$445,2,FALSE)&AJ293&\"_\"&VLOOKUP(AK293,List!$K$2:$M$447,2,FALSE)","v":"LCP01A04_SF"},{"$f":"_xlfn.IFNA(\"L\"&AM293&\" \"&\"AT%I\"&B291*4&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J293&\"*)\",\" \")","v":"LLCP01A04_SF AT%I20.3 :BOOL; (*照明面板宴会厅-场景反馈*)"},"LLCP01A04_SF            AT%I20.3       :BOOL; (*照明面板宴会厅-场景反馈*)",null,"LCP01A04_SF","照明面板宴会厅-场景反馈",4259]
[{"$nulls":5},5,null,null,null,"照明面板宴会厅-场景反馈",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL294,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL294,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A05","场景反馈","照明面板-场景反馈",{"$f":"VLOOKUP(AH294,List!$B$3:$D$445,2,FALSE)&AJ294&\"_\"&VLOOKUP(AK294,List!$K$2:$M$447,2,FALSE)","v":"LCP01A05_SF"},{"$f":"_xlfn.IFNA(\"L\"&AM294&\" \"&\"AT%I\"&B291*4&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J294&\"*)\",\" \")","v":"LLCP01A05_SF AT%I20.4 :BOOL; (*照明面板宴会厅-场景反馈*)"},"LLCP01A05_SF            AT%I20.4       :BOOL; (*照明面板宴会厅-场景反馈*)",null,"LCP01A05_SF","照明面板宴会厅-场景反馈",4260]
[{"$nulls":5},6,null,null,null,"照明面板宴会厅-场景反馈",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL295,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL295,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A06","场景反馈","照明面板-场景反馈",{"$f":"VLOOKUP(AH295,List!$B$3:$D$445,2,FALSE)&AJ295&\"_\"&VLOOKUP(AK295,List!$K$2:$M$447,2,FALSE)","v":"LCP01A06_SF"},{"$f":"_xlfn.IFNA(\"L\"&AM295&\" \"&\"AT%I\"&B291*4&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J295&\"*)\",\" \")","v":"LLCP01A06_SF AT%I20.5 :BOOL; (*照明面板宴会厅-场景反馈*)"},"LLCP01A06_SF            AT%I20.5       :BOOL; (*照明面板宴会厅-场景反馈*)",null,"LCP01A06_SF","照明面板宴会厅-场景反馈",4261]
[{"$nulls":5},7,null,null,null,"照明面板宴会厅-场景反馈",{"$nulls":16},{"$f":"IF(AI296=\"\",\"\",AI296)","v":"宴会厅"},{"$f":"_xlfn.IFNA(VLOOKUP(AL296,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL296,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A07","场景反馈",{"$f":"AH296&\"-\"&AK296","v":"照明面板-场景反馈"},{"$f":"VLOOKUP(AH296,List!$B$3:$D$445,2,FALSE)&AJ296&\"_\"&VLOOKUP(AK296,List!$K$2:$M$447,2,FALSE)","v":"LCP01A07_SF"},{"$f":"_xlfn.IFNA(\"L\"&AM296&\" \"&\"AT%I\"&B291*4&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J296&\"*)\",\" \")","v":"LLCP01A07_SF AT%I20.6 :BOOL; (*照明面板宴会厅-场景反馈*)"},"LLCP01A07_SF            AT%I20.6       :BOOL; (*照明面板宴会厅-场景反馈*)",null,"LCP01A07_SF",{"$f":"J296","v":"照明面板宴会厅-场景反馈"},4262]
[{"$nulls":5},8,null,null,null,"照明面板宴会厅-场景反馈",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL297,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL297,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A08","场景反馈","照明面板-场景反馈",{"$f":"VLOOKUP(AH297,List!$B$3:$D$445,2,FALSE)&AJ297&\"_\"&VLOOKUP(AK297,List!$K$2:$M$447,2,FALSE)","v":"LCP01A08_SF"},{"$f":"_xlfn.IFNA(\"L\"&AM297&\" \"&\"AT%I\"&B291*4&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J297&\"*)\",\" \")","v":"LLCP01A08_SF AT%I20.7 :BOOL; (*照明面板宴会厅-场景反馈*)"},"LLCP01A08_SF            AT%I20.7       :BOOL; (*照明面板宴会厅-场景反馈*)",null,"LCP01A08_SF","照明面板宴会厅-场景反馈",4263]
[".",{"$nulls":4},9,null,null,null,"照明面板宴会厅-场景反馈",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL298,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL298,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A09","场景反馈","照明面板-场景反馈",{"$f":"VLOOKUP(AH298,List!$B$3:$D$445,2,FALSE)&AJ298&\"_\"&VLOOKUP(AK298,List!$K$2:$M$447,2,FALSE)","v":"LCP01A09_SF"},{"$f":"_xlfn.IFNA(\"L\"&AM298&\" \"&\"AT%I\"&B291*4+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J298&\"*)\",\" \")","v":"LLCP01A09_SF AT%I21.0 :BOOL; (*照明面板宴会厅-场景反馈*)"},"LLCP01A09_SF            AT%I21.0       :BOOL; (*照明面板宴会厅-场景反馈*)",null,"LCP01A09_SF","照明面板宴会厅-场景反馈",4264]
[null,"BRBP_0901A",{"$nulls":38},{"$f":"\"(* \"&B299&\"地址: \"&B301&\" *)\"","v":"(* BRBP_0901A地址: 6 *)"}]
[null,"addr",null,null,null,1,null,null,null,{"$f":"AH300&AA300&\"-\"&AK300","v":"照明面板宴会厅-场景控制"},{"$nulls":16},{"$f":"IF(AI300=\"\",\"\",AI300)","v":"宴会厅"},{"$f":"_xlfn.IFNA(VLOOKUP(AL300,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL300,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A01","场景控制",{"$f":"AH300&\"-\"&AK300","v":"照明面板-场景控制"},{"$f":"VLOOKUP(AH300,List!$B$3:$D$445,2,FALSE)&AJ300&\"_\"&VLOOKUP(AK300,List!$K$2:$M$447,2,FALSE)","v":"LCP01A01_SC"},{"$f":"_xlfn.IFNA(\"L\"&AM300&\" \"&\"AT%Q\"&B301*4&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J300&\"*)\",\" \")","v":"LLCP01A01_SC AT%Q24.0 :BOOL; (*照明面板宴会厅-场景控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN300,SEARCH(\"AT%\",AN300),,REPT(\" \",25-SEARCH(\"AT%\",AN300))),SEARCH(\":\",REPLACE(AN300,SEARCH(\"AT%\",AN300),,REPT(\" \",25-SEARCH(\"AT%\",AN300)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN300,SEARCH(\"AT%\",AN300),,REPT(\" \",25-SEARCH(\"AT%\",AN300)))))),\" \")","v":"LLCP01A01_SC            AT%Q24.0       :BOOL; (*照明面板宴会厅-场景控制*)"},null,{"$f":"AM300","v":"LCP01A01_SC"},{"$f":"J300","v":"照明面板宴会厅-场景控制"},{"$f":"(($B301*4+512)*8+F300-1)","v":4288}]
[null,{"$f":"B291+1","v":6},null,null,null,2,null,null,null,{"$f":"AH301&AA301&\"-\"&AK301","v":"照明面板宴会厅-场景控制"},{"$nulls":16},{"$f":"IF(AI301=\"\",\"\",AI301)","v":"宴会厅"},{"$f":"_xlfn.IFNA(VLOOKUP(AL301,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL301,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A02","场景控制",{"$f":"AH301&\"-\"&AK301","v":"照明面板-场景控制"},{"$f":"VLOOKUP(AH301,List!$B$3:$D$445,2,FALSE)&AJ301&\"_\"&VLOOKUP(AK301,List!$K$2:$M$447,2,FALSE)","v":"LCP01A02_SC"},{"$f":"_xlfn.IFNA(\"L\"&AM301&\" \"&\"AT%Q\"&B301*4&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J301&\"*)\",\" \")","v":"LLCP01A02_SC AT%Q24.1 :BOOL; (*照明面板宴会厅-场景控制*)"},"LLCP01A02_SC            AT%Q24.1       :BOOL; (*照明面板宴会厅-场景控制*)",null,"LCP01A02_SC",{"$f":"J301","v":"照明面板宴会厅-场景控制"},{"$f":"AS300+1","v":4289}]
[null,"kbs",null,null,null,3,null,null,null,"照明面板宴会厅-场景控制",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL302,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL302,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A03","场景控制","照明面板-场景控制",{"$f":"VLOOKUP(AH302,List!$B$3:$D$445,2,FALSE)&AJ302&\"_\"&VLOOKUP(AK302,List!$K$2:$M$447,2,FALSE)","v":"LCP01A03_SC"},{"$f":"_xlfn.IFNA(\"L\"&AM302&\" \"&\"AT%Q\"&B301*4&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J302&\"*)\",\" \")","v":"LLCP01A03_SC AT%Q24.2 :BOOL; (*照明面板宴会厅-场景控制*)"},"LLCP01A03_SC            AT%Q24.2       :BOOL; (*照明面板宴会厅-场景控制*)",null,"LCP01A03_SC","照明面板宴会厅-场景控制",{"$f":"AS301+1","v":4290}]
[null,50,null,null,null,4,null,null,null,"照明面板宴会厅-场景控制",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL303,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL303,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A04","场景控制","照明面板-场景控制",{"$f":"VLOOKUP(AH303,List!$B$3:$D$445,2,FALSE)&AJ303&\"_\"&VLOOKUP(AK303,List!$K$2:$M$447,2,FALSE)","v":"LCP01A04_SC"},{"$f":"_xlfn.IFNA(\"L\"&AM303&\" \"&\"AT%Q\"&B301*4&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J303&\"*)\",\" \")","v":"LLCP01A04_SC AT%Q24.3 :BOOL; (*照明面板宴会厅-场景控制*)"},"LLCP01A04_SC            AT%Q24.3       :BOOL; (*照明面板宴会厅-场景控制*)",null,"LCP01A04_SC","照明面板宴会厅-场景控制",4291]
[{"$nulls":5},5,null,null,null,"照明面板宴会厅-场景控制",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL304,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL304,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A05","场景控制","照明面板-场景控制",{"$f":"VLOOKUP(AH304,List!$B$3:$D$445,2,FALSE)&AJ304&\"_\"&VLOOKUP(AK304,List!$K$2:$M$447,2,FALSE)","v":"LCP01A05_SC"},{"$f":"_xlfn.IFNA(\"L\"&AM304&\" \"&\"AT%Q\"&B301*4&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J304&\"*)\",\" \")","v":"LLCP01A05_SC AT%Q24.4 :BOOL; (*照明面板宴会厅-场景控制*)"},"LLCP01A05_SC            AT%Q24.4       :BOOL; (*照明面板宴会厅-场景控制*)",null,"LCP01A05_SC","照明面板宴会厅-场景控制",4292]
[{"$nulls":5},6,null,null,null,"照明面板宴会厅-场景控制",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL305,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL305,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A06","场景控制","照明面板-场景控制",{"$f":"VLOOKUP(AH305,List!$B$3:$D$445,2,FALSE)&AJ305&\"_\"&VLOOKUP(AK305,List!$K$2:$M$447,2,FALSE)","v":"LCP01A06_SC"},{"$f":"_xlfn.IFNA(\"L\"&AM305&\" \"&\"AT%Q\"&B301*4&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J305&\"*)\",\" \")","v":"LLCP01A06_SC AT%Q24.5 :BOOL; (*照明面板宴会厅-场景控制*)"},"LLCP01A06_SC            AT%Q24.5       :BOOL; (*照明面板宴会厅-场景控制*)",null,"LCP01A06_SC","照明面板宴会厅-场景控制",4293]
[{"$nulls":5},7,null,null,null,"照明面板宴会厅-场景控制",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL306,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL306,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A07","场景控制","照明面板-场景控制",{"$f":"VLOOKUP(AH306,List!$B$3:$D$445,2,FALSE)&AJ306&\"_\"&VLOOKUP(AK306,List!$K$2:$M$447,2,FALSE)","v":"LCP01A07_SC"},{"$f":"_xlfn.IFNA(\"L\"&AM306&\" \"&\"AT%Q\"&B301*4&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J306&\"*)\",\" \")","v":"LLCP01A07_SC AT%Q24.6 :BOOL; (*照明面板宴会厅-场景控制*)"},"LLCP01A07_SC            AT%Q24.6       :BOOL; (*照明面板宴会厅-场景控制*)",null,"LCP01A07_SC","照明面板宴会厅-场景控制",4294]
[{"$nulls":5},8,null,null,null,"照明面板宴会厅-场景控制",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL307,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL307,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A08","场景控制","照明面板-场景控制",{"$f":"VLOOKUP(AH307,List!$B$3:$D$445,2,FALSE)&AJ307&\"_\"&VLOOKUP(AK307,List!$K$2:$M$447,2,FALSE)","v":"LCP01A08_SC"},{"$f":"_xlfn.IFNA(\"L\"&AM307&\" \"&\"AT%Q\"&B301*4&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J307&\"*)\",\" \")","v":"LLCP01A08_SC AT%Q24.7 :BOOL; (*照明面板宴会厅-场景控制*)"},"LLCP01A08_SC            AT%Q24.7       :BOOL; (*照明面板宴会厅-场景控制*)",null,"LCP01A08_SC","照明面板宴会厅-场景控制",4295]
[".",{"$nulls":4},9,null,null,null,"照明面板宴会厅-场景控制",{"$nulls":16},"宴会厅",{"$f":"_xlfn.IFNA(VLOOKUP(AL308,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL308,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明面板","宴会厅","01A09","场景控制","照明面板-场景控制",{"$f":"VLOOKUP(AH308,List!$B$3:$D$445,2,FALSE)&AJ308&\"_\"&VLOOKUP(AK308,List!$K$2:$M$447,2,FALSE)","v":"LCP01A09_SC"},{"$f":"_xlfn.IFNA(\"L\"&AM308&\" \"&\"AT%Q\"&B301*4+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J308&\"*)\",\" \")","v":"LLCP01A09_SC AT%Q25.0 :BOOL; (*照明面板宴会厅-场景控制*)"},"LLCP01A09_SC            AT%Q25.0       :BOOL; (*照明面板宴会厅-场景控制*)",null,"LCP01A09_SC","照明面板宴会厅-场景控制",4296]
[null,"中间变量",{"$nulls":33},{"$f":"COUNTA($AJ$7:AJ308)","v":106},{"$nulls":4},{"$f":"\"(* \"&B309&\":总计干接点:\"&AJ309&\" *)\"","v":"(* 中间变量:总计干接点:106 *)"}]
[null,"100.0",{"$f":"IF((IF(OR(G310=\"INT \",G310=\"WORD\",G310=\"BOOL\"),MOD(B310,2),MOD(B310,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"INT ",null,null,{"$f":"AH310&AA310&\"-\"&AK310","v":"控制箱DDCB101-硬件总点位"},{"$nulls":16},"DDCB101",{"$nulls":6},"控制箱","DDCB101",null,"硬件总点位","控制箱-硬件总点位",{"$f":"AI310&VLOOKUP(AH310,List!B:D,2,FALSE)&AJ310&\"_\"&VLOOKUP(AK310,List!K:M,2,FALSE)","v":"DDCB101BOX_THB"},{"$f":"_xlfn.IFNA(\"L\"&AM310&\" \"&\"AT%M\"&B310&\" :\"&G310&\";\"&\" \"&\"(*\"&J310&\"*)\",\" \")","v":"LDDCB101BOX_THB AT%M100.0 :INT ; (*控制箱DDCB101-硬件总点位*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN310,SEARCH(\"AT%\",AN310),,REPT(\" \",25-SEARCH(\"AT%\",AN310))),SEARCH(\":\",REPLACE(AN310,SEARCH(\"AT%\",AN310),,REPT(\" \",25-SEARCH(\"AT%\",AN310)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN310,SEARCH(\"AT%\",AN310),,REPT(\" \",25-SEARCH(\"AT%\",AN310)))))),\" \")","v":"LDDCB101BOX_THB         AT%M100.0      :INT ; (*控制箱DDCB101-硬件总点位*)"}]
[null,{"$f":"IF(OR(G310=\"REAL\",G310=\"DWORD\",G310=\"DINT\"),(IF(OR(G311=\"REAL\",G311=\"DWORD\",G311=\"DINT\"),B310+4+MOD(B310,4),B310+4)),(IF(OR(G311=\"REAL\",G311=\"DWORD\",G311=\"DINT\"),B310+4+MOD(B310,4),B310+2)))&\".0\"","v":"102.0"},{"$f":"IF((IF(OR(G311=\"INT \",G311=\"WORD\",G311=\"BOOL\"),MOD(B311,2),MOD(B311,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH311&AA311&\"-\"&AK311","v":"控制箱DDCB101-模块地址状态"},{"$nulls":16},{"$f":"IF(AI311=\"\",\"\",AI311)","v":"DDCB101"},{"$nulls":6},"控制箱","DDCB101",null,"模块地址状态",{"$f":"AH311&\"-\"&AK311","v":"控制箱-模块地址状态"},{"$f":"AI311&VLOOKUP(AH311,List!B:D,2,FALSE)&AJ311&\"_\"&VLOOKUP(AK311,List!K:M,2,FALSE)","v":"DDCB101BOX_DS"},{"$f":"_xlfn.IFNA(\"L\"&AM311&\" \"&\"AT%M\"&B311&\" :\"&G311&\";\"&\" \"&\"(*\"&J311&\"*)\",\" \")","v":"LDDCB101BOX_DS AT%M102.0 :BOOL; (*控制箱DDCB101-模块地址状态*)"},"LDDCB101BOX_DS          AT%M102.0      :BOOL; (*控制箱DDCB101-模块地址状态*)"]
[null,"104.0","验证通过",null,null,null,"BOOL",null,null,"控制箱DDCB102-模块地址状态",{"$nulls":16},"DDCB102",{"$nulls":6},"控制箱","DDCB102",null,"模块地址状态","控制箱-模块地址状态",{"$f":"AI312&VLOOKUP(AH312,List!B:D,2,FALSE)&AJ312&\"_\"&VLOOKUP(AK312,List!K:M,2,FALSE)","v":"DDCB102BOX_DS"},"LDDCB102BOX_DS AT%M104.0 :BOOL; (*控制箱DDCB102-模块地址状态*)","LDDCB102BOX_DS          AT%M104.0      :BOOL; (*控制箱DDCB102-模块地址状态*)"]
[null,"106.0","验证通过",null,null,null,"BOOL",null,null,"控制箱DDCB103-模块地址状态",{"$nulls":16},"DDCB103",{"$nulls":6},"控制箱","DDCB103",null,"模块地址状态","控制箱-模块地址状态",{"$f":"AI313&VLOOKUP(AH313,List!B:D,2,FALSE)&AJ313&\"_\"&VLOOKUP(AK313,List!K:M,2,FALSE)","v":"DDCB103BOX_DS"},"LDDCB103BOX_DS AT%M106.0 :BOOL; (*控制箱DDCB103-模块地址状态*)","LDDCB103BOX_DS          AT%M106.0      :BOOL; (*控制箱DDCB103-模块地址状态*)"]
[null,"108.0","验证通过",null,null,null,"BOOL",null,null,"控制箱DDCB104-模块地址状态",{"$nulls":16},"DDCB104",{"$nulls":6},"控制箱","DDCB104",null,"模块地址状态","控制箱-模块地址状态",{"$f":"AI314&VLOOKUP(AH314,List!B:D,2,FALSE)&AJ314&\"_\"&VLOOKUP(AK314,List!K:M,2,FALSE)","v":"DDCB104BOX_DS"},"LDDCB104BOX_DS AT%M108.0 :BOOL; (*控制箱DDCB104-模块地址状态*)","LDDCB104BOX_DS          AT%M108.0      :BOOL; (*控制箱DDCB104-模块地址状态*)"]
[null,"110.0","验证通过",null,null,null,"BOOL",null,null,"控制箱DDCB105-模块地址状态",{"$nulls":16},"DDCB105",{"$nulls":6},"控制箱","DDCB105",null,"模块地址状态","控制箱-模块地址状态",{"$f":"AI315&VLOOKUP(AH315,List!B:D,2,FALSE)&AJ315&\"_\"&VLOOKUP(AK315,List!K:M,2,FALSE)","v":"DDCB105BOX_DS"},"LDDCB105BOX_DS AT%M110.0 :BOOL; (*控制箱DDCB105-模块地址状态*)","LDDCB105BOX_DS          AT%M110.0      :BOOL; (*控制箱DDCB105-模块地址状态*)"]
[null,"116.0",{"$f":"IF((IF(OR(G316=\"INT \",G316=\"WORD\",G316=\"BOOL\"),MOD(B316,2),MOD(B316,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"REAL",null,null,"控制箱DDCB101-模块在线比例",{"$nulls":16},"DDCB101",{"$nulls":6},"控制箱","DDCB101",null,"模块在线比例","控制箱-模块在线比例",{"$f":"AI316&VLOOKUP(AH316,List!B:D,2,FALSE)&AJ316&\"_\"&VLOOKUP(AK316,List!K:M,2,FALSE)","v":"DDCB101BOX_OR"},"LDDCB101BOX_OR AT%M116.0 :REAL; (*控制箱DDCB101-模块在线比例*)","LDDCB101BOX_OR          AT%M116.0      :REAL; (*控制箱DDCB101-模块在线比例*)"]
[null,"120.0","验证通过",null,null,null,"REAL",null,null,"控制箱DDCB102-模块在线比例",{"$nulls":16},"DDCB102",{"$nulls":6},"控制箱","DDCB102",null,"模块在线比例","控制箱-模块在线比例",{"$f":"AI317&VLOOKUP(AH317,List!B:D,2,FALSE)&AJ317&\"_\"&VLOOKUP(AK317,List!K:M,2,FALSE)","v":"DDCB102BOX_OR"},"LDDCB102BOX_OR AT%M120.0 :REAL; (*控制箱DDCB102-模块在线比例*)","LDDCB102BOX_OR          AT%M120.0      :REAL; (*控制箱DDCB102-模块在线比例*)"]
[null,"124.0","验证通过",null,null,null,"REAL",null,null,"控制箱DDCB103-模块在线比例",{"$nulls":16},"DDCB103",{"$nulls":6},"控制箱","DDCB103",null,"模块在线比例","控制箱-模块在线比例",{"$f":"AI318&VLOOKUP(AH318,List!B:D,2,FALSE)&AJ318&\"_\"&VLOOKUP(AK318,List!K:M,2,FALSE)","v":"DDCB103BOX_OR"},"LDDCB103BOX_OR AT%M124.0 :REAL; (*控制箱DDCB103-模块在线比例*)","LDDCB103BOX_OR          AT%M124.0      :REAL; (*控制箱DDCB103-模块在线比例*)"]
[null,"128.0","验证通过",null,null,null,"REAL",null,null,"控制箱DDCB104-模块在线比例",{"$nulls":16},"DDCB104",{"$nulls":6},"控制箱","DDCB104",null,"模块在线比例","控制箱-模块在线比例",{"$f":"AI319&VLOOKUP(AH319,List!B:D,2,FALSE)&AJ319&\"_\"&VLOOKUP(AK319,List!K:M,2,FALSE)","v":"DDCB104BOX_OR"},"LDDCB104BOX_OR AT%M128.0 :REAL; (*控制箱DDCB104-模块在线比例*)","LDDCB104BOX_OR          AT%M128.0      :REAL; (*控制箱DDCB104-模块在线比例*)"]
[null,"132.0","验证通过",null,null,null,"REAL",null,null,"控制箱DDCB105-模块在线比例",{"$nulls":16},"DDCB105",{"$nulls":6},"控制箱","DDCB105",null,"模块在线比例","控制箱-模块在线比例",{"$f":"AI320&VLOOKUP(AH320,List!B:D,2,FALSE)&AJ320&\"_\"&VLOOKUP(AK320,List!K:M,2,FALSE)","v":"DDCB105BOX_OR"},"LDDCB105BOX_OR AT%M132.0 :REAL; (*控制箱DDCB105-模块在线比例*)","LDDCB105BOX_OR          AT%M132.0      :REAL; (*控制箱DDCB105-模块在线比例*)"]
[null,"AHU"]
[null,{"$f":"IF(OR(G320=\"REAL\",G320=\"DWORD\",G320=\"DINT\"),(IF(OR(G322=\"REAL\",G322=\"DWORD\",G322=\"DINT\"),B320+4+MOD(B320,4),B320+4)),(IF(OR(G322=\"REAL\",G322=\"DWORD\",G322=\"DINT\"),B320+4+MOD(B320,4),B320+2)))&\".0\"","v":"136.0"},"验证通过",null,null,null,"BOOL",null,null,{"$f":"AH322&AA322&\"-\"&AK322","v":"空调机组BXJ-1AP(KT)1-1-程序控制"},{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","程序控制",{"$f":"AH322&\"-\"&IF(AI322=\"R\",\"新云平台\"&AK322,AK322)","v":"空调机组-程序控制"},{"$f":"VLOOKUP(AH322,List!$B$3:$D$445,2,FALSE)&AJ322&\"_\"&VLOOKUP(AK322,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_PC"},{"$f":"_xlfn.IFNA(\"R\"&AM322&\" \"&\"AT%M\"&B322&\" :\"&G322&\";\"&\" \"&\"(*\"&J322&\"*)\",\" \")","v":"RAHU01A01_PC AT%M136.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-程序控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN322,SEARCH(\"AT%\",AN322),,REPT(\" \",25-SEARCH(\"AT%\",AN322))),SEARCH(\":\",REPLACE(AN322,SEARCH(\"AT%\",AN322),,REPT(\" \",25-SEARCH(\"AT%\",AN322)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN322,SEARCH(\"AT%\",AN322),,REPT(\" \",25-SEARCH(\"AT%\",AN322)))))),\" \")","v":"RAHU01A01_PC            AT%M136.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-程序控制*)"}]
[null,{"$f":"IF(OR(G322=\"REAL\",G322=\"DWORD\",G322=\"DINT\"),(IF(OR(G323=\"REAL\",G323=\"DWORD\",G323=\"DINT\"),B322+4+MOD(B322,4),B322+4)),(IF(OR(G323=\"REAL\",G323=\"DWORD\",G323=\"DINT\"),B322+4+MOD(B322,4),B322+2)))&\".0\"","v":"138.0"},"验证通过",null,null,null,"INT ",null,null,{"$f":"AH323&AA323&\"-\"&AK323","v":"空调机组BXJ-1AP(KT)1-1-季节模式"},{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","季节模式",{"$f":"AH323&\"-\"&IF(AI323=\"R\",\"新云平台\"&AK323,AK323)","v":"空调机组-季节模式"},{"$f":"VLOOKUP(AH323,List!$B$3:$D$445,2,FALSE)&AJ323&\"_\"&VLOOKUP(AK323,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_SM"},{"$f":"_xlfn.IFNA(\"R\"&AM323&\" \"&\"AT%M\"&B323&\" :\"&G323&\";\"&\" \"&\"(*\"&J323&\"*)\",\" \")","v":"RAHU01A01_SM AT%M138.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-季节模式*)"},"RAHU01A01_SM            AT%M138.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-季节模式*)"]
[null,"144.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-设定温度值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","设定温度值","空调机组-设定温度值",{"$f":"VLOOKUP(AH324,List!$B$3:$D$445,2,FALSE)&AJ324&\"_\"&VLOOKUP(AK324,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_TSET"},{"$f":"_xlfn.IFNA(\"R\"&AM324&\" \"&\"AT%M\"&B324&\" :\"&G324&\";\"&\" \"&\"(*\"&J324&\"*)\",\" \")","v":"RAHU01A01_TSET AT%M144.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-设定温度值*)"},"RAHU01A01_TSET          AT%M144.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-设定温度值*)"]
[null,"148.0","验证通过",null,null,null,"BOOL",null,null,"空调机组BXJ-1AP(KT)1-1-程序控制",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","程序控制","空调机组-程序控制",{"$f":"VLOOKUP(AH325,List!$B$3:$D$445,2,FALSE)&AJ325&\"_\"&VLOOKUP(AK325,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_PC"},{"$f":"_xlfn.IFNA(\"L\"&AM325&\" \"&\"AT%M\"&B325&\" :\"&G325&\";\"&\" \"&\"(*\"&J325&\"*)\",\" \")","v":"LAHU01A01_PC AT%M148.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-程序控制*)"},"LAHU01A01_PC            AT%M148.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-程序控制*)"]
[null,"150.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-季节模式",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","季节模式","空调机组-季节模式",{"$f":"VLOOKUP(AH326,List!$B$3:$D$445,2,FALSE)&AJ326&\"_\"&VLOOKUP(AK326,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_SM"},"LAHU01A01_SM AT%M150.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-季节模式*)","LAHU01A01_SM            AT%M150.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-季节模式*)"]
[null,"156.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-设定温度值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","设定温度值","空调机组-设定温度值",{"$f":"VLOOKUP(AH327,List!$B$3:$D$445,2,FALSE)&AJ327&\"_\"&VLOOKUP(AK327,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_TSET"},"LAHU01A01_TSET AT%M156.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-设定温度值*)","LAHU01A01_TSET          AT%M156.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-设定温度值*)"]
[null,"160.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-设备状态代码",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","设备状态代码","空调机组-设备状态代码",{"$f":"VLOOKUP(AH328,List!$B$3:$D$445,2,FALSE)&AJ328&\"_\"&VLOOKUP(AK328,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_SN"},"LAHU01A01_SN AT%M160.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-设备状态代码*)","LAHU01A01_SN            AT%M160.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-设备状态代码*)"]
[null,"164.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-回风温度换算值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","回风温度换算值","空调机组-回风温度换算值",{"$f":"VLOOKUP(AH329,List!$B$3:$D$445,2,FALSE)&AJ329&\"_\"&VLOOKUP(AK329,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_RTS"},"LAHU01A01_RTS AT%M164.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-回风温度换算值*)","LAHU01A01_RTS           AT%M164.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-回风温度换算值*)"]
[null,"168.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-水阀反馈换算值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","水阀反馈换算值","空调机组-水阀反馈换算值",{"$f":"VLOOKUP(AH330,List!$B$3:$D$445,2,FALSE)&AJ330&\"_\"&VLOOKUP(AK330,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_WVBS"},"LAHU01A01_WVBS AT%M168.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-水阀反馈换算值*)","LAHU01A01_WVBS          AT%M168.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-水阀反馈换算值*)"]
[null,"172.0","验证通过",null,null,null,"BOOL",null,null,"空调机组BXJ-1AP(KT)1-1-水阀手动控制",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","水阀手动控制","空调机组-水阀手动控制",{"$f":"VLOOKUP(AH331,List!$B$3:$D$445,2,FALSE)&AJ331&\"_\"&VLOOKUP(AK331,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_WVMC"},"LAHU01A01_WVMC AT%M172.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-水阀手动控制*)","LAHU01A01_WVMC          AT%M172.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-水阀手动控制*)"]
[null,"176.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-水阀手动控制值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","水阀手动控制值","空调机组-水阀手动控制值",{"$f":"VLOOKUP(AH332,List!$B$3:$D$445,2,FALSE)&AJ332&\"_\"&VLOOKUP(AK332,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_WVMV"},"LAHU01A01_WVMV AT%M176.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-水阀手动控制值*)","LAHU01A01_WVMV          AT%M176.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-水阀手动控制值*)"]
[null,"180.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-水阀控制转换值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","水阀控制转换值","空调机组-水阀控制转换值",{"$f":"VLOOKUP(AH333,List!$B$3:$D$445,2,FALSE)&AJ333&\"_\"&VLOOKUP(AK333,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_WVCS"},"LAHU01A01_WVCS AT%M180.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-水阀控制转换值*)","LAHU01A01_WVCS          AT%M180.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-水阀控制转换值*)"]
[null,"182.0","验证通过",null,null,null,"BOOL",null,null,"空调机组BXJ-1AP(KT)1-1-运行时间累积重置",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","运行时间累积重置","空调机组-运行时间累积重置",{"$f":"VLOOKUP(AH334,List!$B$3:$D$445,2,FALSE)&AJ334&\"_\"&VLOOKUP(AK334,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_RST"},"LAHU01A01_RST AT%M182.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-运行时间累积重置*)","LAHU01A01_RST           AT%M182.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-运行时间累积重置*)"]
[null,"188.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-运行时间累积重置值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","运行时间累积重置值","空调机组-运行时间累积重置值",{"$f":"VLOOKUP(AH335,List!$B$3:$D$445,2,FALSE)&AJ335&\"_\"&VLOOKUP(AK335,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_RSTV"},"LAHU01A01_RSTV AT%M188.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-运行时间累积重置值*)","LAHU01A01_RSTV          AT%M188.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-运行时间累积重置值*)"]
[null,"192.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-运行时间累积值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","运行时间累积值","空调机组-运行时间累积值",{"$f":"VLOOKUP(AH336,List!$B$3:$D$445,2,FALSE)&AJ336&\"_\"&VLOOKUP(AK336,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_RH"},"LAHU01A01_RH AT%M192.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-运行时间累积值*)","LAHU01A01_RH            AT%M192.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-运行时间累积值*)"]
[null,"196.0","验证通过",null,null,null,"BOOL",null,null,"空调机组BXJ-1AP(KT)1-1-隔离开关1",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","隔离开关1","空调机组-隔离开关1",{"$f":"VLOOKUP(AH337,List!$B$3:$D$445,2,FALSE)&AJ337&\"_\"&VLOOKUP(AK337,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_ISO1"},"LAHU01A01_ISO1 AT%M196.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-隔离开关1*)","LAHU01A01_ISO1          AT%M196.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-隔离开关1*)"]
[null,"198.0","验证通过",null,null,null,"BOOL",null,null,"空调机组BXJ-1AP(KT)1-1-隔离开关2",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","隔离开关2","空调机组-隔离开关2",{"$f":"VLOOKUP(AH338,List!$B$3:$D$445,2,FALSE)&AJ338&\"_\"&VLOOKUP(AK338,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_ISO2"},"LAHU01A01_ISO2 AT%M198.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-隔离开关2*)","LAHU01A01_ISO2          AT%M198.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-隔离开关2*)"]
[null,"204.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-P调节参数",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","P调节参数","空调机组-P调节参数",{"$f":"VLOOKUP(AH339,List!$B$3:$D$445,2,FALSE)&AJ339&\"_\"&VLOOKUP(AK339,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_VP"},"LAHU01A01_VP AT%M204.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-P调节参数*)","LAHU01A01_VP            AT%M204.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-P调节参数*)"]
[null,"208.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-I调节参数",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","I调节参数","空调机组-I调节参数",{"$f":"VLOOKUP(AH340,List!$B$3:$D$445,2,FALSE)&AJ340&\"_\"&VLOOKUP(AK340,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_VI"},"LAHU01A01_VI AT%M208.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-I调节参数*)","LAHU01A01_VI            AT%M208.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-I调节参数*)"]
[null,"212.0","验证通过",null,null,null,"BOOL",null,null,"空调机组BXJ-1AP(KT)1-1-定时模式",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","定时模式","空调机组-定时模式",{"$f":"VLOOKUP(AH341,List!$B$3:$D$445,2,FALSE)&AJ341&\"_\"&VLOOKUP(AK341,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_TM"},"LAHU01A01_TM AT%M212.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-定时模式*)","LAHU01A01_TM            AT%M212.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-定时模式*)"]
[null,{"$f":"IF(OR(G341=\"REAL\",G341=\"DWORD\",G341=\"DINT\"),(IF(OR(G342=\"REAL\",G342=\"DWORD\",G342=\"DINT\"),B341+4+MOD(B341,4),B341+4)),(IF(OR(G342=\"REAL\",G342=\"DWORD\",G342=\"DINT\"),B341+4+MOD(B341,4),B341+2)))&\".0\"","v":"214.0"},"验证通过",null,null,null,"BOOL",null,null,"空调机组BXJ-1AP(KT)1-1-定时控制",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","定时控制","空调机组-定时控制",{"$f":"VLOOKUP(AH342,List!$B$3:$D$445,2,FALSE)&AJ342&\"_\"&VLOOKUP(AK342,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_TC"},"LAHU01A01_TC AT%M214.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-定时控制*)","LAHU01A01_TC            AT%M214.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-定时控制*)"]
[null,"216.0",{"$f":"IF((IF(OR(G343=\"INT \",G343=\"WORD\",G343=\"BOOL\"),MOD(B343,2),MOD(B343,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"INT ",null,null,{"$f":"AH343&AA343&\"-\"&AK343","v":"空调机组BXJ-1AP(KT)1-1-工作日开启小时"},{"$nulls":16},{"$f":"IF(AI343=\"\",\"\",AI343)","v":"BXJ-1AP(KT)1-1"},{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","工作日开启小时",{"$f":"AH343&\"-\"&IF(AI343=\"R\",\"新云平台\"&AK343,AK343)","v":"空调机组-工作日开启小时"},{"$f":"VLOOKUP(AH343,List!$B$3:$D$445,2,FALSE)&AJ343&\"_\"&VLOOKUP(AK343,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_WOH"},{"$f":"_xlfn.IFNA(\"L\"&AM343&\" \"&\"AT%M\"&B343&\" :\"&G343&\";\"&\" \"&\"(*\"&J343&\"*)\",\" \")","v":"LAHU01A01_WOH AT%M216.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-工作日开启小时*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN343,SEARCH(\"AT%\",AN343),,REPT(\" \",25-SEARCH(\"AT%\",AN343))),SEARCH(\":\",REPLACE(AN343,SEARCH(\"AT%\",AN343),,REPT(\" \",25-SEARCH(\"AT%\",AN343)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN343,SEARCH(\"AT%\",AN343),,REPT(\" \",25-SEARCH(\"AT%\",AN343)))))),\" \")","v":"LAHU01A01_WOH           AT%M216.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-工作日开启小时*)"}]
[null,{"$f":"IF(OR(G343=\"REAL\",G343=\"DWORD\",G343=\"DINT\"),(IF(OR(G344=\"REAL\",G344=\"DWORD\",G344=\"DINT\"),B343+4+MOD(B343,4),B343+4)),(IF(OR(G344=\"REAL\",G344=\"DWORD\",G344=\"DINT\"),B343+4+MOD(B343,4),B343+2)))&\".0\"","v":"218.0"},"验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-工作日开启分钟",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","工作日开启分钟","空调机组-工作日开启分钟",{"$f":"VLOOKUP(AH344,List!$B$3:$D$445,2,FALSE)&AJ344&\"_\"&VLOOKUP(AK344,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_WOM"},"LAHU01A01_WOM AT%M218.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-工作日开启分钟*)","LAHU01A01_WOM           AT%M218.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-工作日开启分钟*)"]
[null,"220.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-工作日关闭小时",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","工作日关闭小时","空调机组-工作日关闭小时",{"$f":"VLOOKUP(AH345,List!$B$3:$D$445,2,FALSE)&AJ345&\"_\"&VLOOKUP(AK345,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_WCH"},"LAHU01A01_WCH AT%M220.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-工作日关闭小时*)","LAHU01A01_WCH           AT%M220.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-工作日关闭小时*)"]
[null,"222.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-工作日关闭分钟",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","工作日关闭分钟","空调机组-工作日关闭分钟",{"$f":"VLOOKUP(AH346,List!$B$3:$D$445,2,FALSE)&AJ346&\"_\"&VLOOKUP(AK346,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_WCM"},"LAHU01A01_WCM AT%M222.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-工作日关闭分钟*)","LAHU01A01_WCM           AT%M222.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-工作日关闭分钟*)"]
[null,{"$f":"IF(OR(G346=\"REAL\",G346=\"DWORD\",G346=\"DINT\"),(IF(OR(G347=\"REAL\",G347=\"DWORD\",G347=\"DINT\"),B346+4+MOD(B346,4),B346+4)),(IF(OR(G347=\"REAL\",G347=\"DWORD\",G347=\"DINT\"),B346+4+MOD(B346,4),B346+2)))&\".0\"","v":"224.0"},{"$f":"IF((IF(OR(G347=\"INT \",G347=\"WORD\",G347=\"BOOL\"),MOD(B347,2),MOD(B347,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"INT ",null,null,{"$f":"AH347&AA347&\"-\"&AK347","v":"空调机组BXJ-1AP(KT)1-1-节假日开启小时"},{"$nulls":16},{"$f":"IF(AI347=\"\",\"\",AI347)","v":"BXJ-1AP(KT)1-1"},{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","节假日开启小时",{"$f":"AH347&\"-\"&IF(AI347=\"R\",\"新云平台\"&AK347,AK347)","v":"空调机组-节假日开启小时"},{"$f":"VLOOKUP(AH347,List!$B$3:$D$445,2,FALSE)&AJ347&\"_\"&VLOOKUP(AK347,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_HOH"},{"$f":"_xlfn.IFNA(\"L\"&AM347&\" \"&\"AT%M\"&B347&\" :\"&G347&\";\"&\" \"&\"(*\"&J347&\"*)\",\" \")","v":"LAHU01A01_HOH AT%M224.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-节假日开启小时*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN347,SEARCH(\"AT%\",AN347),,REPT(\" \",25-SEARCH(\"AT%\",AN347))),SEARCH(\":\",REPLACE(AN347,SEARCH(\"AT%\",AN347),,REPT(\" \",25-SEARCH(\"AT%\",AN347)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN347,SEARCH(\"AT%\",AN347),,REPT(\" \",25-SEARCH(\"AT%\",AN347)))))),\" \")","v":"LAHU01A01_HOH           AT%M224.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-节假日开启小时*)"}]
[null,"226.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-节假日开启分钟",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","节假日开启分钟","空调机组-节假日开启分钟",{"$f":"VLOOKUP(AH348,List!$B$3:$D$445,2,FALSE)&AJ348&\"_\"&VLOOKUP(AK348,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_HOM"},"LAHU01A01_HOM AT%M226.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-节假日开启分钟*)","LAHU01A01_HOM           AT%M226.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-节假日开启分钟*)"]
[null,"228.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-节假日关闭小时",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","节假日关闭小时","空调机组-节假日关闭小时",{"$f":"VLOOKUP(AH349,List!$B$3:$D$445,2,FALSE)&AJ349&\"_\"&VLOOKUP(AK349,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_HCH"},"LAHU01A01_HCH AT%M228.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-节假日关闭小时*)","LAHU01A01_HCH           AT%M228.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-节假日关闭小时*)"]
[null,"230.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-节假日关闭分钟",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","01A01","节假日关闭分钟","空调机组-节假日关闭分钟",{"$f":"VLOOKUP(AH350,List!$B$3:$D$445,2,FALSE)&AJ350&\"_\"&VLOOKUP(AK350,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_HCM"},"LAHU01A01_HCM AT%M230.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-节假日关闭分钟*)","LAHU01A01_HCM           AT%M230.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-节假日关闭分钟*)"]
[null,"FCU"]
[null,{"$f":"IF(OR(G350=\"REAL\",G350=\"DWORD\",G350=\"DINT\"),(IF(OR(G352=\"REAL\",G352=\"DWORD\",G352=\"DINT\"),B350+4+MOD(B350,4),B350+4)),(IF(OR(G352=\"REAL\",G352=\"DWORD\",G352=\"DINT\"),B350+4+MOD(B350,4),B350+2)))&\".0\"","v":"232.0"},{"$f":"IF((IF(OR(G352=\"INT \",G352=\"WORD\",G352=\"BOOL\"),MOD(B352,2),MOD(B352,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH352&AA352&\"-\"&AK352","v":"风机盘管BXJ-1AP(KT)1-7-程序控制"},{"$nulls":16},{"$f":"IF(AI352=\"\",\"\",AI352)","v":"BXJ-1AP(KT)1-7"},{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","程序控制",{"$f":"AH352&\"-\"&IF(AI352=\"R\",\"新云平台\"&AK352,AK352)","v":"风机盘管-程序控制"},{"$f":"VLOOKUP(AH352,List!$B$3:$D$445,2,FALSE)&AJ352&\"_\"&VLOOKUP(AK352,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_PC"},{"$f":"_xlfn.IFNA(\"R\"&AM352&\" \"&\"AT%M\"&B352&\" :\"&G352&\";\"&\" \"&\"(*\"&J352&\"*)\",\" \")","v":"RFCU01A01_PC AT%M232.0 :BOOL; (*风机盘管BXJ-1AP(KT)1-7-程序控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN352,SEARCH(\"AT%\",AN352),,REPT(\" \",25-SEARCH(\"AT%\",AN352))),SEARCH(\":\",REPLACE(AN352,SEARCH(\"AT%\",AN352),,REPT(\" \",25-SEARCH(\"AT%\",AN352)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN352,SEARCH(\"AT%\",AN352),,REPT(\" \",25-SEARCH(\"AT%\",AN352)))))),\" \")","v":"RFCU01A01_PC            AT%M232.0      :BOOL; (*风机盘管BXJ-1AP(KT)1-7-程序控制*)"}]
[null,{"$f":"IF(OR(G352=\"REAL\",G352=\"DWORD\",G352=\"DINT\"),(IF(OR(G353=\"REAL\",G353=\"DWORD\",G353=\"DINT\"),B352+4+MOD(B352,4),B352+4)),(IF(OR(G353=\"REAL\",G353=\"DWORD\",G353=\"DINT\"),B352+4+MOD(B352,4),B352+2)))&\".0\"","v":"234.0"},"验证通过",null,null,null,"INT ",null,null,"风机盘管BXJ-1AP(KT)1-7-季节模式",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","季节模式",{"$f":"AH353&\"-\"&IF(AI353=\"R\",\"新云平台\"&AK353,AK353)","v":"风机盘管-季节模式"},{"$f":"VLOOKUP(AH353,List!$B$3:$D$445,2,FALSE)&AJ353&\"_\"&VLOOKUP(AK353,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_SM"},{"$f":"_xlfn.IFNA(\"R\"&AM353&\" \"&\"AT%M\"&B353&\" :\"&G353&\";\"&\" \"&\"(*\"&J353&\"*)\",\" \")","v":"RFCU01A01_SM AT%M234.0 :INT ; (*风机盘管BXJ-1AP(KT)1-7-季节模式*)"},"RFCU01A01_SM            AT%M234.0      :INT ; (*风机盘管BXJ-1AP(KT)1-7-季节模式*)"]
[null,"240.0","验证通过",null,null,null,"REAL",null,null,"风机盘管BXJ-1AP(KT)1-7-设定温度值",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","设定温度值","风机盘管-设定温度值",{"$f":"VLOOKUP(AH354,List!$B$3:$D$445,2,FALSE)&AJ354&\"_\"&VLOOKUP(AK354,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_TSET"},{"$f":"_xlfn.IFNA(\"R\"&AM354&\" \"&\"AT%M\"&B354&\" :\"&G354&\";\"&\" \"&\"(*\"&J354&\"*)\",\" \")","v":"RFCU01A01_TSET AT%M240.0 :REAL; (*风机盘管BXJ-1AP(KT)1-7-设定温度值*)"},"RFCU01A01_TSET          AT%M240.0      :REAL; (*风机盘管BXJ-1AP(KT)1-7-设定温度值*)"]
[null,"244.0","验证通过",null,null,null,"BOOL",null,null,"风机盘管BXJ-1AP(KT)1-7-程序控制",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","程序控制","风机盘管-程序控制",{"$f":"VLOOKUP(AH355,List!$B$3:$D$445,2,FALSE)&AJ355&\"_\"&VLOOKUP(AK355,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_PC"},{"$f":"_xlfn.IFNA(\"L\"&AM355&\" \"&\"AT%M\"&B355&\" :\"&G355&\";\"&\" \"&\"(*\"&J355&\"*)\",\" \")","v":"LFCU01A01_PC AT%M244.0 :BOOL; (*风机盘管BXJ-1AP(KT)1-7-程序控制*)"},"LFCU01A01_PC            AT%M244.0      :BOOL; (*风机盘管BXJ-1AP(KT)1-7-程序控制*)"]
[null,"246.0","验证通过",null,null,null,"INT ",null,null,"风机盘管BXJ-1AP(KT)1-7-季节模式",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","季节模式","风机盘管-季节模式",{"$f":"VLOOKUP(AH356,List!$B$3:$D$445,2,FALSE)&AJ356&\"_\"&VLOOKUP(AK356,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_SM"},"LFCU01A01_SM AT%M246.0 :INT ; (*风机盘管BXJ-1AP(KT)1-7-季节模式*)","LFCU01A01_SM            AT%M246.0      :INT ; (*风机盘管BXJ-1AP(KT)1-7-季节模式*)"]
[null,"252.0","验证通过",null,null,null,"REAL",null,null,"风机盘管BXJ-1AP(KT)1-7-设定温度值",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","设定温度值","风机盘管-设定温度值",{"$f":"VLOOKUP(AH357,List!$B$3:$D$445,2,FALSE)&AJ357&\"_\"&VLOOKUP(AK357,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_TSET"},"LFCU01A01_TSET AT%M252.0 :REAL; (*风机盘管BXJ-1AP(KT)1-7-设定温度值*)","LFCU01A01_TSET          AT%M252.0      :REAL; (*风机盘管BXJ-1AP(KT)1-7-设定温度值*)"]
[null,"256.0","验证通过",null,null,null,"INT ",null,null,"风机盘管BXJ-1AP(KT)1-7-设备状态代码",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","设备状态代码","风机盘管-设备状态代码",{"$f":"VLOOKUP(AH358,List!$B$3:$D$445,2,FALSE)&AJ358&\"_\"&VLOOKUP(AK358,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_SN"},"LFCU01A01_SN AT%M256.0 :INT ; (*风机盘管BXJ-1AP(KT)1-7-设备状态代码*)","LFCU01A01_SN            AT%M256.0      :INT ; (*风机盘管BXJ-1AP(KT)1-7-设备状态代码*)"]
[null,"260.0","验证通过",null,null,null,"REAL",null,null,"风机盘管BXJ-1AP(KT)1-7-温度换算值",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","温度换算值","风机盘管-温度换算值",{"$f":"VLOOKUP(AH359,List!$B$3:$D$445,2,FALSE)&AJ359&\"_\"&VLOOKUP(AK359,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_TS"},"LFCU01A01_TS AT%M260.0 :REAL; (*风机盘管BXJ-1AP(KT)1-7-温度换算值*)","LFCU01A01_TS            AT%M260.0      :REAL; (*风机盘管BXJ-1AP(KT)1-7-温度换算值*)"]
[null,"264.0",{"$f":"IF((IF(OR(G360=\"INT \",G360=\"WORD\",G360=\"BOOL\"),MOD(B360,2),MOD(B360,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"REAL",null,null,{"$f":"AH360&AA360&\"-\"&AK360","v":"风机盘管BXJ-1AP(KT)1-7-电磁阀手动控制"},{"$nulls":16},{"$f":"IF(AI360=\"\",\"\",AI360)","v":"BXJ-1AP(KT)1-7"},{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","电磁阀手动控制",{"$f":"AH360&\"-\"&IF(AI360=\"R\",\"新云平台\"&AK360,AK360)","v":"风机盘管-电磁阀手动控制"},{"$f":"VLOOKUP(AH360,List!$B$3:$D$445,2,FALSE)&AJ360&\"_\"&VLOOKUP(AK360,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_EVMC"},{"$f":"_xlfn.IFNA(\"L\"&AM360&\" \"&\"AT%M\"&B360&\" :\"&G360&\";\"&\" \"&\"(*\"&J360&\"*)\",\" \")","v":"LFCU01A01_EVMC AT%M264.0 :REAL; (*风机盘管BXJ-1AP(KT)1-7-电磁阀手动控制*)"},"LFCU01A01_EVMC          AT%M264.0      :REAL; (*风机盘管BXJ-1AP(KT)1-7-电磁阀手动控制*)"]
[null,"268.0","验证通过",null,null,null,"BOOL",null,null,"风机盘管BXJ-1AP(KT)1-7-电磁阀手动控制值",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","电磁阀手动控制值","风机盘管-电磁阀手动控制值",{"$f":"VLOOKUP(AH361,List!$B$3:$D$445,2,FALSE)&AJ361&\"_\"&VLOOKUP(AK361,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_EVMV"},"LFCU01A01_EVMV AT%M268.0 :BOOL; (*风机盘管BXJ-1AP(KT)1-7-电磁阀手动控制值*)","LFCU01A01_EVMV          AT%M268.0      :BOOL; (*风机盘管BXJ-1AP(KT)1-7-电磁阀手动控制值*)"]
[null,"270.0",{"$f":"IF((IF(OR(G362=\"INT \",G362=\"WORD\",G362=\"BOOL\"),MOD(B362,2),MOD(B362,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH362&AA362&\"-\"&AK362","v":"风机盘管BXJ-1AP(KT)1-7-运行时间累积重置"},{"$nulls":16},{"$f":"IF(AI362=\"\",\"\",AI362)","v":"BXJ-1AP(KT)1-7"},{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","运行时间累积重置",{"$f":"AH362&\"-\"&IF(AI362=\"R\",\"新云平台\"&AK362,AK362)","v":"风机盘管-运行时间累积重置"},{"$f":"VLOOKUP(AH362,List!$B$3:$D$445,2,FALSE)&AJ362&\"_\"&VLOOKUP(AK362,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_RST"},{"$f":"_xlfn.IFNA(\"L\"&AM362&\" \"&\"AT%M\"&B362&\" :\"&G362&\";\"&\" \"&\"(*\"&J362&\"*)\",\" \")","v":"LFCU01A01_RST AT%M270.0 :BOOL; (*风机盘管BXJ-1AP(KT)1-7-运行时间累积重置*)"},"LFCU01A01_RST           AT%M270.0      :BOOL; (*风机盘管BXJ-1AP(KT)1-7-运行时间累积重置*)"]
[null,"276.0","验证通过",null,null,null,"REAL",null,null,"风机盘管BXJ-1AP(KT)1-7-运行时间累积重置值",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","运行时间累积重置值","风机盘管-运行时间累积重置值",{"$f":"VLOOKUP(AH363,List!$B$3:$D$445,2,FALSE)&AJ363&\"_\"&VLOOKUP(AK363,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_RSTV"},"LFCU01A01_RSTV AT%M276.0 :REAL; (*风机盘管BXJ-1AP(KT)1-7-运行时间累积重置值*)","LFCU01A01_RSTV          AT%M276.0      :REAL; (*风机盘管BXJ-1AP(KT)1-7-运行时间累积重置值*)"]
[null,"280.0","验证通过",null,null,null,"REAL",null,null,"风机盘管BXJ-1AP(KT)1-7-运行时间累积值",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","运行时间累积值","风机盘管-运行时间累积值",{"$f":"VLOOKUP(AH364,List!$B$3:$D$445,2,FALSE)&AJ364&\"_\"&VLOOKUP(AK364,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_RH"},"LFCU01A01_RH AT%M280.0 :REAL; (*风机盘管BXJ-1AP(KT)1-7-运行时间累积值*)","LFCU01A01_RH            AT%M280.0      :REAL; (*风机盘管BXJ-1AP(KT)1-7-运行时间累积值*)"]
[null,"284.0",{"$f":"IF((IF(OR(G365=\"INT \",G365=\"WORD\",G365=\"BOOL\"),MOD(B365,2),MOD(B365,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH365&AA365&\"-\"&AK365","v":"风机盘管BXJ-1AP(KT)1-7-隔离开关1"},{"$nulls":16},{"$f":"IF(AI365=\"\",\"\",AI365)","v":"BXJ-1AP(KT)1-7"},{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","隔离开关1",{"$f":"AH365&\"-\"&IF(AI365=\"R\",\"新云平台\"&AK365,AK365)","v":"风机盘管-隔离开关1"},{"$f":"VLOOKUP(AH365,List!$B$3:$D$445,2,FALSE)&AJ365&\"_\"&VLOOKUP(AK365,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_ISO1"},{"$f":"_xlfn.IFNA(\"L\"&AM365&\" \"&\"AT%M\"&B365&\" :\"&G365&\";\"&\" \"&\"(*\"&J365&\"*)\",\" \")","v":"LFCU01A01_ISO1 AT%M284.0 :BOOL; (*风机盘管BXJ-1AP(KT)1-7-隔离开关1*)"},"LFCU01A01_ISO1          AT%M284.0      :BOOL; (*风机盘管BXJ-1AP(KT)1-7-隔离开关1*)"]
[null,"286.0","验证通过",null,null,null,"BOOL",null,null,"风机盘管BXJ-1AP(KT)1-7-定时模式",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","定时模式","风机盘管-定时模式",{"$f":"VLOOKUP(AH366,List!$B$3:$D$445,2,FALSE)&AJ366&\"_\"&VLOOKUP(AK366,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_TM"},"LFCU01A01_TM AT%M286.0 :BOOL; (*风机盘管BXJ-1AP(KT)1-7-定时模式*)","LFCU01A01_TM            AT%M286.0      :BOOL; (*风机盘管BXJ-1AP(KT)1-7-定时模式*)"]
[null,"288.0","验证通过",null,null,null,"BOOL",null,null,"风机盘管BXJ-1AP(KT)1-7-定时控制",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","定时控制","风机盘管-定时控制",{"$f":"VLOOKUP(AH367,List!$B$3:$D$445,2,FALSE)&AJ367&\"_\"&VLOOKUP(AK367,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_TC"},"LFCU01A01_TC AT%M288.0 :BOOL; (*风机盘管BXJ-1AP(KT)1-7-定时控制*)","LFCU01A01_TC            AT%M288.0      :BOOL; (*风机盘管BXJ-1AP(KT)1-7-定时控制*)"]
[null,"290.0","验证通过",null,null,null,"INT ",null,null,"风机盘管BXJ-1AP(KT)1-7-工作日开启小时",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","工作日开启小时","风机盘管-工作日开启小时",{"$f":"VLOOKUP(AH368,List!$B$3:$D$445,2,FALSE)&AJ368&\"_\"&VLOOKUP(AK368,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_WOH"},"LFCU01A01_WOH AT%M290.0 :INT ; (*风机盘管BXJ-1AP(KT)1-7-工作日开启小时*)","LFCU01A01_WOH           AT%M290.0      :INT ; (*风机盘管BXJ-1AP(KT)1-7-工作日开启小时*)"]
[null,"292.0","验证通过",null,null,null,"INT ",null,null,"风机盘管BXJ-1AP(KT)1-7-工作日开启分钟",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","工作日开启分钟","风机盘管-工作日开启分钟",{"$f":"VLOOKUP(AH369,List!$B$3:$D$445,2,FALSE)&AJ369&\"_\"&VLOOKUP(AK369,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_WOM"},"LFCU01A01_WOM AT%M292.0 :INT ; (*风机盘管BXJ-1AP(KT)1-7-工作日开启分钟*)","LFCU01A01_WOM           AT%M292.0      :INT ; (*风机盘管BXJ-1AP(KT)1-7-工作日开启分钟*)"]
[null,"294.0","验证通过",null,null,null,"INT ",null,null,"风机盘管BXJ-1AP(KT)1-7-工作日关闭小时",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","工作日关闭小时","风机盘管-工作日关闭小时",{"$f":"VLOOKUP(AH370,List!$B$3:$D$445,2,FALSE)&AJ370&\"_\"&VLOOKUP(AK370,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_WCH"},"LFCU01A01_WCH AT%M294.0 :INT ; (*风机盘管BXJ-1AP(KT)1-7-工作日关闭小时*)","LFCU01A01_WCH           AT%M294.0      :INT ; (*风机盘管BXJ-1AP(KT)1-7-工作日关闭小时*)"]
[null,"296.0","验证通过",null,null,null,"INT ",null,null,"风机盘管BXJ-1AP(KT)1-7-工作日关闭分钟",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","工作日关闭分钟","风机盘管-工作日关闭分钟",{"$f":"VLOOKUP(AH371,List!$B$3:$D$445,2,FALSE)&AJ371&\"_\"&VLOOKUP(AK371,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_WCM"},"LFCU01A01_WCM AT%M296.0 :INT ; (*风机盘管BXJ-1AP(KT)1-7-工作日关闭分钟*)","LFCU01A01_WCM           AT%M296.0      :INT ; (*风机盘管BXJ-1AP(KT)1-7-工作日关闭分钟*)"]
[null,"298.0","验证通过",null,null,null,"INT ",null,null,"风机盘管BXJ-1AP(KT)1-7-节假日开启小时",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","节假日开启小时","风机盘管-节假日开启小时",{"$f":"VLOOKUP(AH372,List!$B$3:$D$445,2,FALSE)&AJ372&\"_\"&VLOOKUP(AK372,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_HOH"},"LFCU01A01_HOH AT%M298.0 :INT ; (*风机盘管BXJ-1AP(KT)1-7-节假日开启小时*)","LFCU01A01_HOH           AT%M298.0      :INT ; (*风机盘管BXJ-1AP(KT)1-7-节假日开启小时*)"]
[null,"300.0","验证通过",null,null,null,"INT ",null,null,"风机盘管BXJ-1AP(KT)1-7-节假日开启分钟",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","节假日开启分钟","风机盘管-节假日开启分钟",{"$f":"VLOOKUP(AH373,List!$B$3:$D$445,2,FALSE)&AJ373&\"_\"&VLOOKUP(AK373,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_HOM"},"LFCU01A01_HOM AT%M300.0 :INT ; (*风机盘管BXJ-1AP(KT)1-7-节假日开启分钟*)","LFCU01A01_HOM           AT%M300.0      :INT ; (*风机盘管BXJ-1AP(KT)1-7-节假日开启分钟*)"]
[null,"302.0","验证通过",null,null,null,"INT ",null,null,"风机盘管BXJ-1AP(KT)1-7-节假日关闭小时",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","节假日关闭小时","风机盘管-节假日关闭小时",{"$f":"VLOOKUP(AH374,List!$B$3:$D$445,2,FALSE)&AJ374&\"_\"&VLOOKUP(AK374,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_HCH"},"LFCU01A01_HCH AT%M302.0 :INT ; (*风机盘管BXJ-1AP(KT)1-7-节假日关闭小时*)","LFCU01A01_HCH           AT%M302.0      :INT ; (*风机盘管BXJ-1AP(KT)1-7-节假日关闭小时*)"]
[null,"304.0","验证通过",null,null,null,"INT ",null,null,"风机盘管BXJ-1AP(KT)1-7-节假日关闭分钟",{"$nulls":16},"BXJ-1AP(KT)1-7",{"$nulls":6},"风机盘管","BXJ-1AP(KT)1-7","01A01","节假日关闭分钟","风机盘管-节假日关闭分钟",{"$f":"VLOOKUP(AH375,List!$B$3:$D$445,2,FALSE)&AJ375&\"_\"&VLOOKUP(AK375,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_HCM"},"LFCU01A01_HCM AT%M304.0 :INT ; (*风机盘管BXJ-1AP(KT)1-7-节假日关闭分钟*)","LFCU01A01_HCM           AT%M304.0      :INT ; (*风机盘管BXJ-1AP(KT)1-7-节假日关闭分钟*)"]
[null,"PAU"]
[null,{"$f":"IF(OR(G375=\"REAL\",G375=\"DWORD\",G375=\"DINT\"),(IF(OR(G377=\"REAL\",G377=\"DWORD\",G377=\"DINT\"),B375+4+MOD(B375,4),B375+4)),(IF(OR(G377=\"REAL\",G377=\"DWORD\",G377=\"DINT\"),B375+4+MOD(B375,4),B375+2)))&\".0\"","v":"306.0"},{"$f":"IF((IF(OR(G377=\"INT \",G377=\"WORD\",G377=\"BOOL\"),MOD(B377,2),MOD(B377,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH377&AA377&\"-\"&AK377","v":"P新风机组BXJ-1AP(KT)1-2-程序控制"},{"$nulls":16},{"$f":"IF(AI377=\"\",\"\",AI377)","v":"BXJ-1AP(KT)1-2"},{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","程序控制",{"$f":"AH377&\"-\"&IF(AI377=\"R\",\"新云平台\"&AK377,AK377)","v":"P新风机组-程序控制"},{"$f":"VLOOKUP(AH377,List!$B$3:$D$445,2,FALSE)&AJ377&\"_\"&VLOOKUP(AK377,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_PC"},{"$f":"_xlfn.IFNA(\"R\"&AM377&\" \"&\"AT%M\"&B377&\" :\"&G377&\";\"&\" \"&\"(*\"&J377&\"*)\",\" \")","v":"RPAU01A02_PC AT%M306.0 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-程序控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN377,SEARCH(\"AT%\",AN377),,REPT(\" \",25-SEARCH(\"AT%\",AN377))),SEARCH(\":\",REPLACE(AN377,SEARCH(\"AT%\",AN377),,REPT(\" \",25-SEARCH(\"AT%\",AN377)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN377,SEARCH(\"AT%\",AN377),,REPT(\" \",25-SEARCH(\"AT%\",AN377)))))),\" \")","v":"RPAU01A02_PC            AT%M306.0      :BOOL; (*P新风机组BXJ-1AP(KT)1-2-程序控制*)"}]
[null,{"$f":"IF(OR(G377=\"REAL\",G377=\"DWORD\",G377=\"DINT\"),(IF(OR(G378=\"REAL\",G378=\"DWORD\",G378=\"DINT\"),B377+4+MOD(B377,4),B377+4)),(IF(OR(G378=\"REAL\",G378=\"DWORD\",G378=\"DINT\"),B377+4+MOD(B377,4),B377+2)))&\".0\"","v":"308.0"},"验证通过",null,null,null,"INT ",null,null,"P新风机组BXJ-1AP(KT)1-2-季节模式",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","季节模式",{"$f":"AH378&\"-\"&IF(AI378=\"R\",\"新云平台\"&AK378,AK378)","v":"P新风机组-季节模式"},{"$f":"VLOOKUP(AH378,List!$B$3:$D$445,2,FALSE)&AJ378&\"_\"&VLOOKUP(AK378,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_SM"},{"$f":"_xlfn.IFNA(\"R\"&AM378&\" \"&\"AT%M\"&B378&\" :\"&G378&\";\"&\" \"&\"(*\"&J378&\"*)\",\" \")","v":"RPAU01A02_SM AT%M308.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-季节模式*)"},"RPAU01A02_SM            AT%M308.0      :INT ; (*P新风机组BXJ-1AP(KT)1-2-季节模式*)"]
[null,"312.0","验证通过",null,null,null,"REAL",null,null,"P新风机组BXJ-1AP(KT)1-2-设定温度值",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","设定温度值","P新风机组-设定温度值",{"$f":"VLOOKUP(AH379,List!$B$3:$D$445,2,FALSE)&AJ379&\"_\"&VLOOKUP(AK379,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_TSET"},{"$f":"_xlfn.IFNA(\"R\"&AM379&\" \"&\"AT%M\"&B379&\" :\"&G379&\";\"&\" \"&\"(*\"&J379&\"*)\",\" \")","v":"RPAU01A02_TSET AT%M312.0 :REAL; (*P新风机组BXJ-1AP(KT)1-2-设定温度值*)"},"RPAU01A02_TSET          AT%M312.0      :REAL; (*P新风机组BXJ-1AP(KT)1-2-设定温度值*)"]
[null,"316.0","验证通过",null,null,null,"BOOL",null,null,"P新风机组BXJ-1AP(KT)1-2-程序控制",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","程序控制","P新风机组-程序控制",{"$f":"VLOOKUP(AH380,List!$B$3:$D$445,2,FALSE)&AJ380&\"_\"&VLOOKUP(AK380,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_PC"},{"$f":"_xlfn.IFNA(\"L\"&AM380&\" \"&\"AT%M\"&B380&\" :\"&G380&\";\"&\" \"&\"(*\"&J380&\"*)\",\" \")","v":"LPAU01A02_PC AT%M316.0 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-程序控制*)"},"LPAU01A02_PC            AT%M316.0      :BOOL; (*P新风机组BXJ-1AP(KT)1-2-程序控制*)"]
[null,"318.0","验证通过",null,null,null,"INT ",null,null,"P新风机组BXJ-1AP(KT)1-2-季节模式",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","季节模式","P新风机组-季节模式",{"$f":"VLOOKUP(AH381,List!$B$3:$D$445,2,FALSE)&AJ381&\"_\"&VLOOKUP(AK381,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_SM"},"LPAU01A02_SM AT%M318.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-季节模式*)","LPAU01A02_SM            AT%M318.0      :INT ; (*P新风机组BXJ-1AP(KT)1-2-季节模式*)"]
[null,"324.0","验证通过",null,null,null,"REAL",null,null,"P新风机组BXJ-1AP(KT)1-2-设定温度值",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","设定温度值","P新风机组-设定温度值",{"$f":"VLOOKUP(AH382,List!$B$3:$D$445,2,FALSE)&AJ382&\"_\"&VLOOKUP(AK382,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_TSET"},"LPAU01A02_TSET AT%M324.0 :REAL; (*P新风机组BXJ-1AP(KT)1-2-设定温度值*)","LPAU01A02_TSET          AT%M324.0      :REAL; (*P新风机组BXJ-1AP(KT)1-2-设定温度值*)"]
[null,"328.0","验证通过",null,null,null,"INT ",null,null,"P新风机组BXJ-1AP(KT)1-2-设备状态代码",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","设备状态代码","P新风机组-设备状态代码",{"$f":"VLOOKUP(AH383,List!$B$3:$D$445,2,FALSE)&AJ383&\"_\"&VLOOKUP(AK383,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_SN"},"LPAU01A02_SN AT%M328.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-设备状态代码*)","LPAU01A02_SN            AT%M328.0      :INT ; (*P新风机组BXJ-1AP(KT)1-2-设备状态代码*)"]
[null,"332.0","验证通过",null,null,null,"REAL",null,null,"P新风机组BXJ-1AP(KT)1-2-送风温度换算值",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","送风温度换算值","P新风机组-送风温度换算值",{"$f":"VLOOKUP(AH384,List!$B$3:$D$445,2,FALSE)&AJ384&\"_\"&VLOOKUP(AK384,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_STS"},"LPAU01A02_STS AT%M332.0 :REAL; (*P新风机组BXJ-1AP(KT)1-2-送风温度换算值*)","LPAU01A02_STS           AT%M332.0      :REAL; (*P新风机组BXJ-1AP(KT)1-2-送风温度换算值*)"]
[null,"336.0",{"$f":"IF((IF(OR(G385=\"INT \",G385=\"WORD\",G385=\"BOOL\"),MOD(B385,2),MOD(B385,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"REAL",null,null,{"$f":"AH385&AA385&\"-\"&AK385","v":"P新风机组BXJ-1AP(KT)1-2-水阀反馈换算值"},{"$nulls":16},{"$f":"IF(AI385=\"\",\"\",AI385)","v":"BXJ-1AP(KT)1-2"},{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","水阀反馈换算值",{"$f":"AH385&\"-\"&IF(AI385=\"R\",\"新云平台\"&AK385,AK385)","v":"P新风机组-水阀反馈换算值"},{"$f":"VLOOKUP(AH385,List!$B$3:$D$445,2,FALSE)&AJ385&\"_\"&VLOOKUP(AK385,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_WVBS"},{"$f":"_xlfn.IFNA(\"L\"&AM385&\" \"&\"AT%M\"&B385&\" :\"&G385&\";\"&\" \"&\"(*\"&J385&\"*)\",\" \")","v":"LPAU01A02_WVBS AT%M336.0 :REAL; (*P新风机组BXJ-1AP(KT)1-2-水阀反馈换算值*)"},"LPAU01A02_WVBS          AT%M336.0      :REAL; (*P新风机组BXJ-1AP(KT)1-2-水阀反馈换算值*)"]
[null,"340.0","验证通过",null,null,null,"BOOL",null,null,"P新风机组BXJ-1AP(KT)1-2-水阀手动控制",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","水阀手动控制","P新风机组-水阀手动控制",{"$f":"VLOOKUP(AH386,List!$B$3:$D$445,2,FALSE)&AJ386&\"_\"&VLOOKUP(AK386,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_WVMC"},"LPAU01A02_WVMC AT%M340.0 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-水阀手动控制*)","LPAU01A02_WVMC          AT%M340.0      :BOOL; (*P新风机组BXJ-1AP(KT)1-2-水阀手动控制*)"]
[null,"344.0","验证通过",null,null,null,"REAL",null,null,"P新风机组BXJ-1AP(KT)1-2-水阀手动控制值",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","水阀手动控制值","P新风机组-水阀手动控制值",{"$f":"VLOOKUP(AH387,List!$B$3:$D$445,2,FALSE)&AJ387&\"_\"&VLOOKUP(AK387,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_WVMV"},"LPAU01A02_WVMV AT%M344.0 :REAL; (*P新风机组BXJ-1AP(KT)1-2-水阀手动控制值*)","LPAU01A02_WVMV          AT%M344.0      :REAL; (*P新风机组BXJ-1AP(KT)1-2-水阀手动控制值*)"]
[null,"348.0","验证通过",null,null,null,"INT ",null,null,"P新风机组BXJ-1AP(KT)1-2-水阀控制转换值",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","水阀控制转换值","P新风机组-水阀控制转换值",{"$f":"VLOOKUP(AH388,List!$B$3:$D$445,2,FALSE)&AJ388&\"_\"&VLOOKUP(AK388,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_WVCS"},"LPAU01A02_WVCS AT%M348.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-水阀控制转换值*)","LPAU01A02_WVCS          AT%M348.0      :INT ; (*P新风机组BXJ-1AP(KT)1-2-水阀控制转换值*)"]
[null,"350.0",{"$f":"IF((IF(OR(G389=\"INT \",G389=\"WORD\",G389=\"BOOL\"),MOD(B389,2),MOD(B389,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH389&AA389&\"-\"&AK389","v":"P新风机组BXJ-1AP(KT)1-2-运行时间累积重置"},{"$nulls":16},{"$f":"IF(AI389=\"\",\"\",AI389)","v":"BXJ-1AP(KT)1-2"},{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","运行时间累积重置",{"$f":"AH389&\"-\"&IF(AI389=\"R\",\"新云平台\"&AK389,AK389)","v":"P新风机组-运行时间累积重置"},{"$f":"VLOOKUP(AH389,List!$B$3:$D$445,2,FALSE)&AJ389&\"_\"&VLOOKUP(AK389,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_RST"},{"$f":"_xlfn.IFNA(\"L\"&AM389&\" \"&\"AT%M\"&B389&\" :\"&G389&\";\"&\" \"&\"(*\"&J389&\"*)\",\" \")","v":"LPAU01A02_RST AT%M350.0 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-运行时间累积重置*)"},"LPAU01A02_RST           AT%M350.0      :BOOL; (*P新风机组BXJ-1AP(KT)1-2-运行时间累积重置*)"]
[null,"356.0","验证通过",null,null,null,"REAL",null,null,"P新风机组BXJ-1AP(KT)1-2-运行时间累积重置值",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","运行时间累积重置值","P新风机组-运行时间累积重置值",{"$f":"VLOOKUP(AH390,List!$B$3:$D$445,2,FALSE)&AJ390&\"_\"&VLOOKUP(AK390,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_RSTV"},"LPAU01A02_RSTV AT%M356.0 :REAL; (*P新风机组BXJ-1AP(KT)1-2-运行时间累积重置值*)","LPAU01A02_RSTV          AT%M356.0      :REAL; (*P新风机组BXJ-1AP(KT)1-2-运行时间累积重置值*)"]
[null,"360.0","验证通过",null,null,null,"REAL",null,null,"P新风机组BXJ-1AP(KT)1-2-运行时间累积值",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","运行时间累积值","P新风机组-运行时间累积值",{"$f":"VLOOKUP(AH391,List!$B$3:$D$445,2,FALSE)&AJ391&\"_\"&VLOOKUP(AK391,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_RH"},"LPAU01A02_RH AT%M360.0 :REAL; (*P新风机组BXJ-1AP(KT)1-2-运行时间累积值*)","LPAU01A02_RH            AT%M360.0      :REAL; (*P新风机组BXJ-1AP(KT)1-2-运行时间累积值*)"]
[null,"364.0",{"$f":"IF((IF(OR(G392=\"INT \",G392=\"WORD\",G392=\"BOOL\"),MOD(B392,2),MOD(B392,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH392&AA392&\"-\"&AK392","v":"P新风机组BXJ-1AP(KT)1-2-隔离开关1"},{"$nulls":16},{"$f":"IF(AI392=\"\",\"\",AI392)","v":"BXJ-1AP(KT)1-2"},{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","隔离开关1",{"$f":"AH392&\"-\"&IF(AI392=\"R\",\"新云平台\"&AK392,AK392)","v":"P新风机组-隔离开关1"},{"$f":"VLOOKUP(AH392,List!$B$3:$D$445,2,FALSE)&AJ392&\"_\"&VLOOKUP(AK392,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_ISO1"},{"$f":"_xlfn.IFNA(\"L\"&AM392&\" \"&\"AT%M\"&B392&\" :\"&G392&\";\"&\" \"&\"(*\"&J392&\"*)\",\" \")","v":"LPAU01A02_ISO1 AT%M364.0 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-隔离开关1*)"},"LPAU01A02_ISO1          AT%M364.0      :BOOL; (*P新风机组BXJ-1AP(KT)1-2-隔离开关1*)"]
[null,"366.0","验证通过",null,null,null,"BOOL",null,null,"P新风机组BXJ-1AP(KT)1-2-隔离开关2",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","隔离开关2","P新风机组-隔离开关2",{"$f":"VLOOKUP(AH393,List!$B$3:$D$445,2,FALSE)&AJ393&\"_\"&VLOOKUP(AK393,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_ISO2"},"LPAU01A02_ISO2 AT%M366.0 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-隔离开关2*)","LPAU01A02_ISO2          AT%M366.0      :BOOL; (*P新风机组BXJ-1AP(KT)1-2-隔离开关2*)"]
[null,"368.0",{"$f":"IF((IF(OR(G394=\"INT \",G394=\"WORD\",G394=\"BOOL\"),MOD(B394,2),MOD(B394,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH394&AA394&\"-\"&AK394","v":"P新风机组BXJ-1AP(KT)1-2-隔离开关3"},{"$nulls":16},{"$f":"IF(AI394=\"\",\"\",AI394)","v":"BXJ-1AP(KT)1-2"},{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","隔离开关3",{"$f":"AH394&\"-\"&IF(AI394=\"R\",\"新云平台\"&AK394,AK394)","v":"P新风机组-隔离开关3"},{"$f":"VLOOKUP(AH394,List!$B$3:$D$445,2,FALSE)&AJ394&\"_\"&VLOOKUP(AK394,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_ISO3"},{"$f":"_xlfn.IFNA(\"L\"&AM394&\" \"&\"AT%M\"&B394&\" :\"&G394&\";\"&\" \"&\"(*\"&J394&\"*)\",\" \")","v":"LPAU01A02_ISO3 AT%M368.0 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-隔离开关3*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN394,SEARCH(\"AT%\",AN394),,REPT(\" \",25-SEARCH(\"AT%\",AN394))),SEARCH(\":\",REPLACE(AN394,SEARCH(\"AT%\",AN394),,REPT(\" \",25-SEARCH(\"AT%\",AN394)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN394,SEARCH(\"AT%\",AN394),,REPT(\" \",25-SEARCH(\"AT%\",AN394)))))),\" \")","v":"LPAU01A02_ISO3          AT%M368.0      :BOOL; (*P新风机组BXJ-1AP(KT)1-2-隔离开关3*)"}]
[null,"372.0","验证通过",null,null,null,"REAL",null,null,"P新风机组BXJ-1AP(KT)1-2-P调节参数",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","P调节参数","P新风机组-P调节参数",{"$f":"VLOOKUP(AH395,List!$B$3:$D$445,2,FALSE)&AJ395&\"_\"&VLOOKUP(AK395,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_VP"},"LPAU01A02_VP AT%M372.0 :REAL; (*P新风机组BXJ-1AP(KT)1-2-P调节参数*)","LPAU01A02_VP            AT%M372.0      :REAL; (*P新风机组BXJ-1AP(KT)1-2-P调节参数*)"]
[null,"376.0","验证通过",null,null,null,"REAL",null,null,"P新风机组BXJ-1AP(KT)1-2-I调节参数",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","I调节参数","P新风机组-I调节参数",{"$f":"VLOOKUP(AH396,List!$B$3:$D$445,2,FALSE)&AJ396&\"_\"&VLOOKUP(AK396,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_VI"},"LPAU01A02_VI AT%M376.0 :REAL; (*P新风机组BXJ-1AP(KT)1-2-I调节参数*)","LPAU01A02_VI            AT%M376.0      :REAL; (*P新风机组BXJ-1AP(KT)1-2-I调节参数*)"]
[null,{"$f":"IF(OR(G396=\"REAL\",G396=\"DWORD\",G396=\"DINT\"),(IF(OR(G397=\"REAL\",G397=\"DWORD\",G397=\"DINT\"),B396+4+MOD(B396,4),B396+4)),(IF(OR(G397=\"REAL\",G397=\"DWORD\",G397=\"DINT\"),B396+4+MOD(B396,4),B396+2)))&\".0\"","v":"380.0"},{"$f":"IF((IF(OR(G397=\"INT \",G397=\"WORD\",G397=\"BOOL\"),MOD(B397,2),MOD(B397,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"INT ",null,null,{"$f":"AH397&AA397&\"-\"&AK397","v":"P新风机组BXJ-1AP(KT)1-2-变频手动控制值"},{"$nulls":16},{"$f":"IF(AI397=\"\",\"\",AI397)","v":"BXJ-1AP(KT)1-2"},{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","变频手动控制值",{"$f":"AH397&\"-\"&IF(AI397=\"R\",\"新云平台\"&AK397,AK397)","v":"P新风机组-变频手动控制值"},{"$f":"VLOOKUP(AH397,List!$B$3:$D$445,2,FALSE)&AJ397&\"_\"&VLOOKUP(AK397,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_VFMV"},{"$f":"_xlfn.IFNA(\"L\"&AM397&\" \"&\"AT%M\"&B397&\" :\"&G397&\";\"&\" \"&\"(*\"&J397&\"*)\",\" \")","v":"LPAU01A02_VFMV AT%M380.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-变频手动控制值*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN397,SEARCH(\"AT%\",AN397),,REPT(\" \",25-SEARCH(\"AT%\",AN397))),SEARCH(\":\",REPLACE(AN397,SEARCH(\"AT%\",AN397),,REPT(\" \",25-SEARCH(\"AT%\",AN397)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN397,SEARCH(\"AT%\",AN397),,REPT(\" \",25-SEARCH(\"AT%\",AN397)))))),\" \")","v":"LPAU01A02_VFMV          AT%M380.0      :INT ; (*P新风机组BXJ-1AP(KT)1-2-变频手动控制值*)"}]
[null,"382.0","验证通过",null,null,null,"INT ",null,null,"P新风机组BXJ-1AP(KT)1-2-变频器频率反馈值",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","变频器频率反馈值","P新风机组-变频器频率反馈值",{"$f":"VLOOKUP(AH398,List!$B$3:$D$445,2,FALSE)&AJ398&\"_\"&VLOOKUP(AK398,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_VFBS"},"LPAU01A02_VFBS AT%M382.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-变频器频率反馈值*)","LPAU01A02_VFBS          AT%M382.0      :INT ; (*P新风机组BXJ-1AP(KT)1-2-变频器频率反馈值*)"]
[null,"384.0","验证通过",null,null,null,"INT ",null,null,"P新风机组BXJ-1AP(KT)1-2-变频器频率控制值",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","变频器频率控制值","P新风机组-变频器频率控制值",{"$f":"VLOOKUP(AH399,List!$B$3:$D$445,2,FALSE)&AJ399&\"_\"&VLOOKUP(AK399,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_VFCS"},"LPAU01A02_VFCS AT%M384.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-变频器频率控制值*)","LPAU01A02_VFCS          AT%M384.0      :INT ; (*P新风机组BXJ-1AP(KT)1-2-变频器频率控制值*)"]
[null,"386.0","验证通过",null,null,null,"BOOL",null,null,"P新风机组BXJ-1AP(KT)1-2-联动模式",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","联动模式","P新风机组-联动模式",{"$f":"VLOOKUP(AH400,List!$B$3:$D$445,2,FALSE)&AJ400&\"_\"&VLOOKUP(AK400,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_LM"},"LPAU01A02_LM AT%M386.0 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-联动模式*)","LPAU01A02_LM            AT%M386.0      :BOOL; (*P新风机组BXJ-1AP(KT)1-2-联动模式*)"]
[null,"392.0","验证通过",null,null,null,"REAL",null,null,"P新风机组BXJ-1AP(KT)1-2-CO2设定值",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","CO2设定值","P新风机组-CO2设定值",{"$f":"VLOOKUP(AH401,List!$B$3:$D$445,2,FALSE)&AJ401&\"_\"&VLOOKUP(AK401,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_CO2SET"},"LPAU01A02_CO2SET AT%M392.0 :REAL; (*P新风机组BXJ-1AP(KT)1-2-CO2设定值*)","LPAU01A02_CO2SET        AT%M392.0      :REAL; (*P新风机组BXJ-1AP(KT)1-2-CO2设定值*)"]
[null,"396.0","验证通过",null,null,null,"REAL",null,null,"P新风机组BXJ-1AP(KT)1-2-CO2换算值",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","CO2换算值","P新风机组-CO2换算值",{"$f":"VLOOKUP(AH402,List!$B$3:$D$445,2,FALSE)&AJ402&\"_\"&VLOOKUP(AK402,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_CO2S"},"LPAU01A02_CO2S AT%M396.0 :REAL; (*P新风机组BXJ-1AP(KT)1-2-CO2换算值*)","LPAU01A02_CO2S          AT%M396.0      :REAL; (*P新风机组BXJ-1AP(KT)1-2-CO2换算值*)"]
[null,"400.0","验证通过",null,null,null,"BOOL",null,null,"P新风机组BXJ-1AP(KT)1-2-定时模式",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","定时模式","P新风机组-定时模式",{"$f":"VLOOKUP(AH403,List!$B$3:$D$445,2,FALSE)&AJ403&\"_\"&VLOOKUP(AK403,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_TM"},"LPAU01A02_TM AT%M400.0 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-定时模式*)","LPAU01A02_TM            AT%M400.0      :BOOL; (*P新风机组BXJ-1AP(KT)1-2-定时模式*)"]
[null,"402.0","验证通过",null,null,null,"BOOL",null,null,"P新风机组BXJ-1AP(KT)1-2-定时控制",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","定时控制","P新风机组-定时控制",{"$f":"VLOOKUP(AH404,List!$B$3:$D$445,2,FALSE)&AJ404&\"_\"&VLOOKUP(AK404,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_TC"},"LPAU01A02_TC AT%M402.0 :BOOL; (*P新风机组BXJ-1AP(KT)1-2-定时控制*)","LPAU01A02_TC            AT%M402.0      :BOOL; (*P新风机组BXJ-1AP(KT)1-2-定时控制*)"]
[null,"404.0","验证通过",null,null,null,"INT ",null,null,"P新风机组BXJ-1AP(KT)1-2-工作日开启小时",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","工作日开启小时","P新风机组-工作日开启小时",{"$f":"VLOOKUP(AH405,List!$B$3:$D$445,2,FALSE)&AJ405&\"_\"&VLOOKUP(AK405,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_WOH"},"LPAU01A02_WOH AT%M404.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-工作日开启小时*)","LPAU01A02_WOH           AT%M404.0      :INT ; (*P新风机组BXJ-1AP(KT)1-2-工作日开启小时*)"]
[null,"406.0","验证通过",null,null,null,"INT ",null,null,"P新风机组BXJ-1AP(KT)1-2-工作日开启分钟",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","工作日开启分钟","P新风机组-工作日开启分钟",{"$f":"VLOOKUP(AH406,List!$B$3:$D$445,2,FALSE)&AJ406&\"_\"&VLOOKUP(AK406,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_WOM"},"LPAU01A02_WOM AT%M406.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-工作日开启分钟*)","LPAU01A02_WOM           AT%M406.0      :INT ; (*P新风机组BXJ-1AP(KT)1-2-工作日开启分钟*)"]
[null,"408.0","验证通过",null,null,null,"INT ",null,null,"P新风机组BXJ-1AP(KT)1-2-工作日关闭小时",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","工作日关闭小时","P新风机组-工作日关闭小时",{"$f":"VLOOKUP(AH407,List!$B$3:$D$445,2,FALSE)&AJ407&\"_\"&VLOOKUP(AK407,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_WCH"},"LPAU01A02_WCH AT%M408.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-工作日关闭小时*)","LPAU01A02_WCH           AT%M408.0      :INT ; (*P新风机组BXJ-1AP(KT)1-2-工作日关闭小时*)"]
[null,"410.0","验证通过",null,null,null,"INT ",null,null,"P新风机组BXJ-1AP(KT)1-2-工作日关闭分钟",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","工作日关闭分钟","P新风机组-工作日关闭分钟",{"$f":"VLOOKUP(AH408,List!$B$3:$D$445,2,FALSE)&AJ408&\"_\"&VLOOKUP(AK408,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_WCM"},"LPAU01A02_WCM AT%M410.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-工作日关闭分钟*)","LPAU01A02_WCM           AT%M410.0      :INT ; (*P新风机组BXJ-1AP(KT)1-2-工作日关闭分钟*)"]
[null,"412.0","验证通过",null,null,null,"INT ",null,null,"P新风机组BXJ-1AP(KT)1-2-节假日开启小时",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","节假日开启小时","P新风机组-节假日开启小时",{"$f":"VLOOKUP(AH409,List!$B$3:$D$445,2,FALSE)&AJ409&\"_\"&VLOOKUP(AK409,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_HOH"},"LPAU01A02_HOH AT%M412.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-节假日开启小时*)","LPAU01A02_HOH           AT%M412.0      :INT ; (*P新风机组BXJ-1AP(KT)1-2-节假日开启小时*)"]
[null,"414.0","验证通过",null,null,null,"INT ",null,null,"P新风机组BXJ-1AP(KT)1-2-节假日开启分钟",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","节假日开启分钟","P新风机组-节假日开启分钟",{"$f":"VLOOKUP(AH410,List!$B$3:$D$445,2,FALSE)&AJ410&\"_\"&VLOOKUP(AK410,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_HOM"},"LPAU01A02_HOM AT%M414.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-节假日开启分钟*)","LPAU01A02_HOM           AT%M414.0      :INT ; (*P新风机组BXJ-1AP(KT)1-2-节假日开启分钟*)"]
[null,"416.0","验证通过",null,null,null,"INT ",null,null,"P新风机组BXJ-1AP(KT)1-2-节假日关闭小时",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","节假日关闭小时","P新风机组-节假日关闭小时",{"$f":"VLOOKUP(AH411,List!$B$3:$D$445,2,FALSE)&AJ411&\"_\"&VLOOKUP(AK411,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_HCH"},"LPAU01A02_HCH AT%M416.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-节假日关闭小时*)","LPAU01A02_HCH           AT%M416.0      :INT ; (*P新风机组BXJ-1AP(KT)1-2-节假日关闭小时*)"]
[null,"418.0","验证通过",null,null,null,"INT ",null,null,"P新风机组BXJ-1AP(KT)1-2-节假日关闭分钟",{"$nulls":16},"BXJ-1AP(KT)1-2",{"$nulls":6},"P新风机组","BXJ-1AP(KT)1-2","01A02","节假日关闭分钟","P新风机组-节假日关闭分钟",{"$f":"VLOOKUP(AH412,List!$B$3:$D$445,2,FALSE)&AJ412&\"_\"&VLOOKUP(AK412,List!$K$2:$M$447,2,FALSE)","v":"PAU01A02_HCM"},"LPAU01A02_HCM AT%M418.0 :INT ; (*P新风机组BXJ-1AP(KT)1-2-节假日关闭分钟*)","LPAU01A02_HCM           AT%M418.0      :INT ; (*P新风机组BXJ-1AP(KT)1-2-节假日关闭分钟*)"]
[null,"CO"]
[null,{"$f":"IF(OR(G412=\"REAL\",G412=\"DWORD\",G412=\"DINT\"),(IF(OR(G414=\"REAL\",G414=\"DWORD\",G414=\"DINT\"),B412+4+MOD(B412,4),B412+4)),(IF(OR(G414=\"REAL\",G414=\"DWORD\",G414=\"DINT\"),B412+4+MOD(B412,4),B412+2)))&\".0\"","v":"424.0"},{"$f":"IF((IF(OR(G414=\"INT \",G414=\"WORD\",G414=\"BOOL\"),MOD(B414,2),MOD(B414,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"REAL",null,null,{"$f":"AH414&AA414&\"-\"&AK414","v":"室内环境状态CO-1-CO换算值"},{"$nulls":16},{"$f":"IF(AI414=\"\",\"\",AI414)","v":"CO-1"},{"$nulls":6},"室内环境状态","CO-1","B1A01","CO换算值",{"$f":"AH414&\"-\"&IF(AI414=\"R\",\"新云平台\"&AK414,AK414)","v":"室内环境状态-CO换算值"},{"$f":"VLOOKUP(AH414,List!$B$3:$D$445,2,FALSE)&AJ414&\"_\"&VLOOKUP(AK414,List!$K$2:$M$447,2,FALSE)","v":"IESB1A01_COS"},{"$f":"_xlfn.IFNA(\"L\"&AM414&\" \"&\"AT%M\"&B414&\" :\"&G414&\";\"&\" \"&\"(*\"&J414&\"*)\",\" \")","v":"LIESB1A01_COS AT%M424.0 :REAL; (*室内环境状态CO-1-CO换算值*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN414,SEARCH(\"AT%\",AN414),,REPT(\" \",25-SEARCH(\"AT%\",AN414))),SEARCH(\":\",REPLACE(AN414,SEARCH(\"AT%\",AN414),,REPT(\" \",25-SEARCH(\"AT%\",AN414)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN414,SEARCH(\"AT%\",AN414),,REPT(\" \",25-SEARCH(\"AT%\",AN414)))))),\" \")","v":"LIESB1A01_COS           AT%M424.0      :REAL; (*室内环境状态CO-1-CO换算值*)"}]
[null,"EAF"]
[null,{"$f":"IF(OR(G414=\"REAL\",G414=\"DWORD\",G414=\"DINT\"),(IF(OR(G416=\"REAL\",G416=\"DWORD\",G416=\"DINT\"),B414+4+MOD(B414,4),B414+4)),(IF(OR(G416=\"REAL\",G416=\"DWORD\",G416=\"DINT\"),B414+4+MOD(B414,4),B414+2)))&\".0\"","v":"428.0"},{"$f":"IF((IF(OR(G416=\"INT \",G416=\"WORD\",G416=\"BOOL\"),MOD(B416,2),MOD(B416,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH416&AA416&\"-\"&AK416","v":"排风机EAF-B1-01-程序控制"},{"$nulls":16},{"$f":"IF(AI416=\"\",\"\",AI416)","v":"EAF-B1-01"},{"$nulls":6},"排风机","EAF-B1-01","B1A01","程序控制",{"$f":"AH416&\"-\"&IF(AI416=\"R\",\"新云平台\"&AK416,AK416)","v":"排风机-程序控制"},{"$f":"VLOOKUP(AH416,List!$B$3:$D$445,2,FALSE)&AJ416&\"_\"&VLOOKUP(AK416,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_PC"},{"$f":"_xlfn.IFNA(\"R\"&AM416&\" \"&\"AT%M\"&B416&\" :\"&G416&\";\"&\" \"&\"(*\"&J416&\"*)\",\" \")","v":"REAFB1A01_PC AT%M428.0 :BOOL; (*排风机EAF-B1-01-程序控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN416,SEARCH(\"AT%\",AN416),,REPT(\" \",25-SEARCH(\"AT%\",AN416))),SEARCH(\":\",REPLACE(AN416,SEARCH(\"AT%\",AN416),,REPT(\" \",25-SEARCH(\"AT%\",AN416)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN416,SEARCH(\"AT%\",AN416),,REPT(\" \",25-SEARCH(\"AT%\",AN416)))))),\" \")","v":"REAFB1A01_PC            AT%M428.0      :BOOL; (*排风机EAF-B1-01-程序控制*)"}]
[null,{"$f":"IF(OR(G416=\"REAL\",G416=\"DWORD\",G416=\"DINT\"),(IF(OR(G417=\"REAL\",G417=\"DWORD\",G417=\"DINT\"),B416+4+MOD(B416,4),B416+4)),(IF(OR(G417=\"REAL\",G417=\"DWORD\",G417=\"DINT\"),B416+4+MOD(B416,4),B416+2)))&\".0\"","v":"430.0"},"验证通过",null,null,null,"BOOL",null,null,"排风机EAF-B1-01-程序控制",{"$nulls":16},"EAF-B1-01",{"$nulls":6},"排风机","EAF-B1-01","B1A01","程序控制",{"$f":"AH417&\"-\"&IF(AI417=\"R\",\"新云平台\"&AK417,AK417)","v":"排风机-程序控制"},{"$f":"VLOOKUP(AH417,List!$B$3:$D$445,2,FALSE)&AJ417&\"_\"&VLOOKUP(AK417,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_PC"},{"$f":"_xlfn.IFNA(\"L\"&AM417&\" \"&\"AT%M\"&B417&\" :\"&G417&\";\"&\" \"&\"(*\"&J417&\"*)\",\" \")","v":"LEAFB1A01_PC AT%M430.0 :BOOL; (*排风机EAF-B1-01-程序控制*)"},"LEAFB1A01_PC            AT%M430.0      :BOOL; (*排风机EAF-B1-01-程序控制*)"]
[null,"432.0",{"$f":"IF((IF(OR(G418=\"INT \",G418=\"WORD\",G418=\"BOOL\"),MOD(B418,2),MOD(B418,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH418&AA418&\"-\"&AK418","v":"排风机EAF-B1-01-运行时间累积重置"},{"$nulls":16},{"$f":"IF(AI418=\"\",\"\",AI418)","v":"EAF-B1-01"},{"$nulls":6},"排风机","EAF-B1-01","B1A01","运行时间累积重置",{"$f":"AH418&\"-\"&IF(AI418=\"R\",\"新云平台\"&AK418,AK418)","v":"排风机-运行时间累积重置"},{"$f":"VLOOKUP(AH418,List!$B$3:$D$445,2,FALSE)&AJ418&\"_\"&VLOOKUP(AK418,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_RST"},{"$f":"_xlfn.IFNA(\"L\"&AM418&\" \"&\"AT%M\"&B418&\" :\"&G418&\";\"&\" \"&\"(*\"&J418&\"*)\",\" \")","v":"LEAFB1A01_RST AT%M432.0 :BOOL; (*排风机EAF-B1-01-运行时间累积重置*)"},"LEAFB1A01_RST           AT%M432.0      :BOOL; (*排风机EAF-B1-01-运行时间累积重置*)"]
[null,{"$f":"IF(OR(G418=\"REAL\",G418=\"DWORD\",G418=\"DINT\"),(IF(OR(G419=\"REAL\",G419=\"DWORD\",G419=\"DINT\"),B418+4+MOD(B418,4),B418+4)),(IF(OR(G419=\"REAL\",G419=\"DWORD\",G419=\"DINT\"),B418+4+MOD(B418,4),B418+2)))&\".0\"","v":"436.0"},"验证通过",null,null,null,"REAL",null,null,"排风机EAF-B1-01-运行时间累积重置值",{"$nulls":16},"EAF-B1-01",{"$nulls":6},"排风机","EAF-B1-01","B1A01","运行时间累积重置值","排风机-运行时间累积重置值",{"$f":"VLOOKUP(AH419,List!$B$3:$D$445,2,FALSE)&AJ419&\"_\"&VLOOKUP(AK419,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_RSTV"},"LEAFB1A01_RSTV AT%M436.0 :REAL; (*排风机EAF-B1-01-运行时间累积重置值*)","LEAFB1A01_RSTV          AT%M436.0      :REAL; (*排风机EAF-B1-01-运行时间累积重置值*)"]
[null,"440.0","验证通过",null,null,null,"REAL",null,null,"排风机EAF-B1-01-运行时间累积值",{"$nulls":16},"EAF-B1-01",{"$nulls":6},"排风机","EAF-B1-01","B1A01","运行时间累积值","排风机-运行时间累积值",{"$f":"VLOOKUP(AH420,List!$B$3:$D$445,2,FALSE)&AJ420&\"_\"&VLOOKUP(AK420,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_RH"},"LEAFB1A01_RH AT%M440.0 :REAL; (*排风机EAF-B1-01-运行时间累积值*)","LEAFB1A01_RH            AT%M440.0      :REAL; (*排风机EAF-B1-01-运行时间累积值*)"]
[null,"444.0",{"$f":"IF((IF(OR(G421=\"INT \",G421=\"WORD\",G421=\"BOOL\"),MOD(B421,2),MOD(B421,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,"排风机EAF-B1-01-联动模式",{"$nulls":16},"EAF-B1-01",{"$nulls":6},"排风机","EAF-B1-01","B1A01","联动模式","排风机-联动模式",{"$f":"VLOOKUP(AH421,List!$B$3:$D$445,2,FALSE)&AJ421&\"_\"&VLOOKUP(AK421,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_LM"},"LEAFB1A01_LM AT%M444.0 :BOOL; (*排风机EAF-B1-01-联动模式*)","LEAFB1A01_LM            AT%M444.0      :BOOL; (*排风机EAF-B1-01-联动模式*)"]
[null,"448.0","验证通过",null,null,null,"REAL",null,null,"排风机EAF-B1-01-CO设定值",{"$nulls":16},"EAF-B1-01",{"$nulls":6},"排风机","EAF-B1-01","B1A01","CO设定值","排风机-CO设定值",{"$f":"VLOOKUP(AH422,List!$B$3:$D$445,2,FALSE)&AJ422&\"_\"&VLOOKUP(AK422,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_COSET"},"LEAFB1A01_COSET AT%M448.0 :REAL; (*排风机EAF-B1-01-CO设定值*)","LEAFB1A01_COSET         AT%M448.0      :REAL; (*排风机EAF-B1-01-CO设定值*)"]
[null,"452.0","验证通过",null,null,null,"REAL",null,null,{"$f":"AH423&AA423&\"-\"&AK423","v":"排风机EAF-B1-01-温度换算值"},{"$nulls":16},{"$f":"IF(AI423=\"\",\"\",AI423)","v":"EAF-B1-01"},{"$nulls":6},"排风机","EAF-B1-01","B1A01","温度换算值",{"$f":"AH423&\"-\"&IF(AI423=\"R\",\"新云平台\"&AK423,AK423)","v":"排风机-温度换算值"},{"$f":"VLOOKUP(AH423,List!$B$3:$D$445,2,FALSE)&AJ423&\"_\"&VLOOKUP(AK423,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_TS"},{"$f":"_xlfn.IFNA(\"L\"&AM423&\" \"&\"AT%M\"&B423&\" :\"&G423&\";\"&\" \"&\"(*\"&J423&\"*)\",\" \")","v":"LEAFB1A01_TS AT%M452.0 :REAL; (*排风机EAF-B1-01-温度换算值*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN423,SEARCH(\"AT%\",AN423),,REPT(\" \",25-SEARCH(\"AT%\",AN423))),SEARCH(\":\",REPLACE(AN423,SEARCH(\"AT%\",AN423),,REPT(\" \",25-SEARCH(\"AT%\",AN423)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN423,SEARCH(\"AT%\",AN423),,REPT(\" \",25-SEARCH(\"AT%\",AN423)))))),\" \")","v":"LEAFB1A01_TS            AT%M452.0      :REAL; (*排风机EAF-B1-01-温度换算值*)"}]
[null,"456.0",{"$f":"IF((IF(OR(G424=\"INT \",G424=\"WORD\",G424=\"BOOL\"),MOD(B424,2),MOD(B424,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,"排风机EAF-B1-01-隔离开关1",{"$nulls":16},"EAF-B1-01",{"$nulls":6},"排风机","EAF-B1-01","B1A01","隔离开关1","排风机-隔离开关1",{"$f":"VLOOKUP(AH424,List!$B$3:$D$445,2,FALSE)&AJ424&\"_\"&VLOOKUP(AK424,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_ISO1"},"LEAFB1A01_ISO1 AT%M456.0 :BOOL; (*排风机EAF-B1-01-隔离开关1*)","LEAFB1A01_ISO1          AT%M456.0      :BOOL; (*排风机EAF-B1-01-隔离开关1*)"]
[null,"458.0",{"$f":"IF((IF(OR(G425=\"INT \",G425=\"WORD\",G425=\"BOOL\"),MOD(B425,2),MOD(B425,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"INT ",null,null,{"$f":"AH425&AA425&\"-\"&AK425","v":"排风机EAF-B1-01-设备状态代码"},{"$nulls":16},{"$f":"IF(AI425=\"\",\"\",AI425)","v":"EAF-B1-01"},{"$nulls":6},"排风机","EAF-B1-01","B1A01","设备状态代码",{"$f":"AH425&\"-\"&IF(AI425=\"R\",\"新云平台\"&AK425,AK425)","v":"排风机-设备状态代码"},{"$f":"VLOOKUP(AH425,List!$B$3:$D$445,2,FALSE)&AJ425&\"_\"&VLOOKUP(AK425,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_SN"},{"$f":"_xlfn.IFNA(\"L\"&AM425&\" \"&\"AT%M\"&B425&\" :\"&G425&\";\"&\" \"&\"(*\"&J425&\"*)\",\" \")","v":"LEAFB1A01_SN AT%M458.0 :INT ; (*排风机EAF-B1-01-设备状态代码*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN425,SEARCH(\"AT%\",AN425),,REPT(\" \",25-SEARCH(\"AT%\",AN425))),SEARCH(\":\",REPLACE(AN425,SEARCH(\"AT%\",AN425),,REPT(\" \",25-SEARCH(\"AT%\",AN425)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN425,SEARCH(\"AT%\",AN425),,REPT(\" \",25-SEARCH(\"AT%\",AN425)))))),\" \")","v":"LEAFB1A01_SN            AT%M458.0      :INT ; (*排风机EAF-B1-01-设备状态代码*)"}]
[null,"460.0",{"$f":"IF((IF(OR(G426=\"INT \",G426=\"WORD\",G426=\"BOOL\"),MOD(B426,2),MOD(B426,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH426&AA426&\"-\"&AK426","v":"排风机EAF-B1-01-定时模式"},{"$nulls":16},{"$f":"IF(AI426=\"\",\"\",AI426)","v":"EAF-B1-01"},{"$nulls":6},"排风机","EAF-B1-01","B1A01","定时模式",{"$f":"AH426&\"-\"&IF(AI426=\"R\",\"新云平台\"&AK426,AK426)","v":"排风机-定时模式"},{"$f":"VLOOKUP(AH426,List!$B$3:$D$445,2,FALSE)&AJ426&\"_\"&VLOOKUP(AK426,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_TM"},{"$f":"_xlfn.IFNA(\"L\"&AM426&\" \"&\"AT%M\"&B426&\" :\"&G426&\";\"&\" \"&\"(*\"&J426&\"*)\",\" \")","v":"LEAFB1A01_TM AT%M460.0 :BOOL; (*排风机EAF-B1-01-定时模式*)"},"LEAFB1A01_TM            AT%M460.0      :BOOL; (*排风机EAF-B1-01-定时模式*)"]
[null,"462.0","验证通过",null,null,null,"BOOL",null,null,"排风机EAF-B1-01-定时控制",{"$nulls":16},"EAF-B1-01",{"$nulls":6},"排风机","EAF-B1-01","B1A01","定时控制","排风机-定时控制",{"$f":"VLOOKUP(AH427,List!$B$3:$D$445,2,FALSE)&AJ427&\"_\"&VLOOKUP(AK427,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_TC"},"LEAFB1A01_TC AT%M462.0 :BOOL; (*排风机EAF-B1-01-定时控制*)","LEAFB1A01_TC            AT%M462.0      :BOOL; (*排风机EAF-B1-01-定时控制*)"]
[null,"464.0","验证通过",null,null,null,"INT ",null,null,"排风机EAF-B1-01-工作日开启小时",{"$nulls":16},"EAF-B1-01",{"$nulls":6},"排风机","EAF-B1-01","B1A01","工作日开启小时","排风机-工作日开启小时",{"$f":"VLOOKUP(AH428,List!$B$3:$D$445,2,FALSE)&AJ428&\"_\"&VLOOKUP(AK428,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_WOH"},"LEAFB1A01_WOH AT%M464.0 :INT ; (*排风机EAF-B1-01-工作日开启小时*)","LEAFB1A01_WOH           AT%M464.0      :INT ; (*排风机EAF-B1-01-工作日开启小时*)"]
[null,"466.0","验证通过",null,null,null,"INT ",null,null,"排风机EAF-B1-01-工作日开启分钟",{"$nulls":16},"EAF-B1-01",{"$nulls":6},"排风机","EAF-B1-01","B1A01","工作日开启分钟","排风机-工作日开启分钟",{"$f":"VLOOKUP(AH429,List!$B$3:$D$445,2,FALSE)&AJ429&\"_\"&VLOOKUP(AK429,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_WOM"},"LEAFB1A01_WOM AT%M466.0 :INT ; (*排风机EAF-B1-01-工作日开启分钟*)","LEAFB1A01_WOM           AT%M466.0      :INT ; (*排风机EAF-B1-01-工作日开启分钟*)"]
[null,"468.0","验证通过",null,null,null,"INT ",null,null,"排风机EAF-B1-01-工作日关闭小时",{"$nulls":16},"EAF-B1-01",{"$nulls":6},"排风机","EAF-B1-01","B1A01","工作日关闭小时","排风机-工作日关闭小时",{"$f":"VLOOKUP(AH430,List!$B$3:$D$445,2,FALSE)&AJ430&\"_\"&VLOOKUP(AK430,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_WCH"},"LEAFB1A01_WCH AT%M468.0 :INT ; (*排风机EAF-B1-01-工作日关闭小时*)","LEAFB1A01_WCH           AT%M468.0      :INT ; (*排风机EAF-B1-01-工作日关闭小时*)"]
[null,"470.0","验证通过",null,null,null,"INT ",null,null,"排风机EAF-B1-01-工作日关闭分钟",{"$nulls":16},"EAF-B1-01",{"$nulls":6},"排风机","EAF-B1-01","B1A01","工作日关闭分钟","排风机-工作日关闭分钟",{"$f":"VLOOKUP(AH431,List!$B$3:$D$445,2,FALSE)&AJ431&\"_\"&VLOOKUP(AK431,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_WCM"},"LEAFB1A01_WCM AT%M470.0 :INT ; (*排风机EAF-B1-01-工作日关闭分钟*)","LEAFB1A01_WCM           AT%M470.0      :INT ; (*排风机EAF-B1-01-工作日关闭分钟*)"]
[null,"472.0","验证通过",null,null,null,"INT ",null,null,"排风机EAF-B1-01-节假日开启小时",{"$nulls":16},"EAF-B1-01",{"$nulls":6},"排风机","EAF-B1-01","B1A01","节假日开启小时","排风机-节假日开启小时",{"$f":"VLOOKUP(AH432,List!$B$3:$D$445,2,FALSE)&AJ432&\"_\"&VLOOKUP(AK432,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_HOH"},"LEAFB1A01_HOH AT%M472.0 :INT ; (*排风机EAF-B1-01-节假日开启小时*)","LEAFB1A01_HOH           AT%M472.0      :INT ; (*排风机EAF-B1-01-节假日开启小时*)"]
[null,"474.0","验证通过",null,null,null,"INT ",null,null,"排风机EAF-B1-01-节假日开启分钟",{"$nulls":16},"EAF-B1-01",{"$nulls":6},"排风机","EAF-B1-01","B1A01","节假日开启分钟","排风机-节假日开启分钟",{"$f":"VLOOKUP(AH433,List!$B$3:$D$445,2,FALSE)&AJ433&\"_\"&VLOOKUP(AK433,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_HOM"},"LEAFB1A01_HOM AT%M474.0 :INT ; (*排风机EAF-B1-01-节假日开启分钟*)","LEAFB1A01_HOM           AT%M474.0      :INT ; (*排风机EAF-B1-01-节假日开启分钟*)"]
[null,"476.0","验证通过",null,null,null,"INT ",null,null,"排风机EAF-B1-01-节假日关闭小时",{"$nulls":16},"EAF-B1-01",{"$nulls":6},"排风机","EAF-B1-01","B1A01","节假日关闭小时","排风机-节假日关闭小时",{"$f":"VLOOKUP(AH434,List!$B$3:$D$445,2,FALSE)&AJ434&\"_\"&VLOOKUP(AK434,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_HCH"},"LEAFB1A01_HCH AT%M476.0 :INT ; (*排风机EAF-B1-01-节假日关闭小时*)","LEAFB1A01_HCH           AT%M476.0      :INT ; (*排风机EAF-B1-01-节假日关闭小时*)"]
[null,"478.0","验证通过",null,null,null,"INT ",null,null,"排风机EAF-B1-01-节假日关闭分钟",{"$nulls":16},"EAF-B1-01",{"$nulls":6},"排风机","EAF-B1-01","B1A01","节假日关闭分钟","排风机-节假日关闭分钟",{"$f":"VLOOKUP(AH435,List!$B$3:$D$445,2,FALSE)&AJ435&\"_\"&VLOOKUP(AK435,List!$K$2:$M$447,2,FALSE)","v":"EAFB1A01_HCM"},"LEAFB1A01_HCM AT%M478.0 :INT ; (*排风机EAF-B1-01-节假日关闭分钟*)","LEAFB1A01_HCM           AT%M478.0      :INT ; (*排风机EAF-B1-01-节假日关闭分钟*)"]
[null,"SWP"]
[null,{"$f":"IF(OR(G435=\"REAL\",G435=\"DWORD\",G435=\"DINT\"),(IF(OR(G437=\"REAL\",G437=\"DWORD\",G437=\"DINT\"),B435+4+MOD(B435,4),B435+4)),(IF(OR(G437=\"REAL\",G437=\"DWORD\",G437=\"DINT\"),B435+4+MOD(B435,4),B435+2)))&\".0\"","v":"480.0"},{"$f":"IF((IF(OR(G437=\"INT \",G437=\"WORD\",G437=\"BOOL\"),MOD(B437,2),MOD(B437,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH437&AA437&\"-\"&AK437","v":"潜污泵井SUMP-01-运行时间累积重置1"},{"$nulls":16},{"$f":"IF(AI437=\"\",\"\",AI437)","v":"SUMP-01"},{"$nulls":6},"潜污泵井","SUMP-01","B1A01","运行时间累积重置1",{"$f":"AH437&\"-\"&IF(AI437=\"R\",\"新云平台\"&AK437,AK437)","v":"潜污泵井-运行时间累积重置1"},{"$f":"VLOOKUP(AH437,List!$B$3:$D$445,2,FALSE)&AJ437&\"_\"&VLOOKUP(AK437,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_RST1"},{"$f":"_xlfn.IFNA(\"L\"&AM437&\" \"&\"AT%M\"&B437&\" :\"&G437&\";\"&\" \"&\"(*\"&J437&\"*)\",\" \")","v":"LSWPB1A01_RST1 AT%M480.0 :BOOL; (*潜污泵井SUMP-01-运行时间累积重置1*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN437,SEARCH(\"AT%\",AN437),,REPT(\" \",25-SEARCH(\"AT%\",AN437))),SEARCH(\":\",REPLACE(AN437,SEARCH(\"AT%\",AN437),,REPT(\" \",25-SEARCH(\"AT%\",AN437)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN437,SEARCH(\"AT%\",AN437),,REPT(\" \",25-SEARCH(\"AT%\",AN437)))))),\" \")","v":"LSWPB1A01_RST1          AT%M480.0      :BOOL; (*潜污泵井SUMP-01-运行时间累积重置1*)"}]
[null,{"$f":"IF(OR(G437=\"REAL\",G437=\"DWORD\",G437=\"DINT\"),(IF(OR(G438=\"REAL\",G438=\"DWORD\",G438=\"DINT\"),B437+4+MOD(B437,4),B437+4)),(IF(OR(G438=\"REAL\",G438=\"DWORD\",G438=\"DINT\"),B437+4+MOD(B437,4),B437+2)))&\".0\"","v":"484.0"},"验证通过",null,null,null,"REAL",null,null,"潜污泵井SUMP-01-运行时间累积重置值1",{"$nulls":16},"SUMP-01",{"$nulls":6},"潜污泵井","SUMP-01","B1A01","运行时间累积重置值1","潜污泵井-运行时间累积重置值1",{"$f":"VLOOKUP(AH438,List!$B$3:$D$445,2,FALSE)&AJ438&\"_\"&VLOOKUP(AK438,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_RSTV1"},"LSWPB1A01_RSTV1 AT%M484.0 :REAL; (*潜污泵井SUMP-01-运行时间累积重置值1*)","LSWPB1A01_RSTV1         AT%M484.0      :REAL; (*潜污泵井SUMP-01-运行时间累积重置值1*)"]
[null,"488.0","验证通过",null,null,null,"REAL",null,null,"潜污泵井SUMP-01-运行时间累积值1",{"$nulls":16},"SUMP-01",{"$nulls":6},"潜污泵井","SUMP-01","B1A01","运行时间累积值1","潜污泵井-运行时间累积值1",{"$f":"VLOOKUP(AH439,List!$B$3:$D$445,2,FALSE)&AJ439&\"_\"&VLOOKUP(AK439,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_RH1"},"LSWPB1A01_RH1 AT%M488.0 :REAL; (*潜污泵井SUMP-01-运行时间累积值1*)","LSWPB1A01_RH1           AT%M488.0      :REAL; (*潜污泵井SUMP-01-运行时间累积值1*)"]
[null,{"$f":"IF(OR(G439=\"REAL\",G439=\"DWORD\",G439=\"DINT\"),(IF(OR(G440=\"REAL\",G440=\"DWORD\",G440=\"DINT\"),B439+4+MOD(B439,4),B439+4)),(IF(OR(G440=\"REAL\",G440=\"DWORD\",G440=\"DINT\"),B439+4+MOD(B439,4),B439+2)))&\".0\"","v":"492.0"},{"$f":"IF((IF(OR(G440=\"INT \",G440=\"WORD\",G440=\"BOOL\"),MOD(B440,2),MOD(B440,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH440&AA440&\"-\"&AK440","v":"潜污泵井SUMP-01-运行时间累积重置2"},{"$nulls":16},{"$f":"IF(AI440=\"\",\"\",AI440)","v":"SUMP-01"},{"$nulls":6},"潜污泵井","SUMP-01","B1A01","运行时间累积重置2",{"$f":"AH440&\"-\"&IF(AI440=\"R\",\"新云平台\"&AK440,AK440)","v":"潜污泵井-运行时间累积重置2"},{"$f":"VLOOKUP(AH440,List!$B$3:$D$445,2,FALSE)&AJ440&\"_\"&VLOOKUP(AK440,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_RST2"},{"$f":"_xlfn.IFNA(\"L\"&AM440&\" \"&\"AT%M\"&B440&\" :\"&G440&\";\"&\" \"&\"(*\"&J440&\"*)\",\" \")","v":"LSWPB1A01_RST2 AT%M492.0 :BOOL; (*潜污泵井SUMP-01-运行时间累积重置2*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN440,SEARCH(\"AT%\",AN440),,REPT(\" \",25-SEARCH(\"AT%\",AN440))),SEARCH(\":\",REPLACE(AN440,SEARCH(\"AT%\",AN440),,REPT(\" \",25-SEARCH(\"AT%\",AN440)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN440,SEARCH(\"AT%\",AN440),,REPT(\" \",25-SEARCH(\"AT%\",AN440)))))),\" \")","v":"LSWPB1A01_RST2          AT%M492.0      :BOOL; (*潜污泵井SUMP-01-运行时间累积重置2*)"}]
[null,"496.0","验证通过",null,null,null,"REAL",null,null,"潜污泵井SUMP-01-运行时间累积重置值2",{"$nulls":16},"SUMP-01",{"$nulls":6},"潜污泵井","SUMP-01","B1A01","运行时间累积重置值2","潜污泵井-运行时间累积重置值2",{"$f":"VLOOKUP(AH441,List!$B$3:$D$445,2,FALSE)&AJ441&\"_\"&VLOOKUP(AK441,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_RSTV2"},"LSWPB1A01_RSTV2 AT%M496.0 :REAL; (*潜污泵井SUMP-01-运行时间累积重置值2*)","LSWPB1A01_RSTV2         AT%M496.0      :REAL; (*潜污泵井SUMP-01-运行时间累积重置值2*)"]
[null,"500.0","验证通过",null,null,null,"REAL",null,null,"潜污泵井SUMP-01-运行时间累积值2",{"$nulls":16},"SUMP-01",{"$nulls":6},"潜污泵井","SUMP-01","B1A01","运行时间累积值2","潜污泵井-运行时间累积值2",{"$f":"VLOOKUP(AH442,List!$B$3:$D$445,2,FALSE)&AJ442&\"_\"&VLOOKUP(AK442,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_RH2"},"LSWPB1A01_RH2 AT%M500.0 :REAL; (*潜污泵井SUMP-01-运行时间累积值2*)","LSWPB1A01_RH2           AT%M500.0      :REAL; (*潜污泵井SUMP-01-运行时间累积值2*)"]
[null,"504.0",{"$f":"IF((IF(OR(G443=\"INT \",G443=\"WORD\",G443=\"BOOL\"),MOD(B443,2),MOD(B443,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH443&AA443&\"-\"&AK443","v":"潜污泵井SUMP-01-运行时间累积重置3"},{"$nulls":16},{"$f":"IF(AI443=\"\",\"\",AI443)","v":"SUMP-01"},{"$nulls":6},"潜污泵井","SUMP-01","B1A01","运行时间累积重置3",{"$f":"AH443&\"-\"&IF(AI443=\"R\",\"新云平台\"&AK443,AK443)","v":"潜污泵井-运行时间累积重置3"},{"$f":"VLOOKUP(AH443,List!$B$3:$D$445,2,FALSE)&AJ443&\"_\"&VLOOKUP(AK443,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_RST3"},{"$f":"_xlfn.IFNA(\"L\"&AM443&\" \"&\"AT%M\"&B443&\" :\"&G443&\";\"&\" \"&\"(*\"&J443&\"*)\",\" \")","v":"LSWPB1A01_RST3 AT%M504.0 :BOOL; (*潜污泵井SUMP-01-运行时间累积重置3*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN443,SEARCH(\"AT%\",AN443),,REPT(\" \",25-SEARCH(\"AT%\",AN443))),SEARCH(\":\",REPLACE(AN443,SEARCH(\"AT%\",AN443),,REPT(\" \",25-SEARCH(\"AT%\",AN443)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN443,SEARCH(\"AT%\",AN443),,REPT(\" \",25-SEARCH(\"AT%\",AN443)))))),\" \")","v":"LSWPB1A01_RST3          AT%M504.0      :BOOL; (*潜污泵井SUMP-01-运行时间累积重置3*)"}]
[null,"508.0","验证通过",null,null,null,"REAL",null,null,"潜污泵井SUMP-01-运行时间累积重置值3",{"$nulls":16},"SUMP-01",{"$nulls":6},"潜污泵井","SUMP-01","B1A01","运行时间累积重置值3","潜污泵井-运行时间累积重置值3",{"$f":"VLOOKUP(AH444,List!$B$3:$D$445,2,FALSE)&AJ444&\"_\"&VLOOKUP(AK444,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_RSTV3"},"LSWPB1A01_RSTV3 AT%M508.0 :REAL; (*潜污泵井SUMP-01-运行时间累积重置值3*)","LSWPB1A01_RSTV3         AT%M508.0      :REAL; (*潜污泵井SUMP-01-运行时间累积重置值3*)"]
[null,"512.0","验证通过",null,null,null,"REAL",null,null,"潜污泵井SUMP-01-运行时间累积值3",{"$nulls":16},"SUMP-01",{"$nulls":6},"潜污泵井","SUMP-01","B1A01","运行时间累积值3","潜污泵井-运行时间累积值3",{"$f":"VLOOKUP(AH445,List!$B$3:$D$445,2,FALSE)&AJ445&\"_\"&VLOOKUP(AK445,List!$K$2:$M$447,2,FALSE)","v":"SWPB1A01_RH3"},"LSWPB1A01_RH3 AT%M512.0 :REAL; (*潜污泵井SUMP-01-运行时间累积值3*)","LSWPB1A01_RH3           AT%M512.0      :REAL; (*潜污泵井SUMP-01-运行时间累积值3*)"]
[null,"FMJ"]
[null,{"$f":"IF(OR(G445=\"REAL\",G445=\"DWORD\",G445=\"DINT\"),(IF(OR(G447=\"REAL\",G447=\"DWORD\",G447=\"DINT\"),B445+4+MOD(B445,4),B445+4)),(IF(OR(G447=\"REAL\",G447=\"DWORD\",G447=\"DINT\"),B445+4+MOD(B445,4),B445+2)))&\".0\"","v":"516.0"},{"$f":"IF((IF(OR(G447=\"INT \",G447=\"WORD\",G447=\"BOOL\"),MOD(B447,2),MOD(B447,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH447&AA447&\"-\"&AK447","v":"风幕机BXJ-1AP(KT)1-1-程序控制"},{"$nulls":16},{"$f":"IF(AI447=\"\",\"\",AI447)","v":"BXJ-1AP(KT)1-1"},{"$nulls":6},"风幕机","BXJ-1AP(KT)1-1","01A01","程序控制",{"$f":"AH447&\"-\"&IF(AI447=\"R\",\"新云平台\"&AK447,AK447)","v":"风幕机-程序控制"},{"$f":"VLOOKUP(AH447,List!$B$3:$D$445,2,FALSE)&AJ447&\"_\"&VLOOKUP(AK447,List!$K$2:$M$447,2,FALSE)","v":"AC01A01_PC"},{"$f":"_xlfn.IFNA(\"R\"&AM447&\" \"&\"AT%M\"&B447&\" :\"&G447&\";\"&\" \"&\"(*\"&J447&\"*)\",\" \")","v":"RAC01A01_PC AT%M516.0 :BOOL; (*风幕机BXJ-1AP(KT)1-1-程序控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN447,SEARCH(\"AT%\",AN447),,REPT(\" \",25-SEARCH(\"AT%\",AN447))),SEARCH(\":\",REPLACE(AN447,SEARCH(\"AT%\",AN447),,REPT(\" \",25-SEARCH(\"AT%\",AN447)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN447,SEARCH(\"AT%\",AN447),,REPT(\" \",25-SEARCH(\"AT%\",AN447)))))),\" \")","v":"RAC01A01_PC             AT%M516.0      :BOOL; (*风幕机BXJ-1AP(KT)1-1-程序控制*)"}]
[null,{"$f":"IF(OR(G447=\"REAL\",G447=\"DWORD\",G447=\"DINT\"),(IF(OR(G448=\"REAL\",G448=\"DWORD\",G448=\"DINT\"),B447+4+MOD(B447,4),B447+4)),(IF(OR(G448=\"REAL\",G448=\"DWORD\",G448=\"DINT\"),B447+4+MOD(B447,4),B447+2)))&\".0\"","v":"518.0"},"验证通过",null,null,null,"BOOL",null,null,"风幕机BXJ-1AP(KT)1-1-程序控制",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"风幕机","BXJ-1AP(KT)1-1","01A01","程序控制",{"$f":"AH448&\"-\"&IF(AI448=\"R\",\"新云平台\"&AK448,AK448)","v":"风幕机-程序控制"},{"$f":"VLOOKUP(AH448,List!$B$3:$D$445,2,FALSE)&AJ448&\"_\"&VLOOKUP(AK448,List!$K$2:$M$447,2,FALSE)","v":"AC01A01_PC"},{"$f":"_xlfn.IFNA(\"L\"&AM448&\" \"&\"AT%M\"&B448&\" :\"&G448&\";\"&\" \"&\"(*\"&J448&\"*)\",\" \")","v":"LAC01A01_PC AT%M518.0 :BOOL; (*风幕机BXJ-1AP(KT)1-1-程序控制*)"},"LAC01A01_PC             AT%M518.0      :BOOL; (*风幕机BXJ-1AP(KT)1-1-程序控制*)"]
[null,{"$f":"IF(OR(G448=\"REAL\",G448=\"DWORD\",G448=\"DINT\"),(IF(OR(G449=\"REAL\",G449=\"DWORD\",G449=\"DINT\"),B448+4+MOD(B448,4),B448+4)),(IF(OR(G449=\"REAL\",G449=\"DWORD\",G449=\"DINT\"),B448+4+MOD(B448,4),B448+2)))&\".0\"","v":"520.0"},"验证通过",null,null,null,"BOOL",null,null,"风幕机BXJ-1AP(KT)1-1-运行时间累积重置",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"风幕机","BXJ-1AP(KT)1-1","01A01","运行时间累积重置","风幕机-运行时间累积重置",{"$f":"VLOOKUP(AH449,List!$B$3:$D$445,2,FALSE)&AJ449&\"_\"&VLOOKUP(AK449,List!$K$2:$M$447,2,FALSE)","v":"AC01A01_RST"},{"$f":"_xlfn.IFNA(\"L\"&AM449&\" \"&\"AT%M\"&B449&\" :\"&G449&\";\"&\" \"&\"(*\"&J449&\"*)\",\" \")","v":"LAC01A01_RST AT%M520.0 :BOOL; (*风幕机BXJ-1AP(KT)1-1-运行时间累积重置*)"},"LAC01A01_RST            AT%M520.0      :BOOL; (*风幕机BXJ-1AP(KT)1-1-运行时间累积重置*)"]
[null,"524.0","验证通过",null,null,null,"REAL",null,null,"风幕机BXJ-1AP(KT)1-1-运行时间累积重置值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"风幕机","BXJ-1AP(KT)1-1","01A01","运行时间累积重置值","风幕机-运行时间累积重置值",{"$f":"VLOOKUP(AH450,List!$B$3:$D$445,2,FALSE)&AJ450&\"_\"&VLOOKUP(AK450,List!$K$2:$M$447,2,FALSE)","v":"AC01A01_RSTV"},"LAC01A01_RSTV AT%M524.0 :REAL; (*风幕机BXJ-1AP(KT)1-1-运行时间累积重置值*)","LAC01A01_RSTV           AT%M524.0      :REAL; (*风幕机BXJ-1AP(KT)1-1-运行时间累积重置值*)"]
[null,"528.0","验证通过",null,null,null,"REAL",null,null,"风幕机BXJ-1AP(KT)1-1-运行时间累积值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"风幕机","BXJ-1AP(KT)1-1","01A01","运行时间累积值","风幕机-运行时间累积值",{"$f":"VLOOKUP(AH451,List!$B$3:$D$445,2,FALSE)&AJ451&\"_\"&VLOOKUP(AK451,List!$K$2:$M$447,2,FALSE)","v":"AC01A01_RH"},"LAC01A01_RH AT%M528.0 :REAL; (*风幕机BXJ-1AP(KT)1-1-运行时间累积值*)","LAC01A01_RH             AT%M528.0      :REAL; (*风幕机BXJ-1AP(KT)1-1-运行时间累积值*)"]
[null,"532.0",{"$f":"IF((IF(OR(G452=\"INT \",G452=\"WORD\",G452=\"BOOL\"),MOD(B452,2),MOD(B452,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH452&AA452&\"-\"&AK452","v":"风幕机BXJ-1AP(KT)1-1-定时模式"},{"$nulls":16},{"$f":"IF(AI452=\"\",\"\",AI452)","v":"BXJ-1AP(KT)1-1"},{"$nulls":6},"风幕机","BXJ-1AP(KT)1-1","01A01","定时模式",{"$f":"AH452&\"-\"&IF(AI452=\"R\",\"新云平台\"&AK452,AK452)","v":"风幕机-定时模式"},{"$f":"VLOOKUP(AH452,List!$B$3:$D$445,2,FALSE)&AJ452&\"_\"&VLOOKUP(AK452,List!$K$2:$M$447,2,FALSE)","v":"AC01A01_TM"},{"$f":"_xlfn.IFNA(\"L\"&AM452&\" \"&\"AT%M\"&B452&\" :\"&G452&\";\"&\" \"&\"(*\"&J452&\"*)\",\" \")","v":"LAC01A01_TM AT%M532.0 :BOOL; (*风幕机BXJ-1AP(KT)1-1-定时模式*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN452,SEARCH(\"AT%\",AN452),,REPT(\" \",25-SEARCH(\"AT%\",AN452))),SEARCH(\":\",REPLACE(AN452,SEARCH(\"AT%\",AN452),,REPT(\" \",25-SEARCH(\"AT%\",AN452)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN452,SEARCH(\"AT%\",AN452),,REPT(\" \",25-SEARCH(\"AT%\",AN452)))))),\" \")","v":"LAC01A01_TM             AT%M532.0      :BOOL; (*风幕机BXJ-1AP(KT)1-1-定时模式*)"}]
[null,"534.0","验证通过",null,null,null,"BOOL",null,null,"风幕机BXJ-1AP(KT)1-1-定时控制",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"风幕机","BXJ-1AP(KT)1-1","01A01","定时控制","风幕机-定时控制",{"$f":"VLOOKUP(AH453,List!$B$3:$D$445,2,FALSE)&AJ453&\"_\"&VLOOKUP(AK453,List!$K$2:$M$447,2,FALSE)","v":"AC01A01_TC"},"LAC01A01_TC AT%M534.0 :BOOL; (*风幕机BXJ-1AP(KT)1-1-定时控制*)","LAC01A01_TC             AT%M534.0      :BOOL; (*风幕机BXJ-1AP(KT)1-1-定时控制*)"]
[null,"536.0","验证通过",null,null,null,"INT ",null,null,"风幕机BXJ-1AP(KT)1-1-工作日开启小时",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"风幕机","BXJ-1AP(KT)1-1","01A01","工作日开启小时","风幕机-工作日开启小时",{"$f":"VLOOKUP(AH454,List!$B$3:$D$445,2,FALSE)&AJ454&\"_\"&VLOOKUP(AK454,List!$K$2:$M$447,2,FALSE)","v":"AC01A01_WOH"},"LAC01A01_WOH AT%M536.0 :INT ; (*风幕机BXJ-1AP(KT)1-1-工作日开启小时*)","LAC01A01_WOH            AT%M536.0      :INT ; (*风幕机BXJ-1AP(KT)1-1-工作日开启小时*)"]
[null,"538.0","验证通过",null,null,null,"INT ",null,null,"风幕机BXJ-1AP(KT)1-1-工作日开启分钟",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"风幕机","BXJ-1AP(KT)1-1","01A01","工作日开启分钟","风幕机-工作日开启分钟",{"$f":"VLOOKUP(AH455,List!$B$3:$D$445,2,FALSE)&AJ455&\"_\"&VLOOKUP(AK455,List!$K$2:$M$447,2,FALSE)","v":"AC01A01_WOM"},"LAC01A01_WOM AT%M538.0 :INT ; (*风幕机BXJ-1AP(KT)1-1-工作日开启分钟*)","LAC01A01_WOM            AT%M538.0      :INT ; (*风幕机BXJ-1AP(KT)1-1-工作日开启分钟*)"]
[null,"540.0","验证通过",null,null,null,"INT ",null,null,"风幕机BXJ-1AP(KT)1-1-工作日关闭小时",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"风幕机","BXJ-1AP(KT)1-1","01A01","工作日关闭小时","风幕机-工作日关闭小时",{"$f":"VLOOKUP(AH456,List!$B$3:$D$445,2,FALSE)&AJ456&\"_\"&VLOOKUP(AK456,List!$K$2:$M$447,2,FALSE)","v":"AC01A01_WCH"},"LAC01A01_WCH AT%M540.0 :INT ; (*风幕机BXJ-1AP(KT)1-1-工作日关闭小时*)","LAC01A01_WCH            AT%M540.0      :INT ; (*风幕机BXJ-1AP(KT)1-1-工作日关闭小时*)"]
[null,"542.0","验证通过",null,null,null,"INT ",null,null,"风幕机BXJ-1AP(KT)1-1-工作日关闭分钟",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"风幕机","BXJ-1AP(KT)1-1","01A01","工作日关闭分钟","风幕机-工作日关闭分钟",{"$f":"VLOOKUP(AH457,List!$B$3:$D$445,2,FALSE)&AJ457&\"_\"&VLOOKUP(AK457,List!$K$2:$M$447,2,FALSE)","v":"AC01A01_WCM"},"LAC01A01_WCM AT%M542.0 :INT ; (*风幕机BXJ-1AP(KT)1-1-工作日关闭分钟*)","LAC01A01_WCM            AT%M542.0      :INT ; (*风幕机BXJ-1AP(KT)1-1-工作日关闭分钟*)"]
[null,"544.0","验证通过",null,null,null,"INT ",null,null,"风幕机BXJ-1AP(KT)1-1-节假日开启小时",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"风幕机","BXJ-1AP(KT)1-1","01A01","节假日开启小时","风幕机-节假日开启小时",{"$f":"VLOOKUP(AH458,List!$B$3:$D$445,2,FALSE)&AJ458&\"_\"&VLOOKUP(AK458,List!$K$2:$M$447,2,FALSE)","v":"AC01A01_HOH"},"LAC01A01_HOH AT%M544.0 :INT ; (*风幕机BXJ-1AP(KT)1-1-节假日开启小时*)","LAC01A01_HOH            AT%M544.0      :INT ; (*风幕机BXJ-1AP(KT)1-1-节假日开启小时*)"]
[null,"546.0","验证通过",null,null,null,"INT ",null,null,"风幕机BXJ-1AP(KT)1-1-节假日开启分钟",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"风幕机","BXJ-1AP(KT)1-1","01A01","节假日开启分钟","风幕机-节假日开启分钟",{"$f":"VLOOKUP(AH459,List!$B$3:$D$445,2,FALSE)&AJ459&\"_\"&VLOOKUP(AK459,List!$K$2:$M$447,2,FALSE)","v":"AC01A01_HOM"},"LAC01A01_HOM AT%M546.0 :INT ; (*风幕机BXJ-1AP(KT)1-1-节假日开启分钟*)","LAC01A01_HOM            AT%M546.0      :INT ; (*风幕机BXJ-1AP(KT)1-1-节假日开启分钟*)"]
[null,"548.0","验证通过",null,null,null,"INT ",null,null,"风幕机BXJ-1AP(KT)1-1-节假日关闭小时",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"风幕机","BXJ-1AP(KT)1-1","01A01","节假日关闭小时","风幕机-节假日关闭小时",{"$f":"VLOOKUP(AH460,List!$B$3:$D$445,2,FALSE)&AJ460&\"_\"&VLOOKUP(AK460,List!$K$2:$M$447,2,FALSE)","v":"AC01A01_HCH"},"LAC01A01_HCH AT%M548.0 :INT ; (*风幕机BXJ-1AP(KT)1-1-节假日关闭小时*)","LAC01A01_HCH            AT%M548.0      :INT ; (*风幕机BXJ-1AP(KT)1-1-节假日关闭小时*)"]
[null,"550.0","验证通过",null,null,null,"INT ",null,null,"风幕机BXJ-1AP(KT)1-1-节假日关闭分钟",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"风幕机","BXJ-1AP(KT)1-1","01A01","节假日关闭分钟","风幕机-节假日关闭分钟",{"$f":"VLOOKUP(AH461,List!$B$3:$D$445,2,FALSE)&AJ461&\"_\"&VLOOKUP(AK461,List!$K$2:$M$447,2,FALSE)","v":"AC01A01_HCM"},"LAC01A01_HCM AT%M550.0 :INT ; (*风幕机BXJ-1AP(KT)1-1-节假日关闭分钟*)","LAC01A01_HCM            AT%M550.0      :INT ; (*风幕机BXJ-1AP(KT)1-1-节假日关闭分钟*)"]
[null,"PAU"]
[null,{"$f":"IF(OR(G461=\"REAL\",G461=\"DWORD\",G461=\"DINT\"),(IF(OR(G463=\"REAL\",G463=\"DWORD\",G463=\"DINT\"),B461+4+MOD(B461,4),B461+4)),(IF(OR(G463=\"REAL\",G463=\"DWORD\",G463=\"DINT\"),B461+4+MOD(B461,4),B461+2)))&\".0\"","v":"552.0"},{"$f":"IF((IF(OR(G463=\"INT \",G463=\"WORD\",G463=\"BOOL\"),MOD(B463,2),MOD(B463,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH463&AA463&\"-\"&AK463","v":"空调机组BXJ-1AP(KT)1-1-程序控制"},{"$nulls":16},{"$f":"IF(AI463=\"\",\"\",AI463)","v":"BXJ-1AP(KT)1-1"},{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","程序控制",{"$f":"AH463&\"-\"&IF(AI463=\"R\",\"新云平台\"&AK463,AK463)","v":"空调机组-程序控制"},{"$f":"VLOOKUP(AH463,List!$B$3:$D$445,2,FALSE)&AJ463&\"_\"&VLOOKUP(AK463,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_PC"},{"$f":"_xlfn.IFNA(\"L\"&AM463&\" \"&\"AT%M\"&B463&\" :\"&G463&\";\"&\" \"&\"(*\"&J463&\"*)\",\" \")","v":"LAHUYYA01_PC AT%M552.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-程序控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN463,SEARCH(\"AT%\",AN463),,REPT(\" \",25-SEARCH(\"AT%\",AN463))),SEARCH(\":\",REPLACE(AN463,SEARCH(\"AT%\",AN463),,REPT(\" \",25-SEARCH(\"AT%\",AN463)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN463,SEARCH(\"AT%\",AN463),,REPT(\" \",25-SEARCH(\"AT%\",AN463)))))),\" \")","v":"LAHUYYA01_PC            AT%M552.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-程序控制*)"}]
[null,{"$f":"IF(OR(G463=\"REAL\",G463=\"DWORD\",G463=\"DINT\"),(IF(OR(G464=\"REAL\",G464=\"DWORD\",G464=\"DINT\"),B463+4+MOD(B463,4),B463+4)),(IF(OR(G464=\"REAL\",G464=\"DWORD\",G464=\"DINT\"),B463+4+MOD(B463,4),B463+2)))&\".0\"","v":"554.0"},"验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-季节模式",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","季节模式","空调机组-季节模式",{"$f":"VLOOKUP(AH464,List!$B$3:$D$445,2,FALSE)&AJ464&\"_\"&VLOOKUP(AK464,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_SM"},"LAHUYYA01_SM AT%M554.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-季节模式*)","LAHUYYA01_SM            AT%M554.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-季节模式*)"]
[null,"560.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-设定温度值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","设定温度值","空调机组-设定温度值",{"$f":"VLOOKUP(AH465,List!$B$3:$D$445,2,FALSE)&AJ465&\"_\"&VLOOKUP(AK465,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_TSET"},"LAHUYYA01_TSET AT%M560.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-设定温度值*)","LAHUYYA01_TSET          AT%M560.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-设定温度值*)"]
[null,"564.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-设备状态代码",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","设备状态代码","空调机组-设备状态代码",{"$f":"VLOOKUP(AH466,List!$B$3:$D$445,2,FALSE)&AJ466&\"_\"&VLOOKUP(AK466,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_SN"},"LAHUYYA01_SN AT%M564.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-设备状态代码*)","LAHUYYA01_SN            AT%M564.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-设备状态代码*)"]
[null,"568.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-送风温度换算值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","送风温度换算值","空调机组-送风温度换算值",{"$f":"VLOOKUP(AH467,List!$B$3:$D$445,2,FALSE)&AJ467&\"_\"&VLOOKUP(AK467,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_STS"},"LAHUYYA01_STS AT%M568.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-送风温度换算值*)","LAHUYYA01_STS           AT%M568.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-送风温度换算值*)"]
[null,"572.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-回风温度换算值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","回风温度换算值","空调机组-回风温度换算值",{"$f":"VLOOKUP(AH468,List!$B$3:$D$445,2,FALSE)&AJ468&\"_\"&VLOOKUP(AK468,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_RTS"},"LAHUYYA01_RTS AT%M572.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-回风温度换算值*)",{"$f":"IFERROR(REPLACE(REPLACE(AN468,SEARCH(\"AT%\",AN468),,REPT(\" \",25-SEARCH(\"AT%\",AN468))),SEARCH(\":\",REPLACE(AN468,SEARCH(\"AT%\",AN468),,REPT(\" \",25-SEARCH(\"AT%\",AN468)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN468,SEARCH(\"AT%\",AN468),,REPT(\" \",25-SEARCH(\"AT%\",AN468)))))),\" \")","v":"LAHUYYA01_RTS           AT%M572.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-回风温度换算值*)"}]
[null,"576.0",{"$f":"IF((IF(OR(G469=\"INT \",G469=\"WORD\",G469=\"BOOL\"),MOD(B469,2),MOD(B469,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"REAL",null,null,{"$f":"AH469&AA469&\"-\"&AK469","v":"空调机组BXJ-1AP(KT)1-1-水阀反馈换算值"},{"$nulls":16},{"$f":"IF(AI469=\"\",\"\",AI469)","v":"BXJ-1AP(KT)1-1"},{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","水阀反馈换算值",{"$f":"AH469&\"-\"&IF(AI469=\"R\",\"新云平台\"&AK469,AK469)","v":"空调机组-水阀反馈换算值"},{"$f":"VLOOKUP(AH469,List!$B$3:$D$445,2,FALSE)&AJ469&\"_\"&VLOOKUP(AK469,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_WVBS"},{"$f":"_xlfn.IFNA(\"L\"&AM469&\" \"&\"AT%M\"&B469&\" :\"&G469&\";\"&\" \"&\"(*\"&J469&\"*)\",\" \")","v":"LAHUYYA01_WVBS AT%M576.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-水阀反馈换算值*)"},"LAHUYYA01_WVBS          AT%M576.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-水阀反馈换算值*)"]
[null,"580.0","验证通过",null,null,null,"BOOL",null,null,"空调机组BXJ-1AP(KT)1-1-水阀手动控制",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","水阀手动控制","空调机组-水阀手动控制",{"$f":"VLOOKUP(AH470,List!$B$3:$D$445,2,FALSE)&AJ470&\"_\"&VLOOKUP(AK470,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_WVMC"},"LAHUYYA01_WVMC AT%M580.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-水阀手动控制*)","LAHUYYA01_WVMC          AT%M580.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-水阀手动控制*)"]
[null,"584.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-水阀手动控制值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","水阀手动控制值","空调机组-水阀手动控制值",{"$f":"VLOOKUP(AH471,List!$B$3:$D$445,2,FALSE)&AJ471&\"_\"&VLOOKUP(AK471,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_WVMV"},"LAHUYYA01_WVMV AT%M584.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-水阀手动控制值*)","LAHUYYA01_WVMV          AT%M584.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-水阀手动控制值*)"]
[null,"588.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-水阀控制转换值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","水阀控制转换值","空调机组-水阀控制转换值",{"$f":"VLOOKUP(AH472,List!$B$3:$D$445,2,FALSE)&AJ472&\"_\"&VLOOKUP(AK472,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_WVCS"},"LAHUYYA01_WVCS AT%M588.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-水阀控制转换值*)","LAHUYYA01_WVCS          AT%M588.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-水阀控制转换值*)"]
[null,"590.0",{"$f":"IF((IF(OR(G473=\"INT \",G473=\"WORD\",G473=\"BOOL\"),MOD(B473,2),MOD(B473,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH473&AA473&\"-\"&AK473","v":"空调机组BXJ-1AP(KT)1-1-运行时间累积重置"},{"$nulls":16},{"$f":"IF(AI473=\"\",\"\",AI473)","v":"BXJ-1AP(KT)1-1"},{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","运行时间累积重置",{"$f":"AH473&\"-\"&IF(AI473=\"R\",\"新云平台\"&AK473,AK473)","v":"空调机组-运行时间累积重置"},{"$f":"VLOOKUP(AH473,List!$B$3:$D$445,2,FALSE)&AJ473&\"_\"&VLOOKUP(AK473,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_RST"},{"$f":"_xlfn.IFNA(\"L\"&AM473&\" \"&\"AT%M\"&B473&\" :\"&G473&\";\"&\" \"&\"(*\"&J473&\"*)\",\" \")","v":"LAHUYYA01_RST AT%M590.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-运行时间累积重置*)"},"LAHUYYA01_RST           AT%M590.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-运行时间累积重置*)"]
[null,"596.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-运行时间累积重置值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","运行时间累积重置值","空调机组-运行时间累积重置值",{"$f":"VLOOKUP(AH474,List!$B$3:$D$445,2,FALSE)&AJ474&\"_\"&VLOOKUP(AK474,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_RSTV"},"LAHUYYA01_RSTV AT%M596.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-运行时间累积重置值*)","LAHUYYA01_RSTV          AT%M596.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-运行时间累积重置值*)"]
[null,"600.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-运行时间累积值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","运行时间累积值","空调机组-运行时间累积值",{"$f":"VLOOKUP(AH475,List!$B$3:$D$445,2,FALSE)&AJ475&\"_\"&VLOOKUP(AK475,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_RH"},"LAHUYYA01_RH AT%M600.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-运行时间累积值*)","LAHUYYA01_RH            AT%M600.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-运行时间累积值*)"]
[null,"604.0",{"$f":"IF((IF(OR(G476=\"INT \",G476=\"WORD\",G476=\"BOOL\"),MOD(B476,2),MOD(B476,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"BOOL",null,null,{"$f":"AH476&AA476&\"-\"&AK476","v":"空调机组BXJ-1AP(KT)1-1-隔离开关1"},{"$nulls":16},{"$f":"IF(AI476=\"\",\"\",AI476)","v":"BXJ-1AP(KT)1-1"},{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","隔离开关1",{"$f":"AH476&\"-\"&IF(AI476=\"R\",\"新云平台\"&AK476,AK476)","v":"空调机组-隔离开关1"},{"$f":"VLOOKUP(AH476,List!$B$3:$D$445,2,FALSE)&AJ476&\"_\"&VLOOKUP(AK476,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_ISO1"},{"$f":"_xlfn.IFNA(\"L\"&AM476&\" \"&\"AT%M\"&B476&\" :\"&G476&\";\"&\" \"&\"(*\"&J476&\"*)\",\" \")","v":"LAHUYYA01_ISO1 AT%M604.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-隔离开关1*)"},"LAHUYYA01_ISO1          AT%M604.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-隔离开关1*)"]
[null,"606.0","验证通过",null,null,null,"BOOL",null,null,"空调机组BXJ-1AP(KT)1-1-隔离开关2",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","隔离开关2","空调机组-隔离开关2",{"$f":"VLOOKUP(AH477,List!$B$3:$D$445,2,FALSE)&AJ477&\"_\"&VLOOKUP(AK477,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_ISO2"},"LAHUYYA01_ISO2 AT%M606.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-隔离开关2*)","LAHUYYA01_ISO2          AT%M606.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-隔离开关2*)"]
[null,"608.0","验证通过",null,null,null,"BOOL",null,null,"空调机组BXJ-1AP(KT)1-1-隔离开关3",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","隔离开关3","空调机组-隔离开关3",{"$f":"VLOOKUP(AH478,List!$B$3:$D$445,2,FALSE)&AJ478&\"_\"&VLOOKUP(AK478,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_ISO3"},"LAHUYYA01_ISO3 AT%M608.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-隔离开关3*)","LAHUYYA01_ISO3          AT%M608.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-隔离开关3*)"]
[null,"612.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-P调节参数",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","P调节参数","空调机组-P调节参数",{"$f":"VLOOKUP(AH479,List!$B$3:$D$445,2,FALSE)&AJ479&\"_\"&VLOOKUP(AK479,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_VP"},"LAHUYYA01_VP AT%M612.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-P调节参数*)","LAHUYYA01_VP            AT%M612.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-P调节参数*)"]
[null,"616.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-I调节参数",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","I调节参数","空调机组-I调节参数",{"$f":"VLOOKUP(AH480,List!$B$3:$D$445,2,FALSE)&AJ480&\"_\"&VLOOKUP(AK480,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_VI"},"LAHUYYA01_VI AT%M616.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-I调节参数*)","LAHUYYA01_VI            AT%M616.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-I调节参数*)"]
[null,"620.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-变频手动控制值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","变频手动控制值","空调机组-变频手动控制值",{"$f":"VLOOKUP(AH481,List!$B$3:$D$445,2,FALSE)&AJ481&\"_\"&VLOOKUP(AK481,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_VFMV"},"LAHUYYA01_VFMV AT%M620.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-变频手动控制值*)","LAHUYYA01_VFMV          AT%M620.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-变频手动控制值*)"]
[null,"622.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-变频器频率反馈值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","变频器频率反馈值","空调机组-变频器频率反馈值",{"$f":"VLOOKUP(AH482,List!$B$3:$D$445,2,FALSE)&AJ482&\"_\"&VLOOKUP(AK482,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_VFBS"},"LAHUYYA01_VFBS AT%M622.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-变频器频率反馈值*)","LAHUYYA01_VFBS          AT%M622.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-变频器频率反馈值*)"]
[null,"624.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-变频器频率控制值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","变频器频率控制值","空调机组-变频器频率控制值",{"$f":"VLOOKUP(AH483,List!$B$3:$D$445,2,FALSE)&AJ483&\"_\"&VLOOKUP(AK483,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_VFCS"},"LAHUYYA01_VFCS AT%M624.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-变频器频率控制值*)","LAHUYYA01_VFCS          AT%M624.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-变频器频率控制值*)"]
[null,"626.0","验证通过",null,null,null,"BOOL",null,null,"空调机组BXJ-1AP(KT)1-1-联动模式",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","联动模式","空调机组-联动模式",{"$f":"VLOOKUP(AH484,List!$B$3:$D$445,2,FALSE)&AJ484&\"_\"&VLOOKUP(AK484,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_LM"},"LAHUYYA01_LM AT%M626.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-联动模式*)","LAHUYYA01_LM            AT%M626.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-联动模式*)"]
[null,"628.0","验证通过",null,null,null,"BOOL",null,null,"空调机组BXJ-1AP(KT)1-1-风阀联动模式",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","风阀联动模式","空调机组-风阀联动模式",{"$f":"VLOOKUP(AH485,List!$B$3:$D$445,2,FALSE)&AJ485&\"_\"&VLOOKUP(AK485,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_FM"},"LAHUYYA01_FM AT%M628.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-风阀联动模式*)","LAHUYYA01_FM            AT%M628.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-风阀联动模式*)"]
[null,"630.0",{"$f":"IF((IF(OR(G486=\"INT \",G486=\"WORD\",G486=\"BOOL\"),MOD(B486,2),MOD(B486,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"INT ",null,null,{"$f":"AH486&AA486&\"-\"&AK486","v":"空调机组BXJ-1AP(KT)1-1-回风阀控制换算值"},{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","回风阀控制换算值",{"$f":"AH486&\"-\"&IF(AI486=\"R\",\"新云平台\"&AK486,AK486)","v":"空调机组-回风阀控制换算值"},{"$f":"VLOOKUP(AH486,List!$B$3:$D$445,2,FALSE)&AJ486&\"_\"&VLOOKUP(AK486,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_RDCS"},{"$f":"_xlfn.IFNA(\"L\"&AM486&\" \"&\"AT%M\"&B486&\" :\"&G486&\";\"&\" \"&\"(*\"&J486&\"*)\",\" \")","v":"LAHUYYA01_RDCS AT%M630.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-回风阀控制换算值*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN486,SEARCH(\"AT%\",AN486),,REPT(\" \",25-SEARCH(\"AT%\",AN486))),SEARCH(\":\",REPLACE(AN486,SEARCH(\"AT%\",AN486),,REPT(\" \",25-SEARCH(\"AT%\",AN486)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN486,SEARCH(\"AT%\",AN486),,REPT(\" \",25-SEARCH(\"AT%\",AN486)))))),\" \")","v":"LAHUYYA01_RDCS          AT%M630.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-回风阀控制换算值*)"}]
[null,"636.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-回风阀反馈换算值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","回风阀反馈换算值","空调机组-回风阀反馈换算值",{"$f":"VLOOKUP(AH487,List!$B$3:$D$445,2,FALSE)&AJ487&\"_\"&VLOOKUP(AK487,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_RDBS"},"LAHUYYA01_RDBS AT%M636.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-回风阀反馈换算值*)","LAHUYYA01_RDBS          AT%M636.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-回风阀反馈换算值*)"]
[null,"640.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-回风阀手动控制值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","回风阀手动控制值","空调机组-回风阀手动控制值",{"$f":"VLOOKUP(AH488,List!$B$3:$D$445,2,FALSE)&AJ488&\"_\"&VLOOKUP(AK488,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_RDMV"},"LAHUYYA01_RDMV AT%M640.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-回风阀手动控制值*)","LAHUYYA01_RDMV          AT%M640.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-回风阀手动控制值*)"]
[null,"642.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-新风阀控制换算值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","新风阀控制换算值","空调机组-新风阀控制换算值",{"$f":"VLOOKUP(AH489,List!$B$3:$D$445,2,FALSE)&AJ489&\"_\"&VLOOKUP(AK489,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_FDCS"},"LAHUYYA01_FDCS AT%M642.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-新风阀控制换算值*)","LAHUYYA01_FDCS          AT%M642.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-新风阀控制换算值*)"]
[null,"648.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-新风阀反馈换算值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","新风阀反馈换算值","空调机组-新风阀反馈换算值",{"$f":"VLOOKUP(AH490,List!$B$3:$D$445,2,FALSE)&AJ490&\"_\"&VLOOKUP(AK490,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_FDBS"},"LAHUYYA01_FDBS AT%M648.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-新风阀反馈换算值*)","LAHUYYA01_FDBS          AT%M648.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-新风阀反馈换算值*)"]
[null,"652.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-新风阀手动控制值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","新风阀手动控制值","空调机组-新风阀手动控制值",{"$f":"VLOOKUP(AH491,List!$B$3:$D$445,2,FALSE)&AJ491&\"_\"&VLOOKUP(AK491,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_FDMV"},"LAHUYYA01_FDMV AT%M652.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-新风阀手动控制值*)","LAHUYYA01_FDMV          AT%M652.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-新风阀手动控制值*)"]
[null,"656.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-CO2设定值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","CO2设定值","空调机组-CO2设定值",{"$f":"VLOOKUP(AH492,List!$B$3:$D$445,2,FALSE)&AJ492&\"_\"&VLOOKUP(AK492,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_CO2SET"},"LAHUYYA01_CO2SET AT%M656.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-CO2设定值*)","LAHUYYA01_CO2SET        AT%M656.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-CO2设定值*)"]
[null,"660.0","验证通过",null,null,null,"REAL",null,null,"空调机组BXJ-1AP(KT)1-1-CO2换算值",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","CO2换算值","空调机组-CO2换算值",{"$f":"VLOOKUP(AH493,List!$B$3:$D$445,2,FALSE)&AJ493&\"_\"&VLOOKUP(AK493,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_CO2S"},"LAHUYYA01_CO2S AT%M660.0 :REAL; (*空调机组BXJ-1AP(KT)1-1-CO2换算值*)","LAHUYYA01_CO2S          AT%M660.0      :REAL; (*空调机组BXJ-1AP(KT)1-1-CO2换算值*)"]
[null,"664.0","验证通过",null,null,null,"BOOL",null,null,"空调机组BXJ-1AP(KT)1-1-定时模式",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","定时模式","空调机组-定时模式",{"$f":"VLOOKUP(AH494,List!$B$3:$D$445,2,FALSE)&AJ494&\"_\"&VLOOKUP(AK494,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_TM"},"LAHUYYA01_TM AT%M664.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-定时模式*)","LAHUYYA01_TM            AT%M664.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-定时模式*)"]
[null,"666.0","验证通过",null,null,null,"BOOL",null,null,"空调机组BXJ-1AP(KT)1-1-定时控制",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","定时控制","空调机组-定时控制",{"$f":"VLOOKUP(AH495,List!$B$3:$D$445,2,FALSE)&AJ495&\"_\"&VLOOKUP(AK495,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_TC"},"LAHUYYA01_TC AT%M666.0 :BOOL; (*空调机组BXJ-1AP(KT)1-1-定时控制*)","LAHUYYA01_TC            AT%M666.0      :BOOL; (*空调机组BXJ-1AP(KT)1-1-定时控制*)"]
[null,"668.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-工作日开启小时",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","工作日开启小时","空调机组-工作日开启小时",{"$f":"VLOOKUP(AH496,List!$B$3:$D$445,2,FALSE)&AJ496&\"_\"&VLOOKUP(AK496,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_WOH"},"LAHUYYA01_WOH AT%M668.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-工作日开启小时*)","LAHUYYA01_WOH           AT%M668.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-工作日开启小时*)"]
[null,"670.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-工作日开启分钟",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","工作日开启分钟","空调机组-工作日开启分钟",{"$f":"VLOOKUP(AH497,List!$B$3:$D$445,2,FALSE)&AJ497&\"_\"&VLOOKUP(AK497,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_WOM"},"LAHUYYA01_WOM AT%M670.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-工作日开启分钟*)","LAHUYYA01_WOM           AT%M670.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-工作日开启分钟*)"]
[null,"672.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-工作日关闭小时",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","工作日关闭小时","空调机组-工作日关闭小时",{"$f":"VLOOKUP(AH498,List!$B$3:$D$445,2,FALSE)&AJ498&\"_\"&VLOOKUP(AK498,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_WCH"},"LAHUYYA01_WCH AT%M672.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-工作日关闭小时*)","LAHUYYA01_WCH           AT%M672.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-工作日关闭小时*)"]
[null,"674.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-工作日关闭分钟",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","工作日关闭分钟","空调机组-工作日关闭分钟",{"$f":"VLOOKUP(AH499,List!$B$3:$D$445,2,FALSE)&AJ499&\"_\"&VLOOKUP(AK499,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_WCM"},"LAHUYYA01_WCM AT%M674.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-工作日关闭分钟*)","LAHUYYA01_WCM           AT%M674.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-工作日关闭分钟*)"]
[null,"676.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-节假日开启小时",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","节假日开启小时","空调机组-节假日开启小时",{"$f":"VLOOKUP(AH500,List!$B$3:$D$445,2,FALSE)&AJ500&\"_\"&VLOOKUP(AK500,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_HOH"},"LAHUYYA01_HOH AT%M676.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-节假日开启小时*)","LAHUYYA01_HOH           AT%M676.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-节假日开启小时*)"]
[null,"678.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-节假日开启分钟",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","节假日开启分钟","空调机组-节假日开启分钟",{"$f":"VLOOKUP(AH501,List!$B$3:$D$445,2,FALSE)&AJ501&\"_\"&VLOOKUP(AK501,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_HOM"},"LAHUYYA01_HOM AT%M678.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-节假日开启分钟*)","LAHUYYA01_HOM           AT%M678.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-节假日开启分钟*)"]
[null,"680.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-节假日关闭小时",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","节假日关闭小时","空调机组-节假日关闭小时",{"$f":"VLOOKUP(AH502,List!$B$3:$D$445,2,FALSE)&AJ502&\"_\"&VLOOKUP(AK502,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_HCH"},"LAHUYYA01_HCH AT%M680.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-节假日关闭小时*)","LAHUYYA01_HCH           AT%M680.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-节假日关闭小时*)"]
[null,"682.0","验证通过",null,null,null,"INT ",null,null,"空调机组BXJ-1AP(KT)1-1-节假日关闭分钟",{"$nulls":16},"BXJ-1AP(KT)1-1",{"$nulls":6},"空调机组","BXJ-1AP(KT)1-1","YYA01","节假日关闭分钟","空调机组-节假日关闭分钟",{"$f":"VLOOKUP(AH503,List!$B$3:$D$445,2,FALSE)&AJ503&\"_\"&VLOOKUP(AK503,List!$K$2:$M$447,2,FALSE)","v":"AHUYYA01_HCM"},"LAHUYYA01_HCM AT%M682.0 :INT ; (*空调机组BXJ-1AP(KT)1-1-节假日关闭分钟*)","LAHUYYA01_HCM           AT%M682.0      :INT ; (*空调机组BXJ-1AP(KT)1-1-节假日关闭分钟*)"]
[null,"SYS"]
[null,"1500.0",{"$f":"IF((IF(OR(G505=\"INT \",G505=\"WORD\",G505=\"BOOL\"),MOD(B505,2),MOD(B505,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},null,null,null,"INT ",null,null,{"$f":"AH505&AA505&\"-\"&AK505","v":"系统-闪存写入次数"},{"$nulls":16},{"$f":"IF(AI505=\"\",\"\",AI505)","v":""},{"$nulls":6},"系统",null,null,"闪存写入次数",{"$f":"AH505&\"-\"&IF(AI505=\"R\",\"新云平台\"&AK505,AK505)","v":"系统-闪存写入次数"},{"$f":"VLOOKUP(AH505,List!$B$3:$D$445,2,FALSE)&AJ505&\"_\"&VLOOKUP(AK505,List!$K$2:$M$447,2,FALSE)","v":"SYS_WriteNum"},{"$f":"_xlfn.IFNA(\"L\"&AM505&\" \"&\"AT%M\"&B505&\" :\"&G505&\";\"&\" \"&\"(*\"&J505&\"*)\",\" \")","v":"LSYS_WriteNum AT%M1500.0 :INT ; (*系统-闪存写入次数*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN505,SEARCH(\"AT%\",AN505),,REPT(\" \",25-SEARCH(\"AT%\",AN505))),SEARCH(\":\",REPLACE(AN505,SEARCH(\"AT%\",AN505),,REPT(\" \",25-SEARCH(\"AT%\",AN505)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN505,SEARCH(\"AT%\",AN505),,REPT(\" \",25-SEARCH(\"AT%\",AN505)))))),\" \")","v":"LSYS_WriteNum           AT%M1500.0     :INT ; (*系统-闪存写入次数*)"}]
[null,{"$f":"IF(OR(G505=\"REAL\",G505=\"DWORD\",G505=\"DINT\"),(IF(OR(G506=\"REAL\",G506=\"DWORD\",G506=\"DINT\"),B505+4+MOD(B505,4),B505+4)),(IF(OR(G506=\"REAL\",G506=\"DWORD\",G506=\"DINT\"),B505+4+MOD(B505,4),B505+2)))&\".0\"","v":"1502.0"},"验证通过",null,null,null,"BOOL",null,null,"系统-闪存写入成功标记",{"$nulls":16},"",{"$nulls":6},"系统",null,null,"闪存写入成功标记","系统-闪存写入成功标记",{"$f":"VLOOKUP(AH506,List!$B$3:$D$445,2,FALSE)&AJ506&\"_\"&VLOOKUP(AK506,List!$K$2:$M$447,2,FALSE)","v":"SYS_Write_Flag"},"LSYS_Write_Flag AT%M1502.0 :BOOL; (*系统-闪存写入成功标记*)","LSYS_Write_Flag         AT%M1502.0     :BOOL; (*系统-闪存写入成功标记*)"]
[null,"1504.0","验证通过",null,null,null,"BOOL",null,null,"系统-闪存读取成功标记",{"$nulls":16},"",{"$nulls":6},"系统",null,null,"闪存读取成功标记","系统-闪存读取成功标记",{"$f":"VLOOKUP(AH507,List!$B$3:$D$445,2,FALSE)&AJ507&\"_\"&VLOOKUP(AK507,List!$K$2:$M$447,2,FALSE)","v":"SYS_Read_Flag"},"LSYS_Read_Flag AT%M1504.0 :BOOL; (*系统-闪存读取成功标记*)","LSYS_Read_Flag          AT%M1504.0     :BOOL; (*系统-闪存读取成功标记*)"]
[null,"1506.0","验证通过",null,null,null,"INT ",null,null,"系统-变化判断变量",{"$nulls":16},"",{"$nulls":6},"系统",null,null,"变化判断变量","系统-变化判断变量",{"$f":"VLOOKUP(AH508,List!$B$3:$D$445,2,FALSE)&AJ508&\"_\"&VLOOKUP(AK508,List!$K$2:$M$447,2,FALSE)","v":"SYS_Judge_Num"},"LSYS_Judge_Num AT%M1506.0 :INT ; (*系统-变化判断变量*)","LSYS_Judge_Num          AT%M1506.0     :INT ; (*系统-变化判断变量*)"]

{"sheet":"主CPU","index":3,"n_rows":971,"n_cols":13,"rows_kept":971,"cut":false,"hidden":false,"merged":[[0,0,0,12],[1,0,2,0],[1,1,2,1],[1,2,2,2],[1,3,2,3],[1,4,2,4],[1,7,2,7],[1,8,2,8],[1,9,2,9],[1,10,2,10],[1,11,2,11],[1,12,2,12],[1,5,2,6]]}
["NI 0-1023 NQ 1024-2047"]
["设备类型","总线编号","P2P标记","程序编号","点位功能","发送地址\n接收地址",null,"数据类型\n整除验证","数据类型","变量备注","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto"]
[]
["从CPU-->主控CPU",{"$nulls":4},"接收地址.auto","发送地址"]
["命令","I","M","00001","心跳值","5000.0","6000.0",{"$f":"IF((IF(OR(I5=\"INT\",I5=\"WORD\",I5=\"BOOL\"),MOD(F5,2),MOD(F5,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"INT","1#CPU心跳反馈",{"$f":"B5&VLOOKUP(A5,List!$B$3:$D$445,2,FALSE)&D5&\"_\"&VLOOKUP(E5,List!$K$2:$M$447,2,FALSE)","v":"ICMD00001_DHV"},{"$f":"K5&\" \"&\"AT%\"&C5&F5&\" \"&\":\"&I5&\";\"&\" \"&\"(*\"&J5&\"*)\"","v":"ICMD00001_DHV AT%M5000.0 :INT; (*1#CPU心跳反馈*)"},{"$f":"REPLACE(REPLACE(L5,SEARCH(\"AT%\",L5),,REPT(\" \",25-SEARCH(\"AT%\",L5))),SEARCH(\":\",REPLACE(L5,SEARCH(\"AT%\",L5),,REPT(\" \",25-SEARCH(\"AT%\",L5)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L5,SEARCH(\"AT%\",L5),,REPT(\" \",25-SEARCH(\"AT%\",L5))))))","v":"ICMD00001_DHV           AT%M5000.0     :INT; (*1#CPU心跳反馈*)"}]
["命令","I","M","00002","心跳值",{"$f":"IF(OR(I5=\"REAL\",I5=\"DWORD\",I5=\"DINT\"),(IF(OR(I6=\"REAL\",I6=\"DWORD\",I6=\"DINT\"),F5+4+MOD(F5,4),F5+4)),(IF(OR(I6=\"REAL\",I6=\"DWORD\",I6=\"DINT\"),F5+4+MOD(F5,4),F5+2)))&\".0\"","v":"5002.0"},"6000.0",{"$f":"IF((IF(OR(I6=\"INT\",I6=\"WORD\",I6=\"BOOL\"),MOD(F6,2),MOD(F6,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"INT","2#CPU心跳反馈",{"$f":"B6&VLOOKUP(A6,List!$B$3:$D$445,2,FALSE)&D6&\"_\"&VLOOKUP(E6,List!$K$2:$M$447,2,FALSE)","v":"ICMD00002_DHV"},"ICMD00002_DHV AT%M5002.0 :INT; (*2#CPU心跳反馈*)","ICMD00002_DHV           AT%M5002.0     :INT; (*2#CPU心跳反馈*)"]
["命令","I","M","00003","心跳值","5004.0","6000.0","验证通过","INT","3#CPU心跳反馈",{"$f":"B7&VLOOKUP(A7,List!$B$3:$D$445,2,FALSE)&D7&\"_\"&VLOOKUP(E7,List!$K$2:$M$447,2,FALSE)","v":"ICMD00003_DHV"},"ICMD00003_DHV AT%M5004.0 :INT; (*3#CPU心跳反馈*)","ICMD00003_DHV           AT%M5004.0     :INT; (*3#CPU心跳反馈*)"]
["命令","I","M","00004","心跳值","5006.0","6000.0","验证通过","INT","4#CPU心跳反馈",{"$f":"B8&VLOOKUP(A8,List!$B$3:$D$445,2,FALSE)&D8&\"_\"&VLOOKUP(E8,List!$K$2:$M$447,2,FALSE)","v":"ICMD00004_DHV"},"ICMD00004_DHV AT%M5006.0 :INT; (*4#CPU心跳反馈*)","ICMD00004_DHV           AT%M5006.0     :INT; (*4#CPU心跳反馈*)"]
["命令","I","M","00005","心跳值","5008.0","6000.0","验证通过","INT","5#CPU心跳反馈",{"$f":"B9&VLOOKUP(A9,List!$B$3:$D$445,2,FALSE)&D9&\"_\"&VLOOKUP(E9,List!$K$2:$M$447,2,FALSE)","v":"ICMD00005_DHV"},"ICMD00005_DHV AT%M5008.0 :INT; (*5#CPU心跳反馈*)","ICMD00005_DHV           AT%M5008.0     :INT; (*5#CPU心跳反馈*)"]
["命令","I","M","00006","心跳值","5010.0","6000.0","验证通过","INT","6#CPU心跳反馈",{"$f":"B10&VLOOKUP(A10,List!$B$3:$D$445,2,FALSE)&D10&\"_\"&VLOOKUP(E10,List!$K$2:$M$447,2,FALSE)","v":"ICMD00006_DHV"},"ICMD00006_DHV AT%M5010.0 :INT; (*6#CPU心跳反馈*)","ICMD00006_DHV           AT%M5010.0     :INT; (*6#CPU心跳反馈*)"]
["命令","I","M","00007","心跳值","5012.0","6000.0","验证通过","INT","7#CPU心跳反馈",{"$f":"B11&VLOOKUP(A11,List!$B$3:$D$445,2,FALSE)&D11&\"_\"&VLOOKUP(E11,List!$K$2:$M$447,2,FALSE)","v":"ICMD00007_DHV"},"ICMD00007_DHV AT%M5012.0 :INT; (*7#CPU心跳反馈*)","ICMD00007_DHV           AT%M5012.0     :INT; (*7#CPU心跳反馈*)"]
["命令","I","M","00008","心跳值","5014.0","6000.0","验证通过","INT","8#CPU心跳反馈",{"$f":"B12&VLOOKUP(A12,List!$B$3:$D$445,2,FALSE)&D12&\"_\"&VLOOKUP(E12,List!$K$2:$M$447,2,FALSE)","v":"ICMD00008_DHV"},"ICMD00008_DHV AT%M5014.0 :INT; (*8#CPU心跳反馈*)","ICMD00008_DHV           AT%M5014.0     :INT; (*8#CPU心跳反馈*)"]
["命令","I","M","00009","心跳值","5016.0","6000.0","验证通过","INT","9#CPU心跳反馈",{"$f":"B13&VLOOKUP(A13,List!$B$3:$D$445,2,FALSE)&D13&\"_\"&VLOOKUP(E13,List!$K$2:$M$447,2,FALSE)","v":"ICMD00009_DHV"},"ICMD00009_DHV AT%M5016.0 :INT; (*9#CPU心跳反馈*)","ICMD00009_DHV           AT%M5016.0     :INT; (*9#CPU心跳反馈*)"]
["命令","I","M","00010","心跳值","5018.0","6000.0","验证通过","INT","10#CPU心跳反馈",{"$f":"B14&VLOOKUP(A14,List!$B$3:$D$445,2,FALSE)&D14&\"_\"&VLOOKUP(E14,List!$K$2:$M$447,2,FALSE)","v":"ICMD00010_DHV"},"ICMD00010_DHV AT%M5018.0 :INT; (*10#CPU心跳反馈*)","ICMD00010_DHV           AT%M5018.0     :INT; (*10#CPU心跳反馈*)"]
["命令","I","M","00011","心跳值","5020.0","6000.0","验证通过","INT","11#CPU心跳反馈",{"$f":"B15&VLOOKUP(A15,List!$B$3:$D$445,2,FALSE)&D15&\"_\"&VLOOKUP(E15,List!$K$2:$M$447,2,FALSE)","v":"ICMD00011_DHV"},"ICMD00011_DHV AT%M5020.0 :INT; (*11#CPU心跳反馈*)","ICMD00011_DHV           AT%M5020.0     :INT; (*11#CPU心跳反馈*)"]
["命令","I","M","00012","心跳值","5022.0","6000.0","验证通过","INT","12#CPU心跳反馈",{"$f":"B16&VLOOKUP(A16,List!$B$3:$D$445,2,FALSE)&D16&\"_\"&VLOOKUP(E16,List!$K$2:$M$447,2,FALSE)","v":"ICMD00012_DHV"},"ICMD00012_DHV AT%M5022.0 :INT; (*12#CPU心跳反馈*)","ICMD00012_DHV           AT%M5022.0     :INT; (*12#CPU心跳反馈*)"]
["命令","I","M","00013","心跳值","5024.0","6000.0","验证通过","INT","13#CPU心跳反馈",{"$f":"B17&VLOOKUP(A17,List!$B$3:$D$445,2,FALSE)&D17&\"_\"&VLOOKUP(E17,List!$K$2:$M$447,2,FALSE)","v":"ICMD00013_DHV"},"ICMD00013_DHV AT%M5024.0 :INT; (*13#CPU心跳反馈*)","ICMD00013_DHV           AT%M5024.0     :INT; (*13#CPU心跳反馈*)"]
["命令","I","M","00014","心跳值","5026.0","6000.0","验证通过","INT","14#CPU心跳反馈",{"$f":"B18&VLOOKUP(A18,List!$B$3:$D$445,2,FALSE)&D18&\"_\"&VLOOKUP(E18,List!$K$2:$M$447,2,FALSE)","v":"ICMD00014_DHV"},"ICMD00014_DHV AT%M5026.0 :INT; (*14#CPU心跳反馈*)","ICMD00014_DHV           AT%M5026.0     :INT; (*14#CPU心跳反馈*)"]
["命令","I","M","00015","心跳值","5028.0","6000.0","验证通过","INT","15#CPU心跳反馈",{"$f":"B19&VLOOKUP(A19,List!$B$3:$D$445,2,FALSE)&D19&\"_\"&VLOOKUP(E19,List!$K$2:$M$447,2,FALSE)","v":"ICMD00015_DHV"},"ICMD00015_DHV AT%M5028.0 :INT; (*15#CPU心跳反馈*)","ICMD00015_DHV           AT%M5028.0     :INT; (*15#CPU心跳反馈*)"]
["命令","I","M","00016","心跳值","5030.0","6000.0","验证通过","INT","16#CPU心跳反馈",{"$f":"B20&VLOOKUP(A20,List!$B$3:$D$445,2,FALSE)&D20&\"_\"&VLOOKUP(E20,List!$K$2:$M$447,2,FALSE)","v":"ICMD00016_DHV"},"ICMD00016_DHV AT%M5030.0 :INT; (*16#CPU心跳反馈*)","ICMD00016_DHV           AT%M5030.0     :INT; (*16#CPU心跳反馈*)"]
["命令","I","M","00017","心跳值","5032.0","6000.0","验证通过","INT","17#CPU心跳反馈",{"$f":"B21&VLOOKUP(A21,List!$B$3:$D$445,2,FALSE)&D21&\"_\"&VLOOKUP(E21,List!$K$2:$M$447,2,FALSE)","v":"ICMD00017_DHV"},{"$f":"K21&\" \"&\"AT%\"&C21&F21&\" \"&\":\"&I21&\";\"&\" \"&\"(*\"&J21&\"*)\"","v":"ICMD00017_DHV AT%M5032.0 :INT; (*17#CPU心跳反馈*)"},{"$f":"REPLACE(REPLACE(L21,SEARCH(\"AT%\",L21),,REPT(\" \",25-SEARCH(\"AT%\",L21))),SEARCH(\":\",REPLACE(L21,SEARCH(\"AT%\",L21),,REPT(\" \",25-SEARCH(\"AT%\",L21)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L21,SEARCH(\"AT%\",L21),,REPT(\" \",25-SEARCH(\"AT%\",L21))))))","v":"ICMD00017_DHV           AT%M5032.0     :INT; (*17#CPU心跳反馈*)"}]
["命令","I","M","00018","心跳值","5034.0","6000.0","验证通过","INT","18#CPU心跳反馈",{"$f":"B22&VLOOKUP(A22,List!$B$3:$D$445,2,FALSE)&D22&\"_\"&VLOOKUP(E22,List!$K$2:$M$447,2,FALSE)","v":"ICMD00018_DHV"},"ICMD00018_DHV AT%M5034.0 :INT; (*18#CPU心跳反馈*)","ICMD00018_DHV           AT%M5034.0     :INT; (*18#CPU心跳反馈*)"]
["命令","I","M","00019","心跳值","5036.0","6000.0","验证通过","INT","19#CPU心跳反馈",{"$f":"B23&VLOOKUP(A23,List!$B$3:$D$445,2,FALSE)&D23&\"_\"&VLOOKUP(E23,List!$K$2:$M$447,2,FALSE)","v":"ICMD00019_DHV"},"ICMD00019_DHV AT%M5036.0 :INT; (*19#CPU心跳反馈*)","ICMD00019_DHV           AT%M5036.0     :INT; (*19#CPU心跳反馈*)"]
["命令","I","M","00020","心跳值","5038.0","6000.0","验证通过","INT","20#CPU心跳反馈",{"$f":"B24&VLOOKUP(A24,List!$B$3:$D$445,2,FALSE)&D24&\"_\"&VLOOKUP(E24,List!$K$2:$M$447,2,FALSE)","v":"ICMD00020_DHV"},"ICMD00020_DHV AT%M5038.0 :INT; (*20#CPU心跳反馈*)","ICMD00020_DHV           AT%M5038.0     :INT; (*20#CPU心跳反馈*)"]
["命令","I","M","00021","心跳值","5040.0","6000.0","验证通过","INT","21#CPU心跳反馈",{"$f":"B25&VLOOKUP(A25,List!$B$3:$D$445,2,FALSE)&D25&\"_\"&VLOOKUP(E25,List!$K$2:$M$447,2,FALSE)","v":"ICMD00021_DHV"},"ICMD00021_DHV AT%M5040.0 :INT; (*21#CPU心跳反馈*)","ICMD00021_DHV           AT%M5040.0     :INT; (*21#CPU心跳反馈*)"]
["命令","I","M","00022","心跳值","5042.0","6000.0","验证通过","INT","22#CPU心跳反馈",{"$f":"B26&VLOOKUP(A26,List!$B$3:$D$445,2,FALSE)&D26&\"_\"&VLOOKUP(E26,List!$K$2:$M$447,2,FALSE)","v":"ICMD00022_DHV"},"ICMD00022_DHV AT%M5042.0 :INT; (*22#CPU心跳反馈*)","ICMD00022_DHV           AT%M5042.0     :INT; (*22#CPU心跳反馈*)"]
["命令","I","M","00023","心跳值","5044.0","6000.0","验证通过","INT","23#CPU心跳反馈",{"$f":"B27&VLOOKUP(A27,List!$B$3:$D$445,2,FALSE)&D27&\"_\"&VLOOKUP(E27,List!$K$2:$M$447,2,FALSE)","v":"ICMD00023_DHV"},"ICMD00023_DHV AT%M5044.0 :INT; (*23#CPU心跳反馈*)","ICMD00023_DHV           AT%M5044.0     :INT; (*23#CPU心跳反馈*)"]
["命令","I","M","00024","心跳值","5046.0","6000.0","验证通过","INT","24#CPU心跳反馈",{"$f":"B28&VLOOKUP(A28,List!$B$3:$D$445,2,FALSE)&D28&\"_\"&VLOOKUP(E28,List!$K$2:$M$447,2,FALSE)","v":"ICMD00024_DHV"},"ICMD00024_DHV AT%M5046.0 :INT; (*24#CPU心跳反馈*)","ICMD00024_DHV           AT%M5046.0     :INT; (*24#CPU心跳反馈*)"]
["命令","I","M","00025","心跳值","5048.0","6000.0","验证通过","INT","25#CPU心跳反馈",{"$f":"B29&VLOOKUP(A29,List!$B$3:$D$445,2,FALSE)&D29&\"_\"&VLOOKUP(E29,List!$K$2:$M$447,2,FALSE)","v":"ICMD00025_DHV"},{"$f":"K29&\" \"&\"AT%\"&C29&F29&\" \"&\":\"&I29&\";\"&\" \"&\"(*\"&J29&\"*)\"","v":"ICMD00025_DHV AT%M5048.0 :INT; (*25#CPU心跳反馈*)"},{"$f":"REPLACE(REPLACE(L29,SEARCH(\"AT%\",L29),,REPT(\" \",25-SEARCH(\"AT%\",L29))),SEARCH(\":\",REPLACE(L29,SEARCH(\"AT%\",L29),,REPT(\" \",25-SEARCH(\"AT%\",L29)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L29,SEARCH(\"AT%\",L29),,REPT(\" \",25-SEARCH(\"AT%\",L29))))))","v":"ICMD00025_DHV           AT%M5048.0     :INT; (*25#CPU心跳反馈*)"}]
["命令","I","M","00026","心跳值","5050.0","6000.0","验证通过","INT","26#CPU心跳反馈",{"$f":"B30&VLOOKUP(A30,List!$B$3:$D$445,2,FALSE)&D30&\"_\"&VLOOKUP(E30,List!$K$2:$M$447,2,FALSE)","v":"ICMD00026_DHV"},"ICMD00026_DHV AT%M5050.0 :INT; (*26#CPU心跳反馈*)","ICMD00026_DHV           AT%M5050.0     :INT; (*26#CPU心跳反馈*)"]
["命令","I","M","00027","心跳值","5052.0","6000.0","验证通过","INT","27#CPU心跳反馈",{"$f":"B31&VLOOKUP(A31,List!$B$3:$D$445,2,FALSE)&D31&\"_\"&VLOOKUP(E31,List!$K$2:$M$447,2,FALSE)","v":"ICMD00027_DHV"},"ICMD00027_DHV AT%M5052.0 :INT; (*27#CPU心跳反馈*)","ICMD00027_DHV           AT%M5052.0     :INT; (*27#CPU心跳反馈*)"]
["命令","I","M","00028","心跳值","5054.0","6000.0","验证通过","INT","28#CPU心跳反馈",{"$f":"B32&VLOOKUP(A32,List!$B$3:$D$445,2,FALSE)&D32&\"_\"&VLOOKUP(E32,List!$K$2:$M$447,2,FALSE)","v":"ICMD00028_DHV"},"ICMD00028_DHV AT%M5054.0 :INT; (*28#CPU心跳反馈*)","ICMD00028_DHV           AT%M5054.0     :INT; (*28#CPU心跳反馈*)"]
["命令","I","M","00029","心跳值","5056.0","6000.0","验证通过","INT","29#CPU心跳反馈",{"$f":"B33&VLOOKUP(A33,List!$B$3:$D$445,2,FALSE)&D33&\"_\"&VLOOKUP(E33,List!$K$2:$M$447,2,FALSE)","v":"ICMD00029_DHV"},{"$f":"K33&\" \"&\"AT%\"&C33&F33&\" \"&\":\"&I33&\";\"&\" \"&\"(*\"&J33&\"*)\"","v":"ICMD00029_DHV AT%M5056.0 :INT; (*29#CPU心跳反馈*)"},{"$f":"REPLACE(REPLACE(L33,SEARCH(\"AT%\",L33),,REPT(\" \",25-SEARCH(\"AT%\",L33))),SEARCH(\":\",REPLACE(L33,SEARCH(\"AT%\",L33),,REPT(\" \",25-SEARCH(\"AT%\",L33)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L33,SEARCH(\"AT%\",L33),,REPT(\" \",25-SEARCH(\"AT%\",L33))))))","v":"ICMD00029_DHV           AT%M5056.0     :INT; (*29#CPU心跳反馈*)"}]
["命令","I","M","00030","心跳值","5058.0","6000.0","验证通过","INT","30#CPU心跳反馈",{"$f":"B34&VLOOKUP(A34,List!$B$3:$D$445,2,FALSE)&D34&\"_\"&VLOOKUP(E34,List!$K$2:$M$447,2,FALSE)","v":"ICMD00030_DHV"},"ICMD00030_DHV AT%M5058.0 :INT; (*30#CPU心跳反馈*)","ICMD00030_DHV           AT%M5058.0     :INT; (*30#CPU心跳反馈*)"]
["命令","I","M","00031","心跳值","5060.0","6000.0","验证通过","INT","31#CPU心跳反馈",{"$f":"B35&VLOOKUP(A35,List!$B$3:$D$445,2,FALSE)&D35&\"_\"&VLOOKUP(E35,List!$K$2:$M$447,2,FALSE)","v":"ICMD00031_DHV"},{"$f":"K35&\" \"&\"AT%\"&C35&F35&\" \"&\":\"&I35&\";\"&\" \"&\"(*\"&J35&\"*)\"","v":"ICMD00031_DHV AT%M5060.0 :INT; (*31#CPU心跳反馈*)"},{"$f":"REPLACE(REPLACE(L35,SEARCH(\"AT%\",L35),,REPT(\" \",25-SEARCH(\"AT%\",L35))),SEARCH(\":\",REPLACE(L35,SEARCH(\"AT%\",L35),,REPT(\" \",25-SEARCH(\"AT%\",L35)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L35,SEARCH(\"AT%\",L35),,REPT(\" \",25-SEARCH(\"AT%\",L35))))))","v":"ICMD00031_DHV           AT%M5060.0     :INT; (*31#CPU心跳反馈*)"}]
["命令","I","M","00032","心跳值","5062.0","6000.0","验证通过","INT","32#CPU心跳反馈",{"$f":"B36&VLOOKUP(A36,List!$B$3:$D$445,2,FALSE)&D36&\"_\"&VLOOKUP(E36,List!$K$2:$M$447,2,FALSE)","v":"ICMD00032_DHV"},{"$f":"K36&\" \"&\"AT%\"&C36&F36&\" \"&\":\"&I36&\";\"&\" \"&\"(*\"&J36&\"*)\"","v":"ICMD00032_DHV AT%M5062.0 :INT; (*32#CPU心跳反馈*)"},{"$f":"REPLACE(REPLACE(L36,SEARCH(\"AT%\",L36),,REPT(\" \",25-SEARCH(\"AT%\",L36))),SEARCH(\":\",REPLACE(L36,SEARCH(\"AT%\",L36),,REPT(\" \",25-SEARCH(\"AT%\",L36)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L36,SEARCH(\"AT%\",L36),,REPT(\" \",25-SEARCH(\"AT%\",L36))))))","v":"ICMD00032_DHV           AT%M5062.0     :INT; (*32#CPU心跳反馈*)"}]
["主控CPU-->从CPU（地上）",{"$nulls":4},"发送地址","接收地址.auto"]
["命令","RNQ","M","00000","心跳值","4000.0",null,{"$f":"IF((IF(OR(I38=\"INT\",I38=\"WORD\",I38=\"BOOL\"),MOD(F38,2),MOD(F38,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"INT","心跳值",{"$f":"B38&VLOOKUP(A38,List!$B$3:$D$445,2,FALSE)&D38&\"_\"&VLOOKUP(E38,List!$K$2:$M$447,2,FALSE)","v":"RNQCMD00000_DHV"},{"$f":"K38&\" \"&\"AT%\"&C38&F38&\" \"&\":\"&I38&\";\"&\" \"&\"(*\"&J38&\"*)\"","v":"RNQCMD00000_DHV AT%M4000.0 :INT; (*心跳值*)"},{"$f":"REPLACE(REPLACE(L38,SEARCH(\"AT%\",L38),,REPT(\" \",25-SEARCH(\"AT%\",L38))),SEARCH(\":\",REPLACE(L38,SEARCH(\"AT%\",L38),,REPT(\" \",25-SEARCH(\"AT%\",L38)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L38,SEARCH(\"AT%\",L38),,REPT(\" \",25-SEARCH(\"AT%\",L38))))))","v":"RNQCMD00000_DHV         AT%M4000.0     :INT; (*心跳值*)"}]
["空调机组","RNQ","M","00000","新云模式",{"$f":"IF(OR(I38=\"REAL\",I38=\"DWORD\",I38=\"DINT\"),(IF(OR(I39=\"REAL\",I39=\"DWORD\",I39=\"DINT\"),F38+4+MOD(F38,4),F38+4)),(IF(OR(I39=\"REAL\",I39=\"DWORD\",I39=\"DINT\"),F38+4+MOD(F38,4),F38+2)))&\".0\"","v":"4002.0"},null,"验证通过","BOOL","空调机组新云模式",{"$f":"B39&VLOOKUP(A39,List!$B$3:$D$445,2,FALSE)&D39&\"_\"&VLOOKUP(E39,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU00000_CM"},"RNQAHU00000_CM AT%M4002.0 :BOOL; (*空调机组新云模式*)","RNQAHU00000_CM          AT%M4002.0     :BOOL; (*空调机组新云模式*)"]
["风机盘管","RNQ","M","00000","新云模式",{"$f":"IF(OR(I39=\"REAL\",I39=\"DWORD\",I39=\"DINT\"),(IF(OR(I40=\"REAL\",I40=\"DWORD\",I40=\"DINT\"),F39+4+MOD(F39,4),F39+4)),(IF(OR(I40=\"REAL\",I40=\"DWORD\",I40=\"DINT\"),F39+4+MOD(F39,4),F39+2)))&\".0\"","v":"4004.0"},null,"验证通过","BOOL","风机盘管新云模式",{"$f":"B40&VLOOKUP(A40,List!$B$3:$D$445,2,FALSE)&D40&\"_\"&VLOOKUP(E40,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU00000_CM"},"RNQFCU00000_CM AT%M4004.0 :BOOL; (*风机盘管新云模式*)","RNQFCU00000_CM          AT%M4004.0     :BOOL; (*风机盘管新云模式*)"]
["照明控制箱","RNQ","M","00000","新云模式","4006.0",null,"验证通过","BOOL","照明控制箱新云模式",{"$f":"B41&VLOOKUP(A41,List!$B$3:$D$445,2,FALSE)&D41&\"_\"&VLOOKUP(E41,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB00000_CM"},"RNQLCB00000_CM AT%M4006.0 :BOOL; (*照明控制箱新云模式*)","RNQLCB00000_CM          AT%M4006.0     :BOOL; (*照明控制箱新云模式*)"]
["排风机","RNQ","M","00000","新云模式","4008.0",null,{"$f":"IF((IF(OR(I42=\"INT\",I42=\"WORD\",I42=\"BOOL\"),MOD(F42,2),MOD(F42,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","送排风机新云模式",{"$f":"B42&VLOOKUP(A42,List!$B$3:$D$445,2,FALSE)&D42&\"_\"&VLOOKUP(E42,List!$K$2:$M$447,2,FALSE)","v":"RNQEAF00000_CM"},{"$f":"K42&\" \"&\"AT%\"&C42&F42&\" \"&\":\"&I42&\";\"&\" \"&\"(*\"&J42&\"*)\"","v":"RNQEAF00000_CM AT%M4008.0 :BOOL; (*送排风机新云模式*)"},"RNQEAF00000_CM          AT%M4008.0     :BOOL; (*送排风机新云模式*)"]
["P新风机组","RNQ","M","00000","新云模式","4010.0",null,"验证通过","BOOL","新风机组新云模式",{"$f":"B43&VLOOKUP(A43,List!$B$3:$D$445,2,FALSE)&D43&\"_\"&VLOOKUP(E43,List!$K$2:$M$447,2,FALSE)","v":"RNQPAU00000_CM"},"RNQPAU00000_CM AT%M4010.0 :BOOL; (*新风机组新云模式*)","RNQPAU00000_CM          AT%M4010.0     :BOOL; (*新风机组新云模式*)"]
["风幕机","RNQ","M","00000","新云模式","4012.0",null,"验证通过","BOOL","风幕机新云模式",{"$f":"B44&VLOOKUP(A44,List!$B$3:$D$445,2,FALSE)&D44&\"_\"&VLOOKUP(E44,List!$K$2:$M$447,2,FALSE)","v":"RNQAC00000_CM"},"RNQAC00000_CM AT%M4012.0 :BOOL; (*风幕机新云模式*)",{"$f":"REPLACE(REPLACE(L44,SEARCH(\"AT%\",L44),,REPT(\" \",25-SEARCH(\"AT%\",L44))),SEARCH(\":\",REPLACE(L44,SEARCH(\"AT%\",L44),,REPT(\" \",25-SEARCH(\"AT%\",L44)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L44,SEARCH(\"AT%\",L44),,REPT(\" \",25-SEARCH(\"AT%\",L44))))))","v":"RNQAC00000_CM           AT%M4012.0     :BOOL; (*风幕机新云模式*)"}]
["冷水机组","RNQ","M","00000","新云模式","4014.0",null,{"$f":"IF((IF(OR(I45=\"INT\",I45=\"WORD\",I45=\"BOOL\"),MOD(F45,2),MOD(F45,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","冷源新云模式",{"$f":"B45&VLOOKUP(A45,List!$B$3:$D$445,2,FALSE)&D45&\"_\"&VLOOKUP(E45,List!$K$2:$M$447,2,FALSE)","v":"RNQCHR00000_CM"},"RNQCHR00000_CM AT%M4014.0 :BOOL; (*冷源新云模式*)","RNQCHR00000_CM          AT%M4014.0     :BOOL; (*冷源新云模式*)"]
["空调机组","RNQ","M","B3X00","设定温度值","4020.0",null,"验证通过","REAL","空调机组B3层温度全局设定",{"$f":"B46&VLOOKUP(A46,List!$B$3:$D$445,2,FALSE)&D46&\"_\"&VLOOKUP(E46,List!$K$2:$M$447,2,FALSE)","v":"RNQAHUB3X00_TSET"},"RNQAHUB3X00_TSET AT%M4020.0 :REAL; (*空调机组B3层温度全局设定*)","RNQAHUB3X00_TSET        AT%M4020.0     :REAL; (*空调机组B3层温度全局设定*)"]
["空调机组","RNQ","M","B2X00","设定温度值","4024.0",null,"验证通过","REAL","空调机组B2层温度全局设定",{"$f":"B47&VLOOKUP(A47,List!$B$3:$D$445,2,FALSE)&D47&\"_\"&VLOOKUP(E47,List!$K$2:$M$447,2,FALSE)","v":"RNQAHUB2X00_TSET"},"RNQAHUB2X00_TSET AT%M4024.0 :REAL; (*空调机组B2层温度全局设定*)","RNQAHUB2X00_TSET        AT%M4024.0     :REAL; (*空调机组B2层温度全局设定*)"]
["空调机组","RNQ","M","B1X00","设定温度值","4028.0",null,"验证通过","REAL","空调机组B1层温度全局设定",{"$f":"B48&VLOOKUP(A48,List!$B$3:$D$445,2,FALSE)&D48&\"_\"&VLOOKUP(E48,List!$K$2:$M$447,2,FALSE)","v":"RNQAHUB1X00_TSET"},"RNQAHUB1X00_TSET AT%M4028.0 :REAL; (*空调机组B1层温度全局设定*)","RNQAHUB1X00_TSET        AT%M4028.0     :REAL; (*空调机组B1层温度全局设定*)"]
["空调机组","RNQ","M","01X00","设定温度值","4032.0",null,"验证通过","REAL","空调机组1层温度全局设定",{"$f":"B49&VLOOKUP(A49,List!$B$3:$D$445,2,FALSE)&D49&\"_\"&VLOOKUP(E49,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU01X00_TSET"},"RNQAHU01X00_TSET AT%M4032.0 :REAL; (*空调机组1层温度全局设定*)","RNQAHU01X00_TSET        AT%M4032.0     :REAL; (*空调机组1层温度全局设定*)"]
["空调机组","RNQ","M","02X00","设定温度值","4036.0",null,"验证通过","REAL","空调机组2层温度全局设定",{"$f":"B50&VLOOKUP(A50,List!$B$3:$D$445,2,FALSE)&D50&\"_\"&VLOOKUP(E50,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU02X00_TSET"},"RNQAHU02X00_TSET AT%M4036.0 :REAL; (*空调机组2层温度全局设定*)",{"$f":"REPLACE(REPLACE(L50,SEARCH(\"AT%\",L50),,REPT(\" \",25-SEARCH(\"AT%\",L50))),SEARCH(\":\",REPLACE(L50,SEARCH(\"AT%\",L50),,REPT(\" \",25-SEARCH(\"AT%\",L50)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L50,SEARCH(\"AT%\",L50),,REPT(\" \",25-SEARCH(\"AT%\",L50))))))","v":"RNQAHU02X00_TSET        AT%M4036.0     :REAL; (*空调机组2层温度全局设定*)"}]
["空调机组","RNQ","M","03X00","设定温度值","4040.0",null,"验证通过","REAL","空调机组3层温度全局设定",{"$f":"B51&VLOOKUP(A51,List!$B$3:$D$445,2,FALSE)&D51&\"_\"&VLOOKUP(E51,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU03X00_TSET"},"RNQAHU03X00_TSET AT%M4040.0 :REAL; (*空调机组3层温度全局设定*)","RNQAHU03X00_TSET        AT%M4040.0     :REAL; (*空调机组3层温度全局设定*)"]
["空调机组","RNQ","M","04X00","设定温度值","4044.0",null,"验证通过","REAL","空调机组4层温度全局设定",{"$f":"B52&VLOOKUP(A52,List!$B$3:$D$445,2,FALSE)&D52&\"_\"&VLOOKUP(E52,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU04X00_TSET"},"RNQAHU04X00_TSET AT%M4044.0 :REAL; (*空调机组4层温度全局设定*)","RNQAHU04X00_TSET        AT%M4044.0     :REAL; (*空调机组4层温度全局设定*)"]
["空调机组","RNQ","M","05X00","设定温度值","4048.0",null,"验证通过","REAL","空调机组5层温度全局设定",{"$f":"B53&VLOOKUP(A53,List!$B$3:$D$445,2,FALSE)&D53&\"_\"&VLOOKUP(E53,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU05X00_TSET"},"RNQAHU05X00_TSET AT%M4048.0 :REAL; (*空调机组5层温度全局设定*)","RNQAHU05X00_TSET        AT%M4048.0     :REAL; (*空调机组5层温度全局设定*)"]
["空调机组","RNQ","M","06X00","设定温度值","4052.0",null,"验证通过","REAL","空调机组6层温度全局设定",{"$f":"B54&VLOOKUP(A54,List!$B$3:$D$445,2,FALSE)&D54&\"_\"&VLOOKUP(E54,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU06X00_TSET"},"RNQAHU06X00_TSET AT%M4052.0 :REAL; (*空调机组6层温度全局设定*)","RNQAHU06X00_TSET        AT%M4052.0     :REAL; (*空调机组6层温度全局设定*)"]
["空调机组","RNQ","M","07X00","设定温度值","4056.0",null,{"$f":"IF((IF(OR(I55=\"INT\",I55=\"WORD\",I55=\"BOOL\"),MOD(F55,2),MOD(F55,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"REAL","空调机组7层温度全局设定",{"$f":"B55&VLOOKUP(A55,List!$B$3:$D$445,2,FALSE)&D55&\"_\"&VLOOKUP(E55,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU07X00_TSET"},{"$f":"K55&\" \"&\"AT%\"&C55&F55&\" \"&\":\"&I55&\";\"&\" \"&\"(*\"&J55&\"*)\"","v":"RNQAHU07X00_TSET AT%M4056.0 :REAL; (*空调机组7层温度全局设定*)"},{"$f":"REPLACE(REPLACE(L55,SEARCH(\"AT%\",L55),,REPT(\" \",25-SEARCH(\"AT%\",L55))),SEARCH(\":\",REPLACE(L55,SEARCH(\"AT%\",L55),,REPT(\" \",25-SEARCH(\"AT%\",L55)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L55,SEARCH(\"AT%\",L55),,REPT(\" \",25-SEARCH(\"AT%\",L55))))))","v":"RNQAHU07X00_TSET        AT%M4056.0     :REAL; (*空调机组7层温度全局设定*)"}]
["空调机组","RNQ","M","08X00","设定温度值","4060.0",null,"验证通过","REAL","空调机组8层温度全局设定",{"$f":"B56&VLOOKUP(A56,List!$B$3:$D$445,2,FALSE)&D56&\"_\"&VLOOKUP(E56,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU08X00_TSET"},"RNQAHU08X00_TSET AT%M4060.0 :REAL; (*空调机组8层温度全局设定*)","RNQAHU08X00_TSET        AT%M4060.0     :REAL; (*空调机组8层温度全局设定*)"]
["空调机组","RNQ","M","B3X00","季节模式","4064.0",null,"验证通过","INT","空调机组B3层季节模式全局设定",{"$f":"B57&VLOOKUP(A57,List!$B$3:$D$445,2,FALSE)&D57&\"_\"&VLOOKUP(E57,List!$K$2:$M$447,2,FALSE)","v":"RNQAHUB3X00_SM"},"RNQAHUB3X00_SM AT%M4064.0 :INT; (*空调机组B3层季节模式全局设定*)","RNQAHUB3X00_SM          AT%M4064.0     :INT; (*空调机组B3层季节模式全局设定*)"]
["空调机组","RNQ","M","B2X00","季节模式","4066.0",null,"验证通过","INT","空调机组B2层季节模式全局设定",{"$f":"B58&VLOOKUP(A58,List!$B$3:$D$445,2,FALSE)&D58&\"_\"&VLOOKUP(E58,List!$K$2:$M$447,2,FALSE)","v":"RNQAHUB2X00_SM"},"RNQAHUB2X00_SM AT%M4066.0 :INT; (*空调机组B2层季节模式全局设定*)","RNQAHUB2X00_SM          AT%M4066.0     :INT; (*空调机组B2层季节模式全局设定*)"]
["空调机组","RNQ","M","B1X00","季节模式","4068.0",null,"验证通过","INT","空调机组B1层季节模式全局设定",{"$f":"B59&VLOOKUP(A59,List!$B$3:$D$445,2,FALSE)&D59&\"_\"&VLOOKUP(E59,List!$K$2:$M$447,2,FALSE)","v":"RNQAHUB1X00_SM"},"RNQAHUB1X00_SM AT%M4068.0 :INT; (*空调机组B1层季节模式全局设定*)","RNQAHUB1X00_SM          AT%M4068.0     :INT; (*空调机组B1层季节模式全局设定*)"]
["空调机组","RNQ","M","01X00","季节模式","4070.0",null,"验证通过","INT","空调机组1层季节模式全局设定",{"$f":"B60&VLOOKUP(A60,List!$B$3:$D$445,2,FALSE)&D60&\"_\"&VLOOKUP(E60,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU01X00_SM"},"RNQAHU01X00_SM AT%M4070.0 :INT; (*空调机组1层季节模式全局设定*)","RNQAHU01X00_SM          AT%M4070.0     :INT; (*空调机组1层季节模式全局设定*)"]
["空调机组","RNQ","M","02X00","季节模式","4072.0",null,"验证通过","INT","空调机组2层季节模式全局设定",{"$f":"B61&VLOOKUP(A61,List!$B$3:$D$445,2,FALSE)&D61&\"_\"&VLOOKUP(E61,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU02X00_SM"},"RNQAHU02X00_SM AT%M4072.0 :INT; (*空调机组2层季节模式全局设定*)","RNQAHU02X00_SM          AT%M4072.0     :INT; (*空调机组2层季节模式全局设定*)"]
["空调机组","RNQ","M","03X00","季节模式","4074.0",null,"验证通过","INT","空调机组3层季节模式全局设定",{"$f":"B62&VLOOKUP(A62,List!$B$3:$D$445,2,FALSE)&D62&\"_\"&VLOOKUP(E62,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU03X00_SM"},"RNQAHU03X00_SM AT%M4074.0 :INT; (*空调机组3层季节模式全局设定*)","RNQAHU03X00_SM          AT%M4074.0     :INT; (*空调机组3层季节模式全局设定*)"]
["空调机组","RNQ","M","04X00","季节模式","4076.0",null,"验证通过","INT","空调机组4层季节模式全局设定",{"$f":"B63&VLOOKUP(A63,List!$B$3:$D$445,2,FALSE)&D63&\"_\"&VLOOKUP(E63,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU04X00_SM"},"RNQAHU04X00_SM AT%M4076.0 :INT; (*空调机组4层季节模式全局设定*)","RNQAHU04X00_SM          AT%M4076.0     :INT; (*空调机组4层季节模式全局设定*)"]
["空调机组","RNQ","M","05X00","季节模式","4078.0",null,"验证通过","INT","空调机组5层季节模式全局设定",{"$f":"B64&VLOOKUP(A64,List!$B$3:$D$445,2,FALSE)&D64&\"_\"&VLOOKUP(E64,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU05X00_SM"},"RNQAHU05X00_SM AT%M4078.0 :INT; (*空调机组5层季节模式全局设定*)","RNQAHU05X00_SM          AT%M4078.0     :INT; (*空调机组5层季节模式全局设定*)"]
["空调机组","RNQ","M","06X00","季节模式","4080.0",null,"验证通过","INT","空调机组6层季节模式全局设定",{"$f":"B65&VLOOKUP(A65,List!$B$3:$D$445,2,FALSE)&D65&\"_\"&VLOOKUP(E65,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU06X00_SM"},"RNQAHU06X00_SM AT%M4080.0 :INT; (*空调机组6层季节模式全局设定*)","RNQAHU06X00_SM          AT%M4080.0     :INT; (*空调机组6层季节模式全局设定*)"]
["空调机组","RNQ","M","07X00","季节模式","4082.0",null,{"$f":"IF((IF(OR(I66=\"INT\",I66=\"WORD\",I66=\"BOOL\"),MOD(F66,2),MOD(F66,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"INT","空调机组7层季节模式全局设定",{"$f":"B66&VLOOKUP(A66,List!$B$3:$D$445,2,FALSE)&D66&\"_\"&VLOOKUP(E66,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU07X00_SM"},"RNQAHU07X00_SM AT%M4082.0 :INT; (*空调机组7层季节模式全局设定*)","RNQAHU07X00_SM          AT%M4082.0     :INT; (*空调机组7层季节模式全局设定*)"]
["空调机组","RNQ","M","08X00","季节模式","4084.0",null,"验证通过","INT","空调机组8层季节模式全局设定",{"$f":"B67&VLOOKUP(A67,List!$B$3:$D$445,2,FALSE)&D67&\"_\"&VLOOKUP(E67,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU08X00_SM"},"RNQAHU08X00_SM AT%M4084.0 :INT; (*空调机组8层季节模式全局设定*)","RNQAHU08X00_SM          AT%M4084.0     :INT; (*空调机组8层季节模式全局设定*)"]
["空调机组","RNQ","M","B3X00","程序控制","4086.0",null,"验证通过","BOOL","空调机组B3层启停控制",{"$f":"B68&VLOOKUP(A68,List!$B$3:$D$445,2,FALSE)&D68&\"_\"&VLOOKUP(E68,List!$K$2:$M$447,2,FALSE)","v":"RNQAHUB3X00_PC"},"RNQAHUB3X00_PC AT%M4086.0 :BOOL; (*空调机组B3层启停控制*)","RNQAHUB3X00_PC          AT%M4086.0     :BOOL; (*空调机组B3层启停控制*)"]
["空调机组","RNQ","M","B2X00","程序控制","4088.0",null,"验证通过","BOOL","空调机组B2层启停控制",{"$f":"B69&VLOOKUP(A69,List!$B$3:$D$445,2,FALSE)&D69&\"_\"&VLOOKUP(E69,List!$K$2:$M$447,2,FALSE)","v":"RNQAHUB2X00_PC"},"RNQAHUB2X00_PC AT%M4088.0 :BOOL; (*空调机组B2层启停控制*)","RNQAHUB2X00_PC          AT%M4088.0     :BOOL; (*空调机组B2层启停控制*)"]
["空调机组","RNQ","M","B1X00","程序控制","4090.0",null,"验证通过","BOOL","空调机组B1层启停控制",{"$f":"B70&VLOOKUP(A70,List!$B$3:$D$445,2,FALSE)&D70&\"_\"&VLOOKUP(E70,List!$K$2:$M$447,2,FALSE)","v":"RNQAHUB1X00_PC"},"RNQAHUB1X00_PC AT%M4090.0 :BOOL; (*空调机组B1层启停控制*)","RNQAHUB1X00_PC          AT%M4090.0     :BOOL; (*空调机组B1层启停控制*)"]
["空调机组","RNQ","M","01X00","程序控制","4092.0",null,"验证通过","BOOL","空调机组1层启停控制",{"$f":"B71&VLOOKUP(A71,List!$B$3:$D$445,2,FALSE)&D71&\"_\"&VLOOKUP(E71,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU01X00_PC"},"RNQAHU01X00_PC AT%M4092.0 :BOOL; (*空调机组1层启停控制*)","RNQAHU01X00_PC          AT%M4092.0     :BOOL; (*空调机组1层启停控制*)"]
["空调机组","RNQ","M","02X00","程序控制","4094.0",null,"验证通过","BOOL","空调机组2层启停控制",{"$f":"B72&VLOOKUP(A72,List!$B$3:$D$445,2,FALSE)&D72&\"_\"&VLOOKUP(E72,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU02X00_PC"},"RNQAHU02X00_PC AT%M4094.0 :BOOL; (*空调机组2层启停控制*)","RNQAHU02X00_PC          AT%M4094.0     :BOOL; (*空调机组2层启停控制*)"]
["空调机组","RNQ","M","03X00","程序控制","4096.0",null,"验证通过","BOOL","空调机组3层启停控制",{"$f":"B73&VLOOKUP(A73,List!$B$3:$D$445,2,FALSE)&D73&\"_\"&VLOOKUP(E73,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU03X00_PC"},"RNQAHU03X00_PC AT%M4096.0 :BOOL; (*空调机组3层启停控制*)","RNQAHU03X00_PC          AT%M4096.0     :BOOL; (*空调机组3层启停控制*)"]
["空调机组","RNQ","M","04X00","程序控制","4098.0",null,"验证通过","BOOL","空调机组4层启停控制",{"$f":"B74&VLOOKUP(A74,List!$B$3:$D$445,2,FALSE)&D74&\"_\"&VLOOKUP(E74,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU04X00_PC"},"RNQAHU04X00_PC AT%M4098.0 :BOOL; (*空调机组4层启停控制*)","RNQAHU04X00_PC          AT%M4098.0     :BOOL; (*空调机组4层启停控制*)"]
["空调机组","RNQ","M","05X00","程序控制","4100.0",null,"验证通过","BOOL","空调机组5层启停控制",{"$f":"B75&VLOOKUP(A75,List!$B$3:$D$445,2,FALSE)&D75&\"_\"&VLOOKUP(E75,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU05X00_PC"},"RNQAHU05X00_PC AT%M4100.0 :BOOL; (*空调机组5层启停控制*)","RNQAHU05X00_PC          AT%M4100.0     :BOOL; (*空调机组5层启停控制*)"]
["空调机组","RNQ","M","06X00","程序控制","4102.0",null,"验证通过","BOOL","空调机组6层启停控制",{"$f":"B76&VLOOKUP(A76,List!$B$3:$D$445,2,FALSE)&D76&\"_\"&VLOOKUP(E76,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU06X00_PC"},"RNQAHU06X00_PC AT%M4102.0 :BOOL; (*空调机组6层启停控制*)","RNQAHU06X00_PC          AT%M4102.0     :BOOL; (*空调机组6层启停控制*)"]
["空调机组","RNQ","M","07X00","程序控制","4104.0",null,{"$f":"IF((IF(OR(I77=\"INT\",I77=\"WORD\",I77=\"BOOL\"),MOD(F77,2),MOD(F77,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","空调机组7层启停控制",{"$f":"B77&VLOOKUP(A77,List!$B$3:$D$445,2,FALSE)&D77&\"_\"&VLOOKUP(E77,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU07X00_PC"},"RNQAHU07X00_PC AT%M4104.0 :BOOL; (*空调机组7层启停控制*)","RNQAHU07X00_PC          AT%M4104.0     :BOOL; (*空调机组7层启停控制*)"]
["空调机组","RNQ","M","08X00","程序控制","4106.0",null,"验证通过","BOOL","空调机组8层启停控制",{"$f":"B78&VLOOKUP(A78,List!$B$3:$D$445,2,FALSE)&D78&\"_\"&VLOOKUP(E78,List!$K$2:$M$447,2,FALSE)","v":"RNQAHU08X00_PC"},"RNQAHU08X00_PC AT%M4106.0 :BOOL; (*空调机组8层启停控制*)","RNQAHU08X00_PC          AT%M4106.0     :BOOL; (*空调机组8层启停控制*)"]
["风机盘管","RNQ","M","B3X00","设定温度值","4112.0",null,{"$f":"IF((IF(OR(I79=\"INT\",I79=\"WORD\",I79=\"BOOL\"),MOD(F79,2),MOD(F79,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"REAL","风机盘管B3层温度全局设定",{"$f":"B79&VLOOKUP(A79,List!$B$3:$D$445,2,FALSE)&D79&\"_\"&VLOOKUP(E79,List!$K$2:$M$447,2,FALSE)","v":"RNQFCUB3X00_TSET"},{"$f":"K79&\" \"&\"AT%\"&C79&F79&\" \"&\":\"&I79&\";\"&\" \"&\"(*\"&J79&\"*)\"","v":"RNQFCUB3X00_TSET AT%M4112.0 :REAL; (*风机盘管B3层温度全局设定*)"},"RNQFCUB3X00_TSET        AT%M4112.0     :REAL; (*风机盘管B3层温度全局设定*)"]
["风机盘管","RNQ","M","B2X00","设定温度值","4116.0",null,"验证通过","REAL","风机盘管B2层温度全局设定",{"$f":"B80&VLOOKUP(A80,List!$B$3:$D$445,2,FALSE)&D80&\"_\"&VLOOKUP(E80,List!$K$2:$M$447,2,FALSE)","v":"RNQFCUB2X00_TSET"},"RNQFCUB2X00_TSET AT%M4116.0 :REAL; (*风机盘管B2层温度全局设定*)",{"$f":"REPLACE(REPLACE(L80,SEARCH(\"AT%\",L80),,REPT(\" \",25-SEARCH(\"AT%\",L80))),SEARCH(\":\",REPLACE(L80,SEARCH(\"AT%\",L80),,REPT(\" \",25-SEARCH(\"AT%\",L80)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L80,SEARCH(\"AT%\",L80),,REPT(\" \",25-SEARCH(\"AT%\",L80))))))","v":"RNQFCUB2X00_TSET        AT%M4116.0     :REAL; (*风机盘管B2层温度全局设定*)"}]
["风机盘管","RNQ","M","B1X00","设定温度值","4120.0",null,"验证通过","REAL","风机盘管B1层温度全局设定",{"$f":"B81&VLOOKUP(A81,List!$B$3:$D$445,2,FALSE)&D81&\"_\"&VLOOKUP(E81,List!$K$2:$M$447,2,FALSE)","v":"RNQFCUB1X00_TSET"},"RNQFCUB1X00_TSET AT%M4120.0 :REAL; (*风机盘管B1层温度全局设定*)","RNQFCUB1X00_TSET        AT%M4120.0     :REAL; (*风机盘管B1层温度全局设定*)"]
["风机盘管","RNQ","M","01X00","设定温度值","4124.0",null,"验证通过","REAL","风机盘管1层温度全局设定",{"$f":"B82&VLOOKUP(A82,List!$B$3:$D$445,2,FALSE)&D82&\"_\"&VLOOKUP(E82,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU01X00_TSET"},"RNQFCU01X00_TSET AT%M4124.0 :REAL; (*风机盘管1层温度全局设定*)","RNQFCU01X00_TSET        AT%M4124.0     :REAL; (*风机盘管1层温度全局设定*)"]
["风机盘管","RNQ","M","02X00","设定温度值","4128.0",null,"验证通过","REAL","风机盘管2层温度全局设定",{"$f":"B83&VLOOKUP(A83,List!$B$3:$D$445,2,FALSE)&D83&\"_\"&VLOOKUP(E83,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU02X00_TSET"},"RNQFCU02X00_TSET AT%M4128.0 :REAL; (*风机盘管2层温度全局设定*)","RNQFCU02X00_TSET        AT%M4128.0     :REAL; (*风机盘管2层温度全局设定*)"]
["风机盘管","RNQ","M","03X00","设定温度值","4132.0",null,"验证通过","REAL","风机盘管3层温度全局设定",{"$f":"B84&VLOOKUP(A84,List!$B$3:$D$445,2,FALSE)&D84&\"_\"&VLOOKUP(E84,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU03X00_TSET"},"RNQFCU03X00_TSET AT%M4132.0 :REAL; (*风机盘管3层温度全局设定*)","RNQFCU03X00_TSET        AT%M4132.0     :REAL; (*风机盘管3层温度全局设定*)"]
["风机盘管","RNQ","M","04X00","设定温度值","4136.0",null,"验证通过","REAL","风机盘管4层温度全局设定",{"$f":"B85&VLOOKUP(A85,List!$B$3:$D$445,2,FALSE)&D85&\"_\"&VLOOKUP(E85,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU04X00_TSET"},"RNQFCU04X00_TSET AT%M4136.0 :REAL; (*风机盘管4层温度全局设定*)","RNQFCU04X00_TSET        AT%M4136.0     :REAL; (*风机盘管4层温度全局设定*)"]
["风机盘管","RNQ","M","05X00","设定温度值","4140.0",null,"验证通过","REAL","风机盘管5层温度全局设定",{"$f":"B86&VLOOKUP(A86,List!$B$3:$D$445,2,FALSE)&D86&\"_\"&VLOOKUP(E86,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU05X00_TSET"},"RNQFCU05X00_TSET AT%M4140.0 :REAL; (*风机盘管5层温度全局设定*)","RNQFCU05X00_TSET        AT%M4140.0     :REAL; (*风机盘管5层温度全局设定*)"]
["风机盘管","RNQ","M","06X00","设定温度值","4144.0",null,"验证通过","REAL","风机盘管6层温度全局设定",{"$f":"B87&VLOOKUP(A87,List!$B$3:$D$445,2,FALSE)&D87&\"_\"&VLOOKUP(E87,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU06X00_TSET"},"RNQFCU06X00_TSET AT%M4144.0 :REAL; (*风机盘管6层温度全局设定*)","RNQFCU06X00_TSET        AT%M4144.0     :REAL; (*风机盘管6层温度全局设定*)"]
["风机盘管","RNQ","M","07X00","设定温度值","4148.0",null,"验证通过","REAL","风机盘管7层温度全局设定",{"$f":"B88&VLOOKUP(A88,List!$B$3:$D$445,2,FALSE)&D88&\"_\"&VLOOKUP(E88,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU07X00_TSET"},{"$f":"K88&\" \"&\"AT%\"&C88&F88&\" \"&\":\"&I88&\";\"&\" \"&\"(*\"&J88&\"*)\"","v":"RNQFCU07X00_TSET AT%M4148.0 :REAL; (*风机盘管7层温度全局设定*)"},{"$f":"REPLACE(REPLACE(L88,SEARCH(\"AT%\",L88),,REPT(\" \",25-SEARCH(\"AT%\",L88))),SEARCH(\":\",REPLACE(L88,SEARCH(\"AT%\",L88),,REPT(\" \",25-SEARCH(\"AT%\",L88)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L88,SEARCH(\"AT%\",L88),,REPT(\" \",25-SEARCH(\"AT%\",L88))))))","v":"RNQFCU07X00_TSET        AT%M4148.0     :REAL; (*风机盘管7层温度全局设定*)"}]
["风机盘管","RNQ","M","08X00","设定温度值","4152.0",null,"验证通过","REAL","风机盘管8层温度全局设定",{"$f":"B89&VLOOKUP(A89,List!$B$3:$D$445,2,FALSE)&D89&\"_\"&VLOOKUP(E89,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU08X00_TSET"},"RNQFCU08X00_TSET AT%M4152.0 :REAL; (*风机盘管8层温度全局设定*)","RNQFCU08X00_TSET        AT%M4152.0     :REAL; (*风机盘管8层温度全局设定*)"]
["风机盘管","RNQ","M","B3X00","季节模式","4156.0",null,"验证通过","INT","风机盘管B3层季节模式全局设定",{"$f":"B90&VLOOKUP(A90,List!$B$3:$D$445,2,FALSE)&D90&\"_\"&VLOOKUP(E90,List!$K$2:$M$447,2,FALSE)","v":"RNQFCUB3X00_SM"},{"$f":"K90&\" \"&\"AT%\"&C90&F90&\" \"&\":\"&I90&\";\"&\" \"&\"(*\"&J90&\"*)\"","v":"RNQFCUB3X00_SM AT%M4156.0 :INT; (*风机盘管B3层季节模式全局设定*)"},{"$f":"REPLACE(REPLACE(L90,SEARCH(\"AT%\",L90),,REPT(\" \",25-SEARCH(\"AT%\",L90))),SEARCH(\":\",REPLACE(L90,SEARCH(\"AT%\",L90),,REPT(\" \",25-SEARCH(\"AT%\",L90)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L90,SEARCH(\"AT%\",L90),,REPT(\" \",25-SEARCH(\"AT%\",L90))))))","v":"RNQFCUB3X00_SM          AT%M4156.0     :INT; (*风机盘管B3层季节模式全局设定*)"}]
["风机盘管","RNQ","M","B2X00","季节模式","4158.0",null,"验证通过","INT","风机盘管B2层季节模式全局设定",{"$f":"B91&VLOOKUP(A91,List!$B$3:$D$445,2,FALSE)&D91&\"_\"&VLOOKUP(E91,List!$K$2:$M$447,2,FALSE)","v":"RNQFCUB2X00_SM"},"RNQFCUB2X00_SM AT%M4158.0 :INT; (*风机盘管B2层季节模式全局设定*)","RNQFCUB2X00_SM          AT%M4158.0     :INT; (*风机盘管B2层季节模式全局设定*)"]
["风机盘管","RNQ","M","B1X00","季节模式","4160.0",null,"验证通过","INT","风机盘管B1层季节模式全局设定",{"$f":"B92&VLOOKUP(A92,List!$B$3:$D$445,2,FALSE)&D92&\"_\"&VLOOKUP(E92,List!$K$2:$M$447,2,FALSE)","v":"RNQFCUB1X00_SM"},"RNQFCUB1X00_SM AT%M4160.0 :INT; (*风机盘管B1层季节模式全局设定*)","RNQFCUB1X00_SM          AT%M4160.0     :INT; (*风机盘管B1层季节模式全局设定*)"]
["风机盘管","RNQ","M","01X00","季节模式","4162.0",null,"验证通过","INT","风机盘管1层季节模式全局设定",{"$f":"B93&VLOOKUP(A93,List!$B$3:$D$445,2,FALSE)&D93&\"_\"&VLOOKUP(E93,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU01X00_SM"},"RNQFCU01X00_SM AT%M4162.0 :INT; (*风机盘管1层季节模式全局设定*)","RNQFCU01X00_SM          AT%M4162.0     :INT; (*风机盘管1层季节模式全局设定*)"]
["风机盘管","RNQ","M","02X00","季节模式","4164.0",null,"验证通过","INT","风机盘管2层季节模式全局设定",{"$f":"B94&VLOOKUP(A94,List!$B$3:$D$445,2,FALSE)&D94&\"_\"&VLOOKUP(E94,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU02X00_SM"},"RNQFCU02X00_SM AT%M4164.0 :INT; (*风机盘管2层季节模式全局设定*)","RNQFCU02X00_SM          AT%M4164.0     :INT; (*风机盘管2层季节模式全局设定*)"]
["风机盘管","RNQ","M","03X00","季节模式","4166.0",null,"验证通过","INT","风机盘管3层季节模式全局设定",{"$f":"B95&VLOOKUP(A95,List!$B$3:$D$445,2,FALSE)&D95&\"_\"&VLOOKUP(E95,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU03X00_SM"},"RNQFCU03X00_SM AT%M4166.0 :INT; (*风机盘管3层季节模式全局设定*)","RNQFCU03X00_SM          AT%M4166.0     :INT; (*风机盘管3层季节模式全局设定*)"]
["风机盘管","RNQ","M","04X00","季节模式","4168.0",null,"验证通过","INT","风机盘管4层季节模式全局设定",{"$f":"B96&VLOOKUP(A96,List!$B$3:$D$445,2,FALSE)&D96&\"_\"&VLOOKUP(E96,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU04X00_SM"},"RNQFCU04X00_SM AT%M4168.0 :INT; (*风机盘管4层季节模式全局设定*)","RNQFCU04X00_SM          AT%M4168.0     :INT; (*风机盘管4层季节模式全局设定*)"]
["风机盘管","RNQ","M","05X00","季节模式","4170.0",null,"验证通过","INT","风机盘管5层季节模式全局设定",{"$f":"B97&VLOOKUP(A97,List!$B$3:$D$445,2,FALSE)&D97&\"_\"&VLOOKUP(E97,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU05X00_SM"},"RNQFCU05X00_SM AT%M4170.0 :INT; (*风机盘管5层季节模式全局设定*)","RNQFCU05X00_SM          AT%M4170.0     :INT; (*风机盘管5层季节模式全局设定*)"]
["风机盘管","RNQ","M","06X00","季节模式","4172.0",null,"验证通过","INT","风机盘管6层季节模式全局设定",{"$f":"B98&VLOOKUP(A98,List!$B$3:$D$445,2,FALSE)&D98&\"_\"&VLOOKUP(E98,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU06X00_SM"},"RNQFCU06X00_SM AT%M4172.0 :INT; (*风机盘管6层季节模式全局设定*)","RNQFCU06X00_SM          AT%M4172.0     :INT; (*风机盘管6层季节模式全局设定*)"]
["风机盘管","RNQ","M","07X00","季节模式","4174.0",null,"验证通过","INT","风机盘管7层季节模式全局设定",{"$f":"B99&VLOOKUP(A99,List!$B$3:$D$445,2,FALSE)&D99&\"_\"&VLOOKUP(E99,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU07X00_SM"},"RNQFCU07X00_SM AT%M4174.0 :INT; (*风机盘管7层季节模式全局设定*)","RNQFCU07X00_SM          AT%M4174.0     :INT; (*风机盘管7层季节模式全局设定*)"]
["风机盘管","RNQ","M","08X00","季节模式","4176.0",null,"验证通过","INT","风机盘管8层季节模式全局设定",{"$f":"B100&VLOOKUP(A100,List!$B$3:$D$445,2,FALSE)&D100&\"_\"&VLOOKUP(E100,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU08X00_SM"},"RNQFCU08X00_SM AT%M4176.0 :INT; (*风机盘管8层季节模式全局设定*)","RNQFCU08X00_SM          AT%M4176.0     :INT; (*风机盘管8层季节模式全局设定*)"]
["风机盘管","RNQ","M","B3X00","程序控制","4178.0",null,"验证通过","BOOL","风机盘管B3层启停控制",{"$f":"B101&VLOOKUP(A101,List!$B$3:$D$445,2,FALSE)&D101&\"_\"&VLOOKUP(E101,List!$K$2:$M$447,2,FALSE)","v":"RNQFCUB3X00_PC"},"RNQFCUB3X00_PC AT%M4178.0 :BOOL; (*风机盘管B3层启停控制*)","RNQFCUB3X00_PC          AT%M4178.0     :BOOL; (*风机盘管B3层启停控制*)"]
["风机盘管","RNQ","M","B2X00","程序控制","4180.0",null,"验证通过","BOOL","风机盘管B2层启停控制",{"$f":"B102&VLOOKUP(A102,List!$B$3:$D$445,2,FALSE)&D102&\"_\"&VLOOKUP(E102,List!$K$2:$M$447,2,FALSE)","v":"RNQFCUB2X00_PC"},"RNQFCUB2X00_PC AT%M4180.0 :BOOL; (*风机盘管B2层启停控制*)","RNQFCUB2X00_PC          AT%M4180.0     :BOOL; (*风机盘管B2层启停控制*)"]
["风机盘管","RNQ","M","B1X00","程序控制","4182.0",null,"验证通过","BOOL","风机盘管B1层启停控制",{"$f":"B103&VLOOKUP(A103,List!$B$3:$D$445,2,FALSE)&D103&\"_\"&VLOOKUP(E103,List!$K$2:$M$447,2,FALSE)","v":"RNQFCUB1X00_PC"},"RNQFCUB1X00_PC AT%M4182.0 :BOOL; (*风机盘管B1层启停控制*)","RNQFCUB1X00_PC          AT%M4182.0     :BOOL; (*风机盘管B1层启停控制*)"]
["风机盘管","RNQ","M","01X00","程序控制",{"$f":"IF(OR(I103=\"REAL\",I103=\"DWORD\",I103=\"DINT\"),(IF(OR(I104=\"REAL\",I104=\"DWORD\",I104=\"DINT\"),F103+4+MOD(F103,4),F103+4)),(IF(OR(I104=\"REAL\",I104=\"DWORD\",I104=\"DINT\"),F103+4+MOD(F103,4),F103+2)))&\".0\"","v":"4184.0"},null,"验证通过","BOOL","风机盘管1层启停控制",{"$f":"B104&VLOOKUP(A104,List!$B$3:$D$445,2,FALSE)&D104&\"_\"&VLOOKUP(E104,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU01X00_PC"},"RNQFCU01X00_PC AT%M4184.0 :BOOL; (*风机盘管1层启停控制*)","RNQFCU01X00_PC          AT%M4184.0     :BOOL; (*风机盘管1层启停控制*)"]
["风机盘管","RNQ","M","02X00","程序控制","4186.0",null,"验证通过","BOOL","风机盘管2层启停控制",{"$f":"B105&VLOOKUP(A105,List!$B$3:$D$445,2,FALSE)&D105&\"_\"&VLOOKUP(E105,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU02X00_PC"},"RNQFCU02X00_PC AT%M4186.0 :BOOL; (*风机盘管2层启停控制*)","RNQFCU02X00_PC          AT%M4186.0     :BOOL; (*风机盘管2层启停控制*)"]
["风机盘管","RNQ","M","03X00","程序控制","4188.0",null,"验证通过","BOOL","风机盘管3层启停控制",{"$f":"B106&VLOOKUP(A106,List!$B$3:$D$445,2,FALSE)&D106&\"_\"&VLOOKUP(E106,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU03X00_PC"},"RNQFCU03X00_PC AT%M4188.0 :BOOL; (*风机盘管3层启停控制*)","RNQFCU03X00_PC          AT%M4188.0     :BOOL; (*风机盘管3层启停控制*)"]
["风机盘管","RNQ","M","04X00","程序控制","4190.0",null,"验证通过","BOOL","风机盘管4层启停控制",{"$f":"B107&VLOOKUP(A107,List!$B$3:$D$445,2,FALSE)&D107&\"_\"&VLOOKUP(E107,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU04X00_PC"},"RNQFCU04X00_PC AT%M4190.0 :BOOL; (*风机盘管4层启停控制*)","RNQFCU04X00_PC          AT%M4190.0     :BOOL; (*风机盘管4层启停控制*)"]
["风机盘管","RNQ","M","05X00","程序控制","4192.0",null,"验证通过","BOOL","风机盘管5层启停控制",{"$f":"B108&VLOOKUP(A108,List!$B$3:$D$445,2,FALSE)&D108&\"_\"&VLOOKUP(E108,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU05X00_PC"},"RNQFCU05X00_PC AT%M4192.0 :BOOL; (*风机盘管5层启停控制*)","RNQFCU05X00_PC          AT%M4192.0     :BOOL; (*风机盘管5层启停控制*)"]
["风机盘管","RNQ","M","06X00","程序控制","4194.0",null,"验证通过","BOOL","风机盘管6层启停控制",{"$f":"B109&VLOOKUP(A109,List!$B$3:$D$445,2,FALSE)&D109&\"_\"&VLOOKUP(E109,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU06X00_PC"},"RNQFCU06X00_PC AT%M4194.0 :BOOL; (*风机盘管6层启停控制*)","RNQFCU06X00_PC          AT%M4194.0     :BOOL; (*风机盘管6层启停控制*)"]
["风机盘管","RNQ","M","07X00","程序控制","4196.0",null,{"$f":"IF((IF(OR(I110=\"INT\",I110=\"WORD\",I110=\"BOOL\"),MOD(F110,2),MOD(F110,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","风机盘管7层启停控制",{"$f":"B110&VLOOKUP(A110,List!$B$3:$D$445,2,FALSE)&D110&\"_\"&VLOOKUP(E110,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU07X00_PC"},{"$f":"K110&\" \"&\"AT%\"&C110&F110&\" \"&\":\"&I110&\";\"&\" \"&\"(*\"&J110&\"*)\"","v":"RNQFCU07X00_PC AT%M4196.0 :BOOL; (*风机盘管7层启停控制*)"},{"$f":"REPLACE(REPLACE(L110,SEARCH(\"AT%\",L110),,REPT(\" \",25-SEARCH(\"AT%\",L110))),SEARCH(\":\",REPLACE(L110,SEARCH(\"AT%\",L110),,REPT(\" \",25-SEARCH(\"AT%\",L110)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L110,SEARCH(\"AT%\",L110),,REPT(\" \",25-SEARCH(\"AT%\",L110))))))","v":"RNQFCU07X00_PC          AT%M4196.0     :BOOL; (*风机盘管7层启停控制*)"}]
["风机盘管","RNQ","M","08X00","程序控制",{"$f":"IF(OR(I110=\"REAL\",I110=\"DWORD\",I110=\"DINT\"),(IF(OR(I111=\"REAL\",I111=\"DWORD\",I111=\"DINT\"),F110+4+MOD(F110,4),F110+4)),(IF(OR(I111=\"REAL\",I111=\"DWORD\",I111=\"DINT\"),F110+4+MOD(F110,4),F110+2)))&\".0\"","v":"4198.0"},null,"验证通过","BOOL","风机盘管8层启停控制",{"$f":"B111&VLOOKUP(A111,List!$B$3:$D$445,2,FALSE)&D111&\"_\"&VLOOKUP(E111,List!$K$2:$M$447,2,FALSE)","v":"RNQFCU08X00_PC"},"RNQFCU08X00_PC AT%M4198.0 :BOOL; (*风机盘管8层启停控制*)","RNQFCU08X00_PC          AT%M4198.0     :BOOL; (*风机盘管8层启停控制*)"]
["照明控制箱","RNQ","M","B3X0A","启停控制","4200.0",null,"验证通过","BOOL","基础照明A B3层全局启停控制",{"$f":"B112&VLOOKUP(A112,List!$B$3:$D$445,2,FALSE)&D112&\"_\"&VLOOKUP(E112,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB3X0A_C"},"RNQLCBB3X0A_C AT%M4200.0 :BOOL; (*基础照明A B3层全局启停控制*)","RNQLCBB3X0A_C           AT%M4200.0     :BOOL; (*基础照明A B3层全局启停控制*)"]
["照明控制箱","RNQ","M","B2X0A","启停控制",{"$f":"IF(OR(I112=\"REAL\",I112=\"DWORD\",I112=\"DINT\"),(IF(OR(I113=\"REAL\",I113=\"DWORD\",I113=\"DINT\"),F112+4+MOD(F112,4),F112+4)),(IF(OR(I113=\"REAL\",I113=\"DWORD\",I113=\"DINT\"),F112+4+MOD(F112,4),F112+2)))&\".0\"","v":"4202.0"},null,"验证通过","BOOL","基础照明A B2层全局启停控制",{"$f":"B113&VLOOKUP(A113,List!$B$3:$D$445,2,FALSE)&D113&\"_\"&VLOOKUP(E113,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB2X0A_C"},"RNQLCBB2X0A_C AT%M4202.0 :BOOL; (*基础照明A B2层全局启停控制*)","RNQLCBB2X0A_C           AT%M4202.0     :BOOL; (*基础照明A B2层全局启停控制*)"]
["照明控制箱","RNQ","M","B1X0A","启停控制","4204.0",null,"验证通过","BOOL","基础照明A B1层全局启停控制",{"$f":"B114&VLOOKUP(A114,List!$B$3:$D$445,2,FALSE)&D114&\"_\"&VLOOKUP(E114,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB1X0A_C"},"RNQLCBB1X0A_C AT%M4204.0 :BOOL; (*基础照明A B1层全局启停控制*)","RNQLCBB1X0A_C           AT%M4204.0     :BOOL; (*基础照明A B1层全局启停控制*)"]
["照明控制箱","RNQ","M","01X0A","启停控制","4206.0",null,"验证通过","BOOL","基础照明A 1层全局启停控制",{"$f":"B115&VLOOKUP(A115,List!$B$3:$D$445,2,FALSE)&D115&\"_\"&VLOOKUP(E115,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB01X0A_C"},"RNQLCB01X0A_C AT%M4206.0 :BOOL; (*基础照明A 1层全局启停控制*)","RNQLCB01X0A_C           AT%M4206.0     :BOOL; (*基础照明A 1层全局启停控制*)"]
["照明控制箱","RNQ","M","02X0A","启停控制","4208.0",null,"验证通过","BOOL","基础照明A 2层全局启停控制",{"$f":"B116&VLOOKUP(A116,List!$B$3:$D$445,2,FALSE)&D116&\"_\"&VLOOKUP(E116,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB02X0A_C"},"RNQLCB02X0A_C AT%M4208.0 :BOOL; (*基础照明A 2层全局启停控制*)","RNQLCB02X0A_C           AT%M4208.0     :BOOL; (*基础照明A 2层全局启停控制*)"]
["照明控制箱","RNQ","M","03X0A","启停控制","4210.0",null,"验证通过","BOOL","基础照明A 3层全局启停控制",{"$f":"B117&VLOOKUP(A117,List!$B$3:$D$445,2,FALSE)&D117&\"_\"&VLOOKUP(E117,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB03X0A_C"},"RNQLCB03X0A_C AT%M4210.0 :BOOL; (*基础照明A 3层全局启停控制*)","RNQLCB03X0A_C           AT%M4210.0     :BOOL; (*基础照明A 3层全局启停控制*)"]
["照明控制箱","RNQ","M","04X0A","启停控制","4212.0",null,"验证通过","BOOL","基础照明A 4层全局启停控制",{"$f":"B118&VLOOKUP(A118,List!$B$3:$D$445,2,FALSE)&D118&\"_\"&VLOOKUP(E118,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB04X0A_C"},{"$f":"K118&\" \"&\"AT%\"&C118&F118&\" \"&\":\"&I118&\";\"&\" \"&\"(*\"&J118&\"*)\"","v":"RNQLCB04X0A_C AT%M4212.0 :BOOL; (*基础照明A 4层全局启停控制*)"},"RNQLCB04X0A_C           AT%M4212.0     :BOOL; (*基础照明A 4层全局启停控制*)"]
["照明控制箱","RNQ","M","05X0A","启停控制","4214.0",null,"验证通过","BOOL","基础照明A 5层全局启停控制",{"$f":"B119&VLOOKUP(A119,List!$B$3:$D$445,2,FALSE)&D119&\"_\"&VLOOKUP(E119,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB05X0A_C"},"RNQLCB05X0A_C AT%M4214.0 :BOOL; (*基础照明A 5层全局启停控制*)","RNQLCB05X0A_C           AT%M4214.0     :BOOL; (*基础照明A 5层全局启停控制*)"]
["照明控制箱","RNQ","M","06X0A","启停控制","4216.0",null,"验证通过","BOOL","基础照明A 6层全局启停控制",{"$f":"B120&VLOOKUP(A120,List!$B$3:$D$445,2,FALSE)&D120&\"_\"&VLOOKUP(E120,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB06X0A_C"},"RNQLCB06X0A_C AT%M4216.0 :BOOL; (*基础照明A 6层全局启停控制*)","RNQLCB06X0A_C           AT%M4216.0     :BOOL; (*基础照明A 6层全局启停控制*)"]
["照明控制箱","RNQ","M","07X0A","启停控制","4218.0",null,{"$f":"IF((IF(OR(I121=\"INT\",I121=\"WORD\",I121=\"BOOL\"),MOD(F121,2),MOD(F121,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","基础照明A 7层全局启停控制",{"$f":"B121&VLOOKUP(A121,List!$B$3:$D$445,2,FALSE)&D121&\"_\"&VLOOKUP(E121,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB07X0A_C"},{"$f":"K121&\" \"&\"AT%\"&C121&F121&\" \"&\":\"&I121&\";\"&\" \"&\"(*\"&J121&\"*)\"","v":"RNQLCB07X0A_C AT%M4218.0 :BOOL; (*基础照明A 7层全局启停控制*)"},{"$f":"REPLACE(REPLACE(L121,SEARCH(\"AT%\",L121),,REPT(\" \",25-SEARCH(\"AT%\",L121))),SEARCH(\":\",REPLACE(L121,SEARCH(\"AT%\",L121),,REPT(\" \",25-SEARCH(\"AT%\",L121)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L121,SEARCH(\"AT%\",L121),,REPT(\" \",25-SEARCH(\"AT%\",L121))))))","v":"RNQLCB07X0A_C           AT%M4218.0     :BOOL; (*基础照明A 7层全局启停控制*)"}]
["照明控制箱","RNQ","M","08X0A","启停控制","4220.0",null,"验证通过","BOOL","基础照明A 8层全局启停控制",{"$f":"B122&VLOOKUP(A122,List!$B$3:$D$445,2,FALSE)&D122&\"_\"&VLOOKUP(E122,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB08X0A_C"},"RNQLCB08X0A_C AT%M4220.0 :BOOL; (*基础照明A 8层全局启停控制*)","RNQLCB08X0A_C           AT%M4220.0     :BOOL; (*基础照明A 8层全局启停控制*)"]
["照明控制箱","RNQ","M","B3X0B","启停控制","4222.0",null,"验证通过","BOOL","基础照明B B3层全局启停控制",{"$f":"B123&VLOOKUP(A123,List!$B$3:$D$445,2,FALSE)&D123&\"_\"&VLOOKUP(E123,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB3X0B_C"},"RNQLCBB3X0B_C AT%M4222.0 :BOOL; (*基础照明B B3层全局启停控制*)","RNQLCBB3X0B_C           AT%M4222.0     :BOOL; (*基础照明B B3层全局启停控制*)"]
["照明控制箱","RNQ","M","B2X0B","启停控制","4224.0",null,"验证通过","BOOL","基础照明B B2层全局启停控制",{"$f":"B124&VLOOKUP(A124,List!$B$3:$D$445,2,FALSE)&D124&\"_\"&VLOOKUP(E124,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB2X0B_C"},"RNQLCBB2X0B_C AT%M4224.0 :BOOL; (*基础照明B B2层全局启停控制*)","RNQLCBB2X0B_C           AT%M4224.0     :BOOL; (*基础照明B B2层全局启停控制*)"]
["照明控制箱","RNQ","M","B1X0B","启停控制","4226.0",null,"验证通过","BOOL","基础照明B B1层全局启停控制",{"$f":"B125&VLOOKUP(A125,List!$B$3:$D$445,2,FALSE)&D125&\"_\"&VLOOKUP(E125,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB1X0B_C"},"RNQLCBB1X0B_C AT%M4226.0 :BOOL; (*基础照明B B1层全局启停控制*)","RNQLCBB1X0B_C           AT%M4226.0     :BOOL; (*基础照明B B1层全局启停控制*)"]
["照明控制箱","RNQ","M","01X0B","启停控制","4228.0",null,"验证通过","BOOL","基础照明B 1层全局启停控制",{"$f":"B126&VLOOKUP(A126,List!$B$3:$D$445,2,FALSE)&D126&\"_\"&VLOOKUP(E126,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB01X0B_C"},"RNQLCB01X0B_C AT%M4228.0 :BOOL; (*基础照明B 1层全局启停控制*)","RNQLCB01X0B_C           AT%M4228.0     :BOOL; (*基础照明B 1层全局启停控制*)"]
["照明控制箱","RNQ","M","02X0B","启停控制","4230.0",null,"验证通过","BOOL","基础照明B 2层全局启停控制",{"$f":"B127&VLOOKUP(A127,List!$B$3:$D$445,2,FALSE)&D127&\"_\"&VLOOKUP(E127,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB02X0B_C"},"RNQLCB02X0B_C AT%M4230.0 :BOOL; (*基础照明B 2层全局启停控制*)","RNQLCB02X0B_C           AT%M4230.0     :BOOL; (*基础照明B 2层全局启停控制*)"]
["照明控制箱","RNQ","M","03X0B","启停控制","4232.0",null,"验证通过","BOOL","基础照明B 3层全局启停控制",{"$f":"B128&VLOOKUP(A128,List!$B$3:$D$445,2,FALSE)&D128&\"_\"&VLOOKUP(E128,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB03X0B_C"},"RNQLCB03X0B_C AT%M4232.0 :BOOL; (*基础照明B 3层全局启停控制*)","RNQLCB03X0B_C           AT%M4232.0     :BOOL; (*基础照明B 3层全局启停控制*)"]
["照明控制箱","RNQ","M","04X0B","启停控制","4234.0",null,"验证通过","BOOL","基础照明B 4层全局启停控制",{"$f":"B129&VLOOKUP(A129,List!$B$3:$D$445,2,FALSE)&D129&\"_\"&VLOOKUP(E129,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB04X0B_C"},"RNQLCB04X0B_C AT%M4234.0 :BOOL; (*基础照明B 4层全局启停控制*)","RNQLCB04X0B_C           AT%M4234.0     :BOOL; (*基础照明B 4层全局启停控制*)"]
["照明控制箱","RNQ","M","05X0B","启停控制","4236.0",null,"验证通过","BOOL","基础照明B 5层全局启停控制",{"$f":"B130&VLOOKUP(A130,List!$B$3:$D$445,2,FALSE)&D130&\"_\"&VLOOKUP(E130,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB05X0B_C"},"RNQLCB05X0B_C AT%M4236.0 :BOOL; (*基础照明B 5层全局启停控制*)","RNQLCB05X0B_C           AT%M4236.0     :BOOL; (*基础照明B 5层全局启停控制*)"]
["照明控制箱","RNQ","M","06X0B","启停控制","4238.0",null,"验证通过","BOOL","基础照明B 6层全局启停控制",{"$f":"B131&VLOOKUP(A131,List!$B$3:$D$445,2,FALSE)&D131&\"_\"&VLOOKUP(E131,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB06X0B_C"},"RNQLCB06X0B_C AT%M4238.0 :BOOL; (*基础照明B 6层全局启停控制*)","RNQLCB06X0B_C           AT%M4238.0     :BOOL; (*基础照明B 6层全局启停控制*)"]
["照明控制箱","RNQ","M","07X0B","启停控制","4240.0",null,{"$f":"IF((IF(OR(I132=\"INT\",I132=\"WORD\",I132=\"BOOL\"),MOD(F132,2),MOD(F132,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","基础照明B 7层全局启停控制",{"$f":"B132&VLOOKUP(A132,List!$B$3:$D$445,2,FALSE)&D132&\"_\"&VLOOKUP(E132,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB07X0B_C"},{"$f":"K132&\" \"&\"AT%\"&C132&F132&\" \"&\":\"&I132&\";\"&\" \"&\"(*\"&J132&\"*)\"","v":"RNQLCB07X0B_C AT%M4240.0 :BOOL; (*基础照明B 7层全局启停控制*)"},{"$f":"REPLACE(REPLACE(L132,SEARCH(\"AT%\",L132),,REPT(\" \",25-SEARCH(\"AT%\",L132))),SEARCH(\":\",REPLACE(L132,SEARCH(\"AT%\",L132),,REPT(\" \",25-SEARCH(\"AT%\",L132)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L132,SEARCH(\"AT%\",L132),,REPT(\" \",25-SEARCH(\"AT%\",L132))))))","v":"RNQLCB07X0B_C           AT%M4240.0     :BOOL; (*基础照明B 7层全局启停控制*)"}]
["照明控制箱","RNQ","M","08X0B","启停控制","4242.0",null,"验证通过","BOOL","基础照明B 8层全局启停控制",{"$f":"B133&VLOOKUP(A133,List!$B$3:$D$445,2,FALSE)&D133&\"_\"&VLOOKUP(E133,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB08X0B_C"},"RNQLCB08X0B_C AT%M4242.0 :BOOL; (*基础照明B 8层全局启停控制*)","RNQLCB08X0B_C           AT%M4242.0     :BOOL; (*基础照明B 8层全局启停控制*)"]
["照明控制箱","RNQ","M","B3X0C","启停控制","4244.0",null,"验证通过","BOOL","灯带 B3层全局启停控制",{"$f":"B134&VLOOKUP(A134,List!$B$3:$D$445,2,FALSE)&D134&\"_\"&VLOOKUP(E134,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB3X0C_C"},"RNQLCBB3X0C_C AT%M4244.0 :BOOL; (*灯带 B3层全局启停控制*)","RNQLCBB3X0C_C           AT%M4244.0     :BOOL; (*灯带 B3层全局启停控制*)"]
["照明控制箱","RNQ","M","B2X0C","启停控制","4246.0",null,"验证通过","BOOL","灯带 B2层全局启停控制",{"$f":"B135&VLOOKUP(A135,List!$B$3:$D$445,2,FALSE)&D135&\"_\"&VLOOKUP(E135,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB2X0C_C"},"RNQLCBB2X0C_C AT%M4246.0 :BOOL; (*灯带 B2层全局启停控制*)","RNQLCBB2X0C_C           AT%M4246.0     :BOOL; (*灯带 B2层全局启停控制*)"]
["照明控制箱","RNQ","M","B1X0C","启停控制","4248.0",null,"验证通过","BOOL","灯带 B1层全局启停控制",{"$f":"B136&VLOOKUP(A136,List!$B$3:$D$445,2,FALSE)&D136&\"_\"&VLOOKUP(E136,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB1X0C_C"},"RNQLCBB1X0C_C AT%M4248.0 :BOOL; (*灯带 B1层全局启停控制*)","RNQLCBB1X0C_C           AT%M4248.0     :BOOL; (*灯带 B1层全局启停控制*)"]
["照明控制箱","RNQ","M","01X0C","启停控制","4250.0",null,"验证通过","BOOL","灯带 1层全局启停控制",{"$f":"B137&VLOOKUP(A137,List!$B$3:$D$445,2,FALSE)&D137&\"_\"&VLOOKUP(E137,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB01X0C_C"},"RNQLCB01X0C_C AT%M4250.0 :BOOL; (*灯带 1层全局启停控制*)","RNQLCB01X0C_C           AT%M4250.0     :BOOL; (*灯带 1层全局启停控制*)"]
["照明控制箱","RNQ","M","02X0C","启停控制","4252.0",null,"验证通过","BOOL","灯带 2层全局启停控制",{"$f":"B138&VLOOKUP(A138,List!$B$3:$D$445,2,FALSE)&D138&\"_\"&VLOOKUP(E138,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB02X0C_C"},"RNQLCB02X0C_C AT%M4252.0 :BOOL; (*灯带 2层全局启停控制*)","RNQLCB02X0C_C           AT%M4252.0     :BOOL; (*灯带 2层全局启停控制*)"]
["照明控制箱","RNQ","M","03X0C","启停控制","4254.0",null,"验证通过","BOOL","灯带 3层全局启停控制",{"$f":"B139&VLOOKUP(A139,List!$B$3:$D$445,2,FALSE)&D139&\"_\"&VLOOKUP(E139,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB03X0C_C"},"RNQLCB03X0C_C AT%M4254.0 :BOOL; (*灯带 3层全局启停控制*)","RNQLCB03X0C_C           AT%M4254.0     :BOOL; (*灯带 3层全局启停控制*)"]
["照明控制箱","RNQ","M","04X0C","启停控制","4256.0",null,"验证通过","BOOL","灯带 4层全局启停控制",{"$f":"B140&VLOOKUP(A140,List!$B$3:$D$445,2,FALSE)&D140&\"_\"&VLOOKUP(E140,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB04X0C_C"},"RNQLCB04X0C_C AT%M4256.0 :BOOL; (*灯带 4层全局启停控制*)","RNQLCB04X0C_C           AT%M4256.0     :BOOL; (*灯带 4层全局启停控制*)"]
["照明控制箱","RNQ","M","05X0C","启停控制","4258.0",null,"验证通过","BOOL","灯带 5层全局启停控制",{"$f":"B141&VLOOKUP(A141,List!$B$3:$D$445,2,FALSE)&D141&\"_\"&VLOOKUP(E141,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB05X0C_C"},"RNQLCB05X0C_C AT%M4258.0 :BOOL; (*灯带 5层全局启停控制*)","RNQLCB05X0C_C           AT%M4258.0     :BOOL; (*灯带 5层全局启停控制*)"]
["照明控制箱","RNQ","M","06X0C","启停控制","4260.0",null,"验证通过","BOOL","灯带 6层全局启停控制",{"$f":"B142&VLOOKUP(A142,List!$B$3:$D$445,2,FALSE)&D142&\"_\"&VLOOKUP(E142,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB06X0C_C"},"RNQLCB06X0C_C AT%M4260.0 :BOOL; (*灯带 6层全局启停控制*)","RNQLCB06X0C_C           AT%M4260.0     :BOOL; (*灯带 6层全局启停控制*)"]
["照明控制箱","RNQ","M","07X0C","启停控制","4262.0",null,{"$f":"IF((IF(OR(I143=\"INT\",I143=\"WORD\",I143=\"BOOL\"),MOD(F143,2),MOD(F143,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","灯带 7层全局启停控制",{"$f":"B143&VLOOKUP(A143,List!$B$3:$D$445,2,FALSE)&D143&\"_\"&VLOOKUP(E143,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB07X0C_C"},{"$f":"K143&\" \"&\"AT%\"&C143&F143&\" \"&\":\"&I143&\";\"&\" \"&\"(*\"&J143&\"*)\"","v":"RNQLCB07X0C_C AT%M4262.0 :BOOL; (*灯带 7层全局启停控制*)"},{"$f":"REPLACE(REPLACE(L143,SEARCH(\"AT%\",L143),,REPT(\" \",25-SEARCH(\"AT%\",L143))),SEARCH(\":\",REPLACE(L143,SEARCH(\"AT%\",L143),,REPT(\" \",25-SEARCH(\"AT%\",L143)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L143,SEARCH(\"AT%\",L143),,REPT(\" \",25-SEARCH(\"AT%\",L143))))))","v":"RNQLCB07X0C_C           AT%M4262.0     :BOOL; (*灯带 7层全局启停控制*)"}]
["照明控制箱","RNQ","M","08X0C","启停控制","4264.0",null,"验证通过","BOOL","灯带 8层全局启停控制",{"$f":"B144&VLOOKUP(A144,List!$B$3:$D$445,2,FALSE)&D144&\"_\"&VLOOKUP(E144,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB08X0C_C"},"RNQLCB08X0C_C AT%M4264.0 :BOOL; (*灯带 8层全局启停控制*)","RNQLCB08X0C_C           AT%M4264.0     :BOOL; (*灯带 8层全局启停控制*)"]
["照明控制箱","RNQ","M","B3X0D","启停控制","4266.0",null,"验证通过","BOOL","广告 B3层全局启停控制",{"$f":"B145&VLOOKUP(A145,List!$B$3:$D$445,2,FALSE)&D145&\"_\"&VLOOKUP(E145,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB3X0D_C"},"RNQLCBB3X0D_C AT%M4266.0 :BOOL; (*广告 B3层全局启停控制*)","RNQLCBB3X0D_C           AT%M4266.0     :BOOL; (*广告 B3层全局启停控制*)"]
["照明控制箱","RNQ","M","B2X0D","启停控制","4268.0",null,"验证通过","BOOL","广告 B2层全局启停控制",{"$f":"B146&VLOOKUP(A146,List!$B$3:$D$445,2,FALSE)&D146&\"_\"&VLOOKUP(E146,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB2X0D_C"},"RNQLCBB2X0D_C AT%M4268.0 :BOOL; (*广告 B2层全局启停控制*)","RNQLCBB2X0D_C           AT%M4268.0     :BOOL; (*广告 B2层全局启停控制*)"]
["照明控制箱","RNQ","M","B1X0D","启停控制","4270.0",null,"验证通过","BOOL","广告 B1层全局启停控制",{"$f":"B147&VLOOKUP(A147,List!$B$3:$D$445,2,FALSE)&D147&\"_\"&VLOOKUP(E147,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB1X0D_C"},"RNQLCBB1X0D_C AT%M4270.0 :BOOL; (*广告 B1层全局启停控制*)","RNQLCBB1X0D_C           AT%M4270.0     :BOOL; (*广告 B1层全局启停控制*)"]
["照明控制箱","RNQ","M","01X0D","启停控制","4272.0",null,"验证通过","BOOL","广告 1层全局启停控制",{"$f":"B148&VLOOKUP(A148,List!$B$3:$D$445,2,FALSE)&D148&\"_\"&VLOOKUP(E148,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB01X0D_C"},"RNQLCB01X0D_C AT%M4272.0 :BOOL; (*广告 1层全局启停控制*)","RNQLCB01X0D_C           AT%M4272.0     :BOOL; (*广告 1层全局启停控制*)"]
["照明控制箱","RNQ","M","02X0D","启停控制","4274.0",null,"验证通过","BOOL","广告 2层全局启停控制",{"$f":"B149&VLOOKUP(A149,List!$B$3:$D$445,2,FALSE)&D149&\"_\"&VLOOKUP(E149,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB02X0D_C"},"RNQLCB02X0D_C AT%M4274.0 :BOOL; (*广告 2层全局启停控制*)","RNQLCB02X0D_C           AT%M4274.0     :BOOL; (*广告 2层全局启停控制*)"]
["照明控制箱","RNQ","M","03X0D","启停控制","4276.0",null,"验证通过","BOOL","广告 3层全局启停控制",{"$f":"B150&VLOOKUP(A150,List!$B$3:$D$445,2,FALSE)&D150&\"_\"&VLOOKUP(E150,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB03X0D_C"},"RNQLCB03X0D_C AT%M4276.0 :BOOL; (*广告 3层全局启停控制*)","RNQLCB03X0D_C           AT%M4276.0     :BOOL; (*广告 3层全局启停控制*)"]
["照明控制箱","RNQ","M","04X0D","启停控制","4278.0",null,"验证通过","BOOL","广告 4层全局启停控制",{"$f":"B151&VLOOKUP(A151,List!$B$3:$D$445,2,FALSE)&D151&\"_\"&VLOOKUP(E151,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB04X0D_C"},"RNQLCB04X0D_C AT%M4278.0 :BOOL; (*广告 4层全局启停控制*)","RNQLCB04X0D_C           AT%M4278.0     :BOOL; (*广告 4层全局启停控制*)"]
["照明控制箱","RNQ","M","05X0D","启停控制","4280.0",null,"验证通过","BOOL","广告 5层全局启停控制",{"$f":"B152&VLOOKUP(A152,List!$B$3:$D$445,2,FALSE)&D152&\"_\"&VLOOKUP(E152,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB05X0D_C"},"RNQLCB05X0D_C AT%M4280.0 :BOOL; (*广告 5层全局启停控制*)","RNQLCB05X0D_C           AT%M4280.0     :BOOL; (*广告 5层全局启停控制*)"]
["照明控制箱","RNQ","M","06X0D","启停控制","4282.0",null,"验证通过","BOOL","广告 6层全局启停控制",{"$f":"B153&VLOOKUP(A153,List!$B$3:$D$445,2,FALSE)&D153&\"_\"&VLOOKUP(E153,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB06X0D_C"},"RNQLCB06X0D_C AT%M4282.0 :BOOL; (*广告 6层全局启停控制*)","RNQLCB06X0D_C           AT%M4282.0     :BOOL; (*广告 6层全局启停控制*)"]
["照明控制箱","RNQ","M","07X0D","启停控制","4284.0",null,{"$f":"IF((IF(OR(I154=\"INT\",I154=\"WORD\",I154=\"BOOL\"),MOD(F154,2),MOD(F154,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","广告 7层全局启停控制",{"$f":"B154&VLOOKUP(A154,List!$B$3:$D$445,2,FALSE)&D154&\"_\"&VLOOKUP(E154,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB07X0D_C"},{"$f":"K154&\" \"&\"AT%\"&C154&F154&\" \"&\":\"&I154&\";\"&\" \"&\"(*\"&J154&\"*)\"","v":"RNQLCB07X0D_C AT%M4284.0 :BOOL; (*广告 7层全局启停控制*)"},{"$f":"REPLACE(REPLACE(L154,SEARCH(\"AT%\",L154),,REPT(\" \",25-SEARCH(\"AT%\",L154))),SEARCH(\":\",REPLACE(L154,SEARCH(\"AT%\",L154),,REPT(\" \",25-SEARCH(\"AT%\",L154)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L154,SEARCH(\"AT%\",L154),,REPT(\" \",25-SEARCH(\"AT%\",L154))))))","v":"RNQLCB07X0D_C           AT%M4284.0     :BOOL; (*广告 7层全局启停控制*)"}]
["照明控制箱","RNQ","M","08X0D","启停控制","4286.0",null,"验证通过","BOOL","广告 8层全局启停控制",{"$f":"B155&VLOOKUP(A155,List!$B$3:$D$445,2,FALSE)&D155&\"_\"&VLOOKUP(E155,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB08X0D_C"},"RNQLCB08X0D_C AT%M4286.0 :BOOL; (*广告 8层全局启停控制*)","RNQLCB08X0D_C           AT%M4286.0     :BOOL; (*广告 8层全局启停控制*)"]
["照明控制箱","RNQ","M","B3X0E","启停控制","4288.0",null,"验证通过","BOOL","标识 B3层全局启停控制",{"$f":"B156&VLOOKUP(A156,List!$B$3:$D$445,2,FALSE)&D156&\"_\"&VLOOKUP(E156,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB3X0E_C"},"RNQLCBB3X0E_C AT%M4288.0 :BOOL; (*标识 B3层全局启停控制*)","RNQLCBB3X0E_C           AT%M4288.0     :BOOL; (*标识 B3层全局启停控制*)"]
["照明控制箱","RNQ","M","B2X0E","启停控制","4290.0",null,"验证通过","BOOL","标识 B2层全局启停控制",{"$f":"B157&VLOOKUP(A157,List!$B$3:$D$445,2,FALSE)&D157&\"_\"&VLOOKUP(E157,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB2X0E_C"},"RNQLCBB2X0E_C AT%M4290.0 :BOOL; (*标识 B2层全局启停控制*)","RNQLCBB2X0E_C           AT%M4290.0     :BOOL; (*标识 B2层全局启停控制*)"]
["照明控制箱","RNQ","M","B1X0E","启停控制","4292.0",null,"验证通过","BOOL","标识 B1层全局启停控制",{"$f":"B158&VLOOKUP(A158,List!$B$3:$D$445,2,FALSE)&D158&\"_\"&VLOOKUP(E158,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB1X0E_C"},"RNQLCBB1X0E_C AT%M4292.0 :BOOL; (*标识 B1层全局启停控制*)","RNQLCBB1X0E_C           AT%M4292.0     :BOOL; (*标识 B1层全局启停控制*)"]
["照明控制箱","RNQ","M","01X0E","启停控制","4294.0",null,"验证通过","BOOL","标识 1层全局启停控制",{"$f":"B159&VLOOKUP(A159,List!$B$3:$D$445,2,FALSE)&D159&\"_\"&VLOOKUP(E159,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB01X0E_C"},"RNQLCB01X0E_C AT%M4294.0 :BOOL; (*标识 1层全局启停控制*)","RNQLCB01X0E_C           AT%M4294.0     :BOOL; (*标识 1层全局启停控制*)"]
["照明控制箱","RNQ","M","02X0E","启停控制","4296.0",null,"验证通过","BOOL","标识 2层全局启停控制",{"$f":"B160&VLOOKUP(A160,List!$B$3:$D$445,2,FALSE)&D160&\"_\"&VLOOKUP(E160,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB02X0E_C"},"RNQLCB02X0E_C AT%M4296.0 :BOOL; (*标识 2层全局启停控制*)","RNQLCB02X0E_C           AT%M4296.0     :BOOL; (*标识 2层全局启停控制*)"]
["照明控制箱","RNQ","M","03X0E","启停控制","4298.0",null,{"$f":"IF((IF(OR(I161=\"INT\",I161=\"WORD\",I161=\"BOOL\"),MOD(F161,2),MOD(F161,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","标识 3层全局启停控制",{"$f":"B161&VLOOKUP(A161,List!$B$3:$D$445,2,FALSE)&D161&\"_\"&VLOOKUP(E161,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB03X0E_C"},"RNQLCB03X0E_C AT%M4298.0 :BOOL; (*标识 3层全局启停控制*)","RNQLCB03X0E_C           AT%M4298.0     :BOOL; (*标识 3层全局启停控制*)"]
["照明控制箱","RNQ","M","04X0E","启停控制","4300.0",null,"验证通过","BOOL","标识 4层全局启停控制",{"$f":"B162&VLOOKUP(A162,List!$B$3:$D$445,2,FALSE)&D162&\"_\"&VLOOKUP(E162,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB04X0E_C"},"RNQLCB04X0E_C AT%M4300.0 :BOOL; (*标识 4层全局启停控制*)","RNQLCB04X0E_C           AT%M4300.0     :BOOL; (*标识 4层全局启停控制*)"]
["照明控制箱","RNQ","M","05X0E","启停控制","4302.0",null,"验证通过","BOOL","标识 5层全局启停控制",{"$f":"B163&VLOOKUP(A163,List!$B$3:$D$445,2,FALSE)&D163&\"_\"&VLOOKUP(E163,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB05X0E_C"},"RNQLCB05X0E_C AT%M4302.0 :BOOL; (*标识 5层全局启停控制*)","RNQLCB05X0E_C           AT%M4302.0     :BOOL; (*标识 5层全局启停控制*)"]
["照明控制箱","RNQ","M","06X0E","启停控制","4304.0",null,"验证通过","BOOL","标识 6层全局启停控制",{"$f":"B164&VLOOKUP(A164,List!$B$3:$D$445,2,FALSE)&D164&\"_\"&VLOOKUP(E164,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB06X0E_C"},"RNQLCB06X0E_C AT%M4304.0 :BOOL; (*标识 6层全局启停控制*)",{"$f":"REPLACE(REPLACE(L164,SEARCH(\"AT%\",L164),,REPT(\" \",25-SEARCH(\"AT%\",L164))),SEARCH(\":\",REPLACE(L164,SEARCH(\"AT%\",L164),,REPT(\" \",25-SEARCH(\"AT%\",L164)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L164,SEARCH(\"AT%\",L164),,REPT(\" \",25-SEARCH(\"AT%\",L164))))))","v":"RNQLCB06X0E_C           AT%M4304.0     :BOOL; (*标识 6层全局启停控制*)"}]
["照明控制箱","RNQ","M","07X0E","启停控制","4306.0",null,"验证通过","BOOL","标识 7层全局启停控制",{"$f":"B165&VLOOKUP(A165,List!$B$3:$D$445,2,FALSE)&D165&\"_\"&VLOOKUP(E165,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB07X0E_C"},{"$f":"K165&\" \"&\"AT%\"&C165&F165&\" \"&\":\"&I165&\";\"&\" \"&\"(*\"&J165&\"*)\"","v":"RNQLCB07X0E_C AT%M4306.0 :BOOL; (*标识 7层全局启停控制*)"},"RNQLCB07X0E_C           AT%M4306.0     :BOOL; (*标识 7层全局启停控制*)"]
["照明控制箱","RNQ","M","08X0E","启停控制","4308.0",null,"验证通过","BOOL","标识 8层全局启停控制",{"$f":"B166&VLOOKUP(A166,List!$B$3:$D$445,2,FALSE)&D166&\"_\"&VLOOKUP(E166,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB08X0E_C"},"RNQLCB08X0E_C AT%M4308.0 :BOOL; (*标识 8层全局启停控制*)",{"$f":"REPLACE(REPLACE(L166,SEARCH(\"AT%\",L166),,REPT(\" \",25-SEARCH(\"AT%\",L166))),SEARCH(\":\",REPLACE(L166,SEARCH(\"AT%\",L166),,REPT(\" \",25-SEARCH(\"AT%\",L166)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L166,SEARCH(\"AT%\",L166),,REPT(\" \",25-SEARCH(\"AT%\",L166))))))","v":"RNQLCB08X0E_C           AT%M4308.0     :BOOL; (*标识 8层全局启停控制*)"}]
["照明控制箱","RNQ","M","B3X0F","启停控制","4310.0",null,"验证通过","BOOL","备用 B3层全局启停控制",{"$f":"B167&VLOOKUP(A167,List!$B$3:$D$445,2,FALSE)&D167&\"_\"&VLOOKUP(E167,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB3X0F_C"},"RNQLCBB3X0F_C AT%M4310.0 :BOOL; (*备用 B3层全局启停控制*)","RNQLCBB3X0F_C           AT%M4310.0     :BOOL; (*备用 B3层全局启停控制*)"]
["照明控制箱","RNQ","M","B2X0F","启停控制","4312.0",null,"验证通过","BOOL","备用 B2层全局启停控制",{"$f":"B168&VLOOKUP(A168,List!$B$3:$D$445,2,FALSE)&D168&\"_\"&VLOOKUP(E168,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB2X0F_C"},"RNQLCBB2X0F_C AT%M4312.0 :BOOL; (*备用 B2层全局启停控制*)","RNQLCBB2X0F_C           AT%M4312.0     :BOOL; (*备用 B2层全局启停控制*)"]
["照明控制箱","RNQ","M","B1X0F","启停控制","4314.0",null,"验证通过","BOOL","备用 B1层全局启停控制",{"$f":"B169&VLOOKUP(A169,List!$B$3:$D$445,2,FALSE)&D169&\"_\"&VLOOKUP(E169,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB1X0F_C"},"RNQLCBB1X0F_C AT%M4314.0 :BOOL; (*备用 B1层全局启停控制*)","RNQLCBB1X0F_C           AT%M4314.0     :BOOL; (*备用 B1层全局启停控制*)"]
["照明控制箱","RNQ","M","01X0F","启停控制","4316.0",null,"验证通过","BOOL","备用 1层全局启停控制",{"$f":"B170&VLOOKUP(A170,List!$B$3:$D$445,2,FALSE)&D170&\"_\"&VLOOKUP(E170,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB01X0F_C"},"RNQLCB01X0F_C AT%M4316.0 :BOOL; (*备用 1层全局启停控制*)","RNQLCB01X0F_C           AT%M4316.0     :BOOL; (*备用 1层全局启停控制*)"]
["照明控制箱","RNQ","M","02X0F","启停控制","4318.0",null,"验证通过","BOOL","备用 2层全局启停控制",{"$f":"B171&VLOOKUP(A171,List!$B$3:$D$445,2,FALSE)&D171&\"_\"&VLOOKUP(E171,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB02X0F_C"},"RNQLCB02X0F_C AT%M4318.0 :BOOL; (*备用 2层全局启停控制*)","RNQLCB02X0F_C           AT%M4318.0     :BOOL; (*备用 2层全局启停控制*)"]
["照明控制箱","RNQ","M","03X0F","启停控制","4320.0",null,"验证通过","BOOL","备用 3层全局启停控制",{"$f":"B172&VLOOKUP(A172,List!$B$3:$D$445,2,FALSE)&D172&\"_\"&VLOOKUP(E172,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB03X0F_C"},"RNQLCB03X0F_C AT%M4320.0 :BOOL; (*备用 3层全局启停控制*)","RNQLCB03X0F_C           AT%M4320.0     :BOOL; (*备用 3层全局启停控制*)"]
["照明控制箱","RNQ","M","04X0F","启停控制","4322.0",null,"验证通过","BOOL","备用 4层全局启停控制",{"$f":"B173&VLOOKUP(A173,List!$B$3:$D$445,2,FALSE)&D173&\"_\"&VLOOKUP(E173,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB04X0F_C"},"RNQLCB04X0F_C AT%M4322.0 :BOOL; (*备用 4层全局启停控制*)","RNQLCB04X0F_C           AT%M4322.0     :BOOL; (*备用 4层全局启停控制*)"]
["照明控制箱","RNQ","M","05X0F","启停控制","4324.0",null,"验证通过","BOOL","备用 5层全局启停控制",{"$f":"B174&VLOOKUP(A174,List!$B$3:$D$445,2,FALSE)&D174&\"_\"&VLOOKUP(E174,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB05X0F_C"},"RNQLCB05X0F_C AT%M4324.0 :BOOL; (*备用 5层全局启停控制*)","RNQLCB05X0F_C           AT%M4324.0     :BOOL; (*备用 5层全局启停控制*)"]
["照明控制箱","RNQ","M","06X0F","启停控制","4326.0",null,"验证通过","BOOL","备用 6层全局启停控制",{"$f":"B175&VLOOKUP(A175,List!$B$3:$D$445,2,FALSE)&D175&\"_\"&VLOOKUP(E175,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB06X0F_C"},"RNQLCB06X0F_C AT%M4326.0 :BOOL; (*备用 6层全局启停控制*)","RNQLCB06X0F_C           AT%M4326.0     :BOOL; (*备用 6层全局启停控制*)"]
["照明控制箱","RNQ","M","07X0F","启停控制","4328.0",null,"验证通过","BOOL","备用 7层全局启停控制",{"$f":"B176&VLOOKUP(A176,List!$B$3:$D$445,2,FALSE)&D176&\"_\"&VLOOKUP(E176,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB07X0F_C"},{"$f":"K176&\" \"&\"AT%\"&C176&F176&\" \"&\":\"&I176&\";\"&\" \"&\"(*\"&J176&\"*)\"","v":"RNQLCB07X0F_C AT%M4328.0 :BOOL; (*备用 7层全局启停控制*)"},{"$f":"REPLACE(REPLACE(L176,SEARCH(\"AT%\",L176),,REPT(\" \",25-SEARCH(\"AT%\",L176))),SEARCH(\":\",REPLACE(L176,SEARCH(\"AT%\",L176),,REPT(\" \",25-SEARCH(\"AT%\",L176)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L176,SEARCH(\"AT%\",L176),,REPT(\" \",25-SEARCH(\"AT%\",L176))))))","v":"RNQLCB07X0F_C           AT%M4328.0     :BOOL; (*备用 7层全局启停控制*)"}]
["照明控制箱","RNQ","M","08X0F","启停控制",{"$f":"IF(OR(I176=\"REAL\",I176=\"DWORD\",I176=\"DINT\"),(IF(OR(I177=\"REAL\",I177=\"DWORD\",I177=\"DINT\"),F176+4+MOD(F176,4),F176+4)),(IF(OR(I177=\"REAL\",I177=\"DWORD\",I177=\"DINT\"),F176+4+MOD(F176,4),F176+2)))&\".0\"","v":"4330.0"},null,"验证通过","BOOL","备用 8层全局启停控制",{"$f":"B177&VLOOKUP(A177,List!$B$3:$D$445,2,FALSE)&D177&\"_\"&VLOOKUP(E177,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB08X0F_C"},"RNQLCB08X0F_C AT%M4330.0 :BOOL; (*备用 8层全局启停控制*)","RNQLCB08X0F_C           AT%M4330.0     :BOOL; (*备用 8层全局启停控制*)"]
["照明控制箱","RNQ","M","B3X0G","启停控制","4332.0",null,"验证通过","BOOL","备用 B3层全局启停控制",{"$f":"B178&VLOOKUP(A178,List!$B$3:$D$445,2,FALSE)&D178&\"_\"&VLOOKUP(E178,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB3X0G_C"},"RNQLCBB3X0G_C AT%M4332.0 :BOOL; (*备用 B3层全局启停控制*)","RNQLCBB3X0G_C           AT%M4332.0     :BOOL; (*备用 B3层全局启停控制*)"]
["照明控制箱","RNQ","M","B2X0G","启停控制","4334.0",null,"验证通过","BOOL","备用 B2层全局启停控制",{"$f":"B179&VLOOKUP(A179,List!$B$3:$D$445,2,FALSE)&D179&\"_\"&VLOOKUP(E179,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB2X0G_C"},"RNQLCBB2X0G_C AT%M4334.0 :BOOL; (*备用 B2层全局启停控制*)","RNQLCBB2X0G_C           AT%M4334.0     :BOOL; (*备用 B2层全局启停控制*)"]
["照明控制箱","RNQ","M","B1X0G","启停控制","4336.0",null,"验证通过","BOOL","备用 B1层全局启停控制",{"$f":"B180&VLOOKUP(A180,List!$B$3:$D$445,2,FALSE)&D180&\"_\"&VLOOKUP(E180,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB1X0G_C"},"RNQLCBB1X0G_C AT%M4336.0 :BOOL; (*备用 B1层全局启停控制*)","RNQLCBB1X0G_C           AT%M4336.0     :BOOL; (*备用 B1层全局启停控制*)"]
["照明控制箱","RNQ","M","01X0G","启停控制","4338.0",null,"验证通过","BOOL","备用 1层全局启停控制",{"$f":"B181&VLOOKUP(A181,List!$B$3:$D$445,2,FALSE)&D181&\"_\"&VLOOKUP(E181,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB01X0G_C"},"RNQLCB01X0G_C AT%M4338.0 :BOOL; (*备用 1层全局启停控制*)","RNQLCB01X0G_C           AT%M4338.0     :BOOL; (*备用 1层全局启停控制*)"]
["照明控制箱","RNQ","M","02X0G","启停控制","4340.0",null,"验证通过","BOOL","备用 2层全局启停控制",{"$f":"B182&VLOOKUP(A182,List!$B$3:$D$445,2,FALSE)&D182&\"_\"&VLOOKUP(E182,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB02X0G_C"},"RNQLCB02X0G_C AT%M4340.0 :BOOL; (*备用 2层全局启停控制*)","RNQLCB02X0G_C           AT%M4340.0     :BOOL; (*备用 2层全局启停控制*)"]
["照明控制箱","RNQ","M","03X0G","启停控制","4342.0",null,"验证通过","BOOL","备用 3层全局启停控制",{"$f":"B183&VLOOKUP(A183,List!$B$3:$D$445,2,FALSE)&D183&\"_\"&VLOOKUP(E183,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB03X0G_C"},"RNQLCB03X0G_C AT%M4342.0 :BOOL; (*备用 3层全局启停控制*)","RNQLCB03X0G_C           AT%M4342.0     :BOOL; (*备用 3层全局启停控制*)"]
["照明控制箱","RNQ","M","04X0G","启停控制","4344.0",null,"验证通过","BOOL","备用 4层全局启停控制",{"$f":"B184&VLOOKUP(A184,List!$B$3:$D$445,2,FALSE)&D184&\"_\"&VLOOKUP(E184,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB04X0G_C"},"RNQLCB04X0G_C AT%M4344.0 :BOOL; (*备用 4层全局启停控制*)","RNQLCB04X0G_C           AT%M4344.0     :BOOL; (*备用 4层全局启停控制*)"]
["照明控制箱","RNQ","M","05X0G","启停控制","4346.0",null,"验证通过","BOOL","备用 5层全局启停控制",{"$f":"B185&VLOOKUP(A185,List!$B$3:$D$445,2,FALSE)&D185&\"_\"&VLOOKUP(E185,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB05X0G_C"},"RNQLCB05X0G_C AT%M4346.0 :BOOL; (*备用 5层全局启停控制*)","RNQLCB05X0G_C           AT%M4346.0     :BOOL; (*备用 5层全局启停控制*)"]
["照明控制箱","RNQ","M","06X0G","启停控制","4348.0",null,"验证通过","BOOL","备用 6层全局启停控制",{"$f":"B186&VLOOKUP(A186,List!$B$3:$D$445,2,FALSE)&D186&\"_\"&VLOOKUP(E186,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB06X0G_C"},"RNQLCB06X0G_C AT%M4348.0 :BOOL; (*备用 6层全局启停控制*)","RNQLCB06X0G_C           AT%M4348.0     :BOOL; (*备用 6层全局启停控制*)"]
["照明控制箱","RNQ","M","07X0G","启停控制","4350.0",null,"验证通过","BOOL","备用 7层全局启停控制",{"$f":"B187&VLOOKUP(A187,List!$B$3:$D$445,2,FALSE)&D187&\"_\"&VLOOKUP(E187,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB07X0G_C"},{"$f":"K187&\" \"&\"AT%\"&C187&F187&\" \"&\":\"&I187&\";\"&\" \"&\"(*\"&J187&\"*)\"","v":"RNQLCB07X0G_C AT%M4350.0 :BOOL; (*备用 7层全局启停控制*)"},{"$f":"REPLACE(REPLACE(L187,SEARCH(\"AT%\",L187),,REPT(\" \",25-SEARCH(\"AT%\",L187))),SEARCH(\":\",REPLACE(L187,SEARCH(\"AT%\",L187),,REPT(\" \",25-SEARCH(\"AT%\",L187)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L187,SEARCH(\"AT%\",L187),,REPT(\" \",25-SEARCH(\"AT%\",L187))))))","v":"RNQLCB07X0G_C           AT%M4350.0     :BOOL; (*备用 7层全局启停控制*)"}]
["照明控制箱","RNQ","M","08X0G","启停控制","4352.0",null,"验证通过","BOOL","备用 8层全局启停控制",{"$f":"B188&VLOOKUP(A188,List!$B$3:$D$445,2,FALSE)&D188&\"_\"&VLOOKUP(E188,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB08X0G_C"},"RNQLCB08X0G_C AT%M4352.0 :BOOL; (*备用 8层全局启停控制*)","RNQLCB08X0G_C           AT%M4352.0     :BOOL; (*备用 8层全局启停控制*)"]
["照明控制箱","RNQ","M","B3X0H","启停控制","4354.0",null,"验证通过","BOOL","备用 B3层全局启停控制",{"$f":"B189&VLOOKUP(A189,List!$B$3:$D$445,2,FALSE)&D189&\"_\"&VLOOKUP(E189,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB3X0H_C"},"RNQLCBB3X0H_C AT%M4354.0 :BOOL; (*备用 B3层全局启停控制*)","RNQLCBB3X0H_C           AT%M4354.0     :BOOL; (*备用 B3层全局启停控制*)"]
["照明控制箱","RNQ","M","B2X0H","启停控制","4356.0",null,"验证通过","BOOL","备用 B2层全局启停控制",{"$f":"B190&VLOOKUP(A190,List!$B$3:$D$445,2,FALSE)&D190&\"_\"&VLOOKUP(E190,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB2X0H_C"},"RNQLCBB2X0H_C AT%M4356.0 :BOOL; (*备用 B2层全局启停控制*)","RNQLCBB2X0H_C           AT%M4356.0     :BOOL; (*备用 B2层全局启停控制*)"]
["照明控制箱","RNQ","M","B1X0H","启停控制","4358.0",null,"验证通过","BOOL","备用 B1层全局启停控制",{"$f":"B191&VLOOKUP(A191,List!$B$3:$D$445,2,FALSE)&D191&\"_\"&VLOOKUP(E191,List!$K$2:$M$447,2,FALSE)","v":"RNQLCBB1X0H_C"},"RNQLCBB1X0H_C AT%M4358.0 :BOOL; (*备用 B1层全局启停控制*)","RNQLCBB1X0H_C           AT%M4358.0     :BOOL; (*备用 B1层全局启停控制*)"]
["照明控制箱","RNQ","M","01X0H","启停控制","4360.0",null,"验证通过","BOOL","备用 1层全局启停控制",{"$f":"B192&VLOOKUP(A192,List!$B$3:$D$445,2,FALSE)&D192&\"_\"&VLOOKUP(E192,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB01X0H_C"},"RNQLCB01X0H_C AT%M4360.0 :BOOL; (*备用 1层全局启停控制*)","RNQLCB01X0H_C           AT%M4360.0     :BOOL; (*备用 1层全局启停控制*)"]
["照明控制箱","RNQ","M","02X0H","启停控制","4362.0",null,"验证通过","BOOL","备用 2层全局启停控制",{"$f":"B193&VLOOKUP(A193,List!$B$3:$D$445,2,FALSE)&D193&\"_\"&VLOOKUP(E193,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB02X0H_C"},"RNQLCB02X0H_C AT%M4362.0 :BOOL; (*备用 2层全局启停控制*)","RNQLCB02X0H_C           AT%M4362.0     :BOOL; (*备用 2层全局启停控制*)"]
["照明控制箱","RNQ","M","03X0H","启停控制","4364.0",null,"验证通过","BOOL","备用 3层全局启停控制",{"$f":"B194&VLOOKUP(A194,List!$B$3:$D$445,2,FALSE)&D194&\"_\"&VLOOKUP(E194,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB03X0H_C"},"RNQLCB03X0H_C AT%M4364.0 :BOOL; (*备用 3层全局启停控制*)","RNQLCB03X0H_C           AT%M4364.0     :BOOL; (*备用 3层全局启停控制*)"]
["照明控制箱","RNQ","M","04X0H","启停控制","4366.0",null,"验证通过","BOOL","备用 4层全局启停控制",{"$f":"B195&VLOOKUP(A195,List!$B$3:$D$445,2,FALSE)&D195&\"_\"&VLOOKUP(E195,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB04X0H_C"},"RNQLCB04X0H_C AT%M4366.0 :BOOL; (*备用 4层全局启停控制*)","RNQLCB04X0H_C           AT%M4366.0     :BOOL; (*备用 4层全局启停控制*)"]
["照明控制箱","RNQ","M","05X0H","启停控制","4368.0",null,"验证通过","BOOL","备用 5层全局启停控制",{"$f":"B196&VLOOKUP(A196,List!$B$3:$D$445,2,FALSE)&D196&\"_\"&VLOOKUP(E196,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB05X0H_C"},{"$f":"K196&\" \"&\"AT%\"&C196&F196&\" \"&\":\"&I196&\";\"&\" \"&\"(*\"&J196&\"*)\"","v":"RNQLCB05X0H_C AT%M4368.0 :BOOL; (*备用 5层全局启停控制*)"},"RNQLCB05X0H_C           AT%M4368.0     :BOOL; (*备用 5层全局启停控制*)"]
["照明控制箱","RNQ","M","06X0H","启停控制","4370.0",null,"验证通过","BOOL","备用 6层全局启停控制",{"$f":"B197&VLOOKUP(A197,List!$B$3:$D$445,2,FALSE)&D197&\"_\"&VLOOKUP(E197,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB06X0H_C"},"RNQLCB06X0H_C AT%M4370.0 :BOOL; (*备用 6层全局启停控制*)","RNQLCB06X0H_C           AT%M4370.0     :BOOL; (*备用 6层全局启停控制*)"]
["照明控制箱","RNQ","M","07X0H","启停控制","4372.0",null,"验证通过","BOOL","备用 7层全局启停控制",{"$f":"B198&VLOOKUP(A198,List!$B$3:$D$445,2,FALSE)&D198&\"_\"&VLOOKUP(E198,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB07X0H_C"},{"$f":"K198&\" \"&\"AT%\"&C198&F198&\" \"&\":\"&I198&\";\"&\" \"&\"(*\"&J198&\"*)\"","v":"RNQLCB07X0H_C AT%M4372.0 :BOOL; (*备用 7层全局启停控制*)"},{"$f":"REPLACE(REPLACE(L198,SEARCH(\"AT%\",L198),,REPT(\" \",25-SEARCH(\"AT%\",L198))),SEARCH(\":\",REPLACE(L198,SEARCH(\"AT%\",L198),,REPT(\" \",25-SEARCH(\"AT%\",L198)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L198,SEARCH(\"AT%\",L198),,REPT(\" \",25-SEARCH(\"AT%\",L198))))))","v":"RNQLCB07X0H_C           AT%M4372.0     :BOOL; (*备用 7层全局启停控制*)"}]
["照明控制箱","RNQ","M","08X0H","启停控制","4374.0",null,"验证通过","BOOL","备用 8层全局启停控制",{"$f":"B199&VLOOKUP(A199,List!$B$3:$D$445,2,FALSE)&D199&\"_\"&VLOOKUP(E199,List!$K$2:$M$447,2,FALSE)","v":"RNQLCB08X0H_C"},"RNQLCB08X0H_C AT%M4374.0 :BOOL; (*备用 8层全局启停控制*)","RNQLCB08X0H_C           AT%M4374.0     :BOOL; (*备用 8层全局启停控制*)"]
["P新风机组","RNQ","M","05X00","设定温度值","4380.0",null,"验证通过","REAL","新风机组5层温度全局设定",{"$f":"B200&VLOOKUP(A200,List!$B$3:$D$445,2,FALSE)&D200&\"_\"&VLOOKUP(E200,List!$K$2:$M$447,2,FALSE)","v":"RNQPAU05X00_TSET"},"RNQPAU05X00_TSET AT%M4380.0 :REAL; (*新风机组5层温度全局设定*)","RNQPAU05X00_TSET        AT%M4380.0     :REAL; (*新风机组5层温度全局设定*)"]
["P新风机组","RNQ","M","06X00","设定温度值","4384.0",null,"验证通过","REAL","新风机组6层温度全局设定",{"$f":"B201&VLOOKUP(A201,List!$B$3:$D$445,2,FALSE)&D201&\"_\"&VLOOKUP(E201,List!$K$2:$M$447,2,FALSE)","v":"RNQPAU06X00_TSET"},"RNQPAU06X00_TSET AT%M4384.0 :REAL; (*新风机组6层温度全局设定*)","RNQPAU06X00_TSET        AT%M4384.0     :REAL; (*新风机组6层温度全局设定*)"]
["P新风机组","RNQ","M","07X00","设定温度值","4388.0",null,"验证通过","REAL","新风机组7层温度全局设定",{"$f":"B202&VLOOKUP(A202,List!$B$3:$D$445,2,FALSE)&D202&\"_\"&VLOOKUP(E202,List!$K$2:$M$447,2,FALSE)","v":"RNQPAU07X00_TSET"},"RNQPAU07X00_TSET AT%M4388.0 :REAL; (*新风机组7层温度全局设定*)","RNQPAU07X00_TSET        AT%M4388.0     :REAL; (*新风机组7层温度全局设定*)"]
["P新风机组","RNQ","M","08X00","设定温度值","4392.0",null,"验证通过","REAL","新风机组8层温度全局设定",{"$f":"B203&VLOOKUP(A203,List!$B$3:$D$445,2,FALSE)&D203&\"_\"&VLOOKUP(E203,List!$K$2:$M$447,2,FALSE)","v":"RNQPAU08X00_TSET"},"RNQPAU08X00_TSET AT%M4392.0 :REAL; (*新风机组8层温度全局设定*)","RNQPAU08X00_TSET        AT%M4392.0     :REAL; (*新风机组8层温度全局设定*)"]
["P新风机组","RNQ","M","09X00","设定温度值","4396.0",null,"验证通过","REAL","新风机组9层温度全局设定",{"$f":"B204&VLOOKUP(A204,List!$B$3:$D$445,2,FALSE)&D204&\"_\"&VLOOKUP(E204,List!$K$2:$M$447,2,FALSE)","v":"RNQPAU09X00_TSET"},"RNQPAU09X00_TSET AT%M4396.0 :REAL; (*新风机组9层温度全局设定*)","RNQPAU09X00_TSET        AT%M4396.0     :REAL; (*新风机组9层温度全局设定*)"]
["P新风机组","RNQ","M","05X00","季节模式","4400.0",null,"验证通过","INT","新风机组5层季节模式全局设定",{"$f":"B205&VLOOKUP(A205,List!$B$3:$D$445,2,FALSE)&D205&\"_\"&VLOOKUP(E205,List!$K$2:$M$447,2,FALSE)","v":"RNQPAU05X00_SM"},"RNQPAU05X00_SM AT%M4400.0 :INT; (*新风机组5层季节模式全局设定*)","RNQPAU05X00_SM          AT%M4400.0     :INT; (*新风机组5层季节模式全局设定*)"]
["P新风机组","RNQ","M","06X00","季节模式","4402.0",null,"验证通过","INT","新风机组6层季节模式全局设定",{"$f":"B206&VLOOKUP(A206,List!$B$3:$D$445,2,FALSE)&D206&\"_\"&VLOOKUP(E206,List!$K$2:$M$447,2,FALSE)","v":"RNQPAU06X00_SM"},"RNQPAU06X00_SM AT%M4402.0 :INT; (*新风机组6层季节模式全局设定*)","RNQPAU06X00_SM          AT%M4402.0     :INT; (*新风机组6层季节模式全局设定*)"]
["P新风机组","RNQ","M","07X00","季节模式","4404.0",null,"验证通过","INT","新风机组7层季节模式全局设定",{"$f":"B207&VLOOKUP(A207,List!$B$3:$D$445,2,FALSE)&D207&\"_\"&VLOOKUP(E207,List!$K$2:$M$447,2,FALSE)","v":"RNQPAU07X00_SM"},"RNQPAU07X00_SM AT%M4404.0 :INT; (*新风机组7层季节模式全局设定*)","RNQPAU07X00_SM          AT%M4404.0     :INT; (*新风机组7层季节模式全局设定*)"]
["P新风机组","RNQ","M","08X00","季节模式","4406.0",null,"验证通过","INT","新风机组8层季节模式全局设定",{"$f":"B208&VLOOKUP(A208,List!$B$3:$D$445,2,FALSE)&D208&\"_\"&VLOOKUP(E208,List!$K$2:$M$447,2,FALSE)","v":"RNQPAU08X00_SM"},"RNQPAU08X00_SM AT%M4406.0 :INT; (*新风机组8层季节模式全局设定*)","RNQPAU08X00_SM          AT%M4406.0     :INT; (*新风机组8层季节模式全局设定*)"]
["P新风机组","RNQ","M","09X00","季节模式","4408.0",null,"验证通过","INT","新风机组9层季节模式全局设定",{"$f":"B209&VLOOKUP(A209,List!$B$3:$D$445,2,FALSE)&D209&\"_\"&VLOOKUP(E209,List!$K$2:$M$447,2,FALSE)","v":"RNQPAU09X00_SM"},"RNQPAU09X00_SM AT%M4408.0 :INT; (*新风机组9层季节模式全局设定*)","RNQPAU09X00_SM          AT%M4408.0     :INT; (*新风机组9层季节模式全局设定*)"]
["P新风机组","RNQ","M","05X00","程序控制","4410.0",null,"验证通过","BOOL","新风机组5层启停控制",{"$f":"B210&VLOOKUP(A210,List!$B$3:$D$445,2,FALSE)&D210&\"_\"&VLOOKUP(E210,List!$K$2:$M$447,2,FALSE)","v":"RNQPAU05X00_PC"},"RNQPAU05X00_PC AT%M4410.0 :BOOL; (*新风机组5层启停控制*)","RNQPAU05X00_PC          AT%M4410.0     :BOOL; (*新风机组5层启停控制*)"]
["P新风机组","RNQ","M","06X00","程序控制","4412.0",null,"验证通过","BOOL","新风机组6层启停控制",{"$f":"B211&VLOOKUP(A211,List!$B$3:$D$445,2,FALSE)&D211&\"_\"&VLOOKUP(E211,List!$K$2:$M$447,2,FALSE)","v":"RNQPAU06X00_PC"},"RNQPAU06X00_PC AT%M4412.0 :BOOL; (*新风机组6层启停控制*)","RNQPAU06X00_PC          AT%M4412.0     :BOOL; (*新风机组6层启停控制*)"]
["P新风机组","RNQ","M","07X00","程序控制","4414.0",null,"验证通过","BOOL","新风机组7层启停控制",{"$f":"B212&VLOOKUP(A212,List!$B$3:$D$445,2,FALSE)&D212&\"_\"&VLOOKUP(E212,List!$K$2:$M$447,2,FALSE)","v":"RNQPAU07X00_PC"},"RNQPAU07X00_PC AT%M4414.0 :BOOL; (*新风机组7层启停控制*)","RNQPAU07X00_PC          AT%M4414.0     :BOOL; (*新风机组7层启停控制*)"]
["P新风机组","RNQ","M","08X00","程序控制","4416.0",null,"验证通过","BOOL","新风机组8层启停控制",{"$f":"B213&VLOOKUP(A213,List!$B$3:$D$445,2,FALSE)&D213&\"_\"&VLOOKUP(E213,List!$K$2:$M$447,2,FALSE)","v":"RNQPAU08X00_PC"},"RNQPAU08X00_PC AT%M4416.0 :BOOL; (*新风机组8层启停控制*)","RNQPAU08X00_PC          AT%M4416.0     :BOOL; (*新风机组8层启停控制*)"]
["P新风机组","RNQ","M","09X00","程序控制","4418.0",null,"验证通过","BOOL","新风机组9层启停控制",{"$f":"B214&VLOOKUP(A214,List!$B$3:$D$445,2,FALSE)&D214&\"_\"&VLOOKUP(E214,List!$K$2:$M$447,2,FALSE)","v":"RNQPAU09X00_PC"},"RNQPAU09X00_PC AT%M4418.0 :BOOL; (*新风机组9层启停控制*)","RNQPAU09X00_PC          AT%M4418.0     :BOOL; (*新风机组9层启停控制*)"]
["送风机","RNQ","M","B3X00","程序控制","4420.0",null,"验证通过","BOOL","送风机B3层启停控制",{"$f":"B215&VLOOKUP(A215,List!$B$3:$D$445,2,FALSE)&D215&\"_\"&VLOOKUP(E215,List!$K$2:$M$447,2,FALSE)","v":"RNQSAFB3X00_PC"},"RNQSAFB3X00_PC AT%M4420.0 :BOOL; (*送风机B3层启停控制*)","RNQSAFB3X00_PC          AT%M4420.0     :BOOL; (*送风机B3层启停控制*)"]
["送风机","RNQ","M","B2X00","程序控制","4422.0",null,"验证通过","BOOL","送风机B2层启停控制",{"$f":"B216&VLOOKUP(A216,List!$B$3:$D$445,2,FALSE)&D216&\"_\"&VLOOKUP(E216,List!$K$2:$M$447,2,FALSE)","v":"RNQSAFB2X00_PC"},"RNQSAFB2X00_PC AT%M4422.0 :BOOL; (*送风机B2层启停控制*)","RNQSAFB2X00_PC          AT%M4422.0     :BOOL; (*送风机B2层启停控制*)"]
["送风机","RNQ","M","B1X00","程序控制","4424.0",null,"验证通过","BOOL","送风机B1层启停控制",{"$f":"B217&VLOOKUP(A217,List!$B$3:$D$445,2,FALSE)&D217&\"_\"&VLOOKUP(E217,List!$K$2:$M$447,2,FALSE)","v":"RNQSAFB1X00_PC"},"RNQSAFB1X00_PC AT%M4424.0 :BOOL; (*送风机B1层启停控制*)","RNQSAFB1X00_PC          AT%M4424.0     :BOOL; (*送风机B1层启停控制*)"]
["送风机","RNQ","M","05X00","程序控制","4426.0",null,"验证通过","BOOL","送风机5层启停控制",{"$f":"B218&VLOOKUP(A218,List!$B$3:$D$445,2,FALSE)&D218&\"_\"&VLOOKUP(E218,List!$K$2:$M$447,2,FALSE)","v":"RNQSAF05X00_PC"},"RNQSAF05X00_PC AT%M4426.0 :BOOL; (*送风机5层启停控制*)","RNQSAF05X00_PC          AT%M4426.0     :BOOL; (*送风机5层启停控制*)"]
["送风机","RNQ","M","06X00","程序控制","4428.0",null,"验证通过","BOOL","送风机6层启停控制",{"$f":"B219&VLOOKUP(A219,List!$B$3:$D$445,2,FALSE)&D219&\"_\"&VLOOKUP(E219,List!$K$2:$M$447,2,FALSE)","v":"RNQSAF06X00_PC"},"RNQSAF06X00_PC AT%M4428.0 :BOOL; (*送风机6层启停控制*)","RNQSAF06X00_PC          AT%M4428.0     :BOOL; (*送风机6层启停控制*)"]
["送风机","RNQ","M","07X00","程序控制","4430.0",null,"验证通过","BOOL","送风机7层启停控制",{"$f":"B220&VLOOKUP(A220,List!$B$3:$D$445,2,FALSE)&D220&\"_\"&VLOOKUP(E220,List!$K$2:$M$447,2,FALSE)","v":"RNQSAF07X00_PC"},"RNQSAF07X00_PC AT%M4430.0 :BOOL; (*送风机7层启停控制*)","RNQSAF07X00_PC          AT%M4430.0     :BOOL; (*送风机7层启停控制*)"]
["送风机","RNQ","M","08X00","程序控制","4432.0",null,"验证通过","BOOL","送风机8层启停控制",{"$f":"B221&VLOOKUP(A221,List!$B$3:$D$445,2,FALSE)&D221&\"_\"&VLOOKUP(E221,List!$K$2:$M$447,2,FALSE)","v":"RNQSAF08X00_PC"},"RNQSAF08X00_PC AT%M4432.0 :BOOL; (*送风机8层启停控制*)","RNQSAF08X00_PC          AT%M4432.0     :BOOL; (*送风机8层启停控制*)"]
["送风机","RNQ","M","09X00","程序控制","4434.0",null,"验证通过","BOOL","送风机9层启停控制",{"$f":"B222&VLOOKUP(A222,List!$B$3:$D$445,2,FALSE)&D222&\"_\"&VLOOKUP(E222,List!$K$2:$M$447,2,FALSE)","v":"RNQSAF09X00_PC"},"RNQSAF09X00_PC AT%M4434.0 :BOOL; (*送风机9层启停控制*)","RNQSAF09X00_PC          AT%M4434.0     :BOOL; (*送风机9层启停控制*)"]
["排风机","RNQ","M","B3X00","程序控制","4436.0",null,"验证通过","BOOL","排风机B3层启停控制",{"$f":"B223&VLOOKUP(A223,List!$B$3:$D$445,2,FALSE)&D223&\"_\"&VLOOKUP(E223,List!$K$2:$M$447,2,FALSE)","v":"RNQEAFB3X00_PC"},"RNQEAFB3X00_PC AT%M4436.0 :BOOL; (*排风机B3层启停控制*)","RNQEAFB3X00_PC          AT%M4436.0     :BOOL; (*排风机B3层启停控制*)"]
["排风机","RNQ","M","B2X00","程序控制","4438.0",null,"验证通过","BOOL","排风机B2层启停控制",{"$f":"B224&VLOOKUP(A224,List!$B$3:$D$445,2,FALSE)&D224&\"_\"&VLOOKUP(E224,List!$K$2:$M$447,2,FALSE)","v":"RNQEAFB2X00_PC"},"RNQEAFB2X00_PC AT%M4438.0 :BOOL; (*排风机B2层启停控制*)","RNQEAFB2X00_PC          AT%M4438.0     :BOOL; (*排风机B2层启停控制*)"]
["排风机","RNQ","M","B1X00","程序控制","4440.0",null,{"$f":"IF((IF(OR(I225=\"INT\",I225=\"WORD\",I225=\"BOOL\"),MOD(F225,2),MOD(F225,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","排风机B1层启停控制",{"$f":"B225&VLOOKUP(A225,List!$B$3:$D$445,2,FALSE)&D225&\"_\"&VLOOKUP(E225,List!$K$2:$M$447,2,FALSE)","v":"RNQEAFB1X00_PC"},"RNQEAFB1X00_PC AT%M4440.0 :BOOL; (*排风机B1层启停控制*)","RNQEAFB1X00_PC          AT%M4440.0     :BOOL; (*排风机B1层启停控制*)"]
["排风机","RNQ","M","05X00","程序控制","4442.0",null,"验证通过","BOOL","排风机5层启停控制",{"$f":"B226&VLOOKUP(A226,List!$B$3:$D$445,2,FALSE)&D226&\"_\"&VLOOKUP(E226,List!$K$2:$M$447,2,FALSE)","v":"RNQEAF05X00_PC"},"RNQEAF05X00_PC AT%M4442.0 :BOOL; (*排风机5层启停控制*)","RNQEAF05X00_PC          AT%M4442.0     :BOOL; (*排风机5层启停控制*)"]
["排风机","RNQ","M","06X00","程序控制","4444.0",null,"验证通过","BOOL","排风机6层启停控制",{"$f":"B227&VLOOKUP(A227,List!$B$3:$D$445,2,FALSE)&D227&\"_\"&VLOOKUP(E227,List!$K$2:$M$447,2,FALSE)","v":"RNQEAF06X00_PC"},"RNQEAF06X00_PC AT%M4444.0 :BOOL; (*排风机6层启停控制*)","RNQEAF06X00_PC          AT%M4444.0     :BOOL; (*排风机6层启停控制*)"]
["排风机","RNQ","M","07X00","程序控制","4446.0",null,"验证通过","BOOL","排风机7层启停控制",{"$f":"B228&VLOOKUP(A228,List!$B$3:$D$445,2,FALSE)&D228&\"_\"&VLOOKUP(E228,List!$K$2:$M$447,2,FALSE)","v":"RNQEAF07X00_PC"},"RNQEAF07X00_PC AT%M4446.0 :BOOL; (*排风机7层启停控制*)",{"$f":"REPLACE(REPLACE(L228,SEARCH(\"AT%\",L228),,REPT(\" \",25-SEARCH(\"AT%\",L228))),SEARCH(\":\",REPLACE(L228,SEARCH(\"AT%\",L228),,REPT(\" \",25-SEARCH(\"AT%\",L228)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L228,SEARCH(\"AT%\",L228),,REPT(\" \",25-SEARCH(\"AT%\",L228))))))","v":"RNQEAF07X00_PC          AT%M4446.0     :BOOL; (*排风机7层启停控制*)"}]
["排风机","RNQ","M","08X00","程序控制","4448.0",null,"验证通过","BOOL","排风机8层启停控制",{"$f":"B229&VLOOKUP(A229,List!$B$3:$D$445,2,FALSE)&D229&\"_\"&VLOOKUP(E229,List!$K$2:$M$447,2,FALSE)","v":"RNQEAF08X00_PC"},"RNQEAF08X00_PC AT%M4448.0 :BOOL; (*排风机8层启停控制*)","RNQEAF08X00_PC          AT%M4448.0     :BOOL; (*排风机8层启停控制*)"]
["排风机","RNQ","M","09X00","程序控制","4450.0",null,"验证通过","BOOL","排风机9层启停控制",{"$f":"B230&VLOOKUP(A230,List!$B$3:$D$445,2,FALSE)&D230&\"_\"&VLOOKUP(E230,List!$K$2:$M$447,2,FALSE)","v":"RNQEAF09X00_PC"},"RNQEAF09X00_PC AT%M4450.0 :BOOL; (*排风机9层启停控制*)","RNQEAF09X00_PC          AT%M4450.0     :BOOL; (*排风机9层启停控制*)"]
["风幕机","RNQ","M","B3X00","程序控制","4452.0",null,"验证通过","BOOL","风幕机B3层启停控制",{"$f":"B231&VLOOKUP(A231,List!$B$3:$D$445,2,FALSE)&D231&\"_\"&VLOOKUP(E231,List!$K$2:$M$447,2,FALSE)","v":"RNQACB3X00_PC"},"RNQACB3X00_PC AT%M4452.0 :BOOL; (*风幕机B3层启停控制*)","RNQACB3X00_PC           AT%M4452.0     :BOOL; (*风幕机B3层启停控制*)"]
["风幕机","RNQ","M","B2X00","程序控制","4454.0",null,"验证通过","BOOL","风幕机B2层启停控制",{"$f":"B232&VLOOKUP(A232,List!$B$3:$D$445,2,FALSE)&D232&\"_\"&VLOOKUP(E232,List!$K$2:$M$447,2,FALSE)","v":"RNQACB2X00_PC"},"RNQACB2X00_PC AT%M4454.0 :BOOL; (*风幕机B2层启停控制*)","RNQACB2X00_PC           AT%M4454.0     :BOOL; (*风幕机B2层启停控制*)"]
["风幕机","RNQ","M","B1X00","程序控制","4456.0",null,"验证通过","BOOL","风幕机B1层启停控制",{"$f":"B233&VLOOKUP(A233,List!$B$3:$D$445,2,FALSE)&D233&\"_\"&VLOOKUP(E233,List!$K$2:$M$447,2,FALSE)","v":"RNQACB1X00_PC"},"RNQACB1X00_PC AT%M4456.0 :BOOL; (*风幕机B1层启停控制*)","RNQACB1X00_PC           AT%M4456.0     :BOOL; (*风幕机B1层启停控制*)"]
["风幕机","RNQ","M","01X00","程序控制","4458.0",null,"验证通过","BOOL","风幕机1层启停控制",{"$f":"B234&VLOOKUP(A234,List!$B$3:$D$445,2,FALSE)&D234&\"_\"&VLOOKUP(E234,List!$K$2:$M$447,2,FALSE)","v":"RNQAC01X00_PC"},"RNQAC01X00_PC AT%M4458.0 :BOOL; (*风幕机1层启停控制*)","RNQAC01X00_PC           AT%M4458.0     :BOOL; (*风幕机1层启停控制*)"]
["风幕机","RNQ","M","02X00","程序控制","4460.0",null,"验证通过","BOOL","风幕机2层启停控制",{"$f":"B235&VLOOKUP(A235,List!$B$3:$D$445,2,FALSE)&D235&\"_\"&VLOOKUP(E235,List!$K$2:$M$447,2,FALSE)","v":"RNQAC02X00_PC"},"RNQAC02X00_PC AT%M4460.0 :BOOL; (*风幕机2层启停控制*)","RNQAC02X00_PC           AT%M4460.0     :BOOL; (*风幕机2层启停控制*)"]
["风幕机","RNQ","M","03X00","程序控制","4462.0",null,"验证通过","BOOL","风幕机3层启停控制",{"$f":"B236&VLOOKUP(A236,List!$B$3:$D$445,2,FALSE)&D236&\"_\"&VLOOKUP(E236,List!$K$2:$M$447,2,FALSE)","v":"RNQAC03X00_PC"},"RNQAC03X00_PC AT%M4462.0 :BOOL; (*风幕机3层启停控制*)","RNQAC03X00_PC           AT%M4462.0     :BOOL; (*风幕机3层启停控制*)"]
["风幕机","RNQ","M","04X00","程序控制","4464.0",null,"验证通过","BOOL","风幕机4层启停控制",{"$f":"B237&VLOOKUP(A237,List!$B$3:$D$445,2,FALSE)&D237&\"_\"&VLOOKUP(E237,List!$K$2:$M$447,2,FALSE)","v":"RNQAC04X00_PC"},"RNQAC04X00_PC AT%M4464.0 :BOOL; (*风幕机4层启停控制*)","RNQAC04X00_PC           AT%M4464.0     :BOOL; (*风幕机4层启停控制*)"]
["风幕机","RNQ","M","05X00","程序控制","4466.0",null,"验证通过","BOOL","风幕机5层启停控制",{"$f":"B238&VLOOKUP(A238,List!$B$3:$D$445,2,FALSE)&D238&\"_\"&VLOOKUP(E238,List!$K$2:$M$447,2,FALSE)","v":"RNQAC05X00_PC"},"RNQAC05X00_PC AT%M4466.0 :BOOL; (*风幕机5层启停控制*)","RNQAC05X00_PC           AT%M4466.0     :BOOL; (*风幕机5层启停控制*)"]
["风幕机","RNQ","M","06X00","程序控制","4468.0",null,{"$f":"IF((IF(OR(I239=\"INT\",I239=\"WORD\",I239=\"BOOL\"),MOD(F239,2),MOD(F239,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","风幕机6层启停控制",{"$f":"B239&VLOOKUP(A239,List!$B$3:$D$445,2,FALSE)&D239&\"_\"&VLOOKUP(E239,List!$K$2:$M$447,2,FALSE)","v":"RNQAC06X00_PC"},{"$f":"K239&\" \"&\"AT%\"&C239&F239&\" \"&\":\"&I239&\";\"&\" \"&\"(*\"&J239&\"*)\"","v":"RNQAC06X00_PC AT%M4468.0 :BOOL; (*风幕机6层启停控制*)"},{"$f":"REPLACE(REPLACE(L239,SEARCH(\"AT%\",L239),,REPT(\" \",25-SEARCH(\"AT%\",L239))),SEARCH(\":\",REPLACE(L239,SEARCH(\"AT%\",L239),,REPT(\" \",25-SEARCH(\"AT%\",L239)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L239,SEARCH(\"AT%\",L239),,REPT(\" \",25-SEARCH(\"AT%\",L239))))))","v":"RNQAC06X00_PC           AT%M4468.0     :BOOL; (*风幕机6层启停控制*)"}]
["风幕机","RNQ","M","07X00","程序控制","4470.0",null,"验证通过","BOOL","风幕机7层启停控制",{"$f":"B240&VLOOKUP(A240,List!$B$3:$D$445,2,FALSE)&D240&\"_\"&VLOOKUP(E240,List!$K$2:$M$447,2,FALSE)","v":"RNQAC07X00_PC"},{"$f":"K240&\" \"&\"AT%\"&C240&F240&\" \"&\":\"&I240&\";\"&\" \"&\"(*\"&J240&\"*)\"","v":"RNQAC07X00_PC AT%M4470.0 :BOOL; (*风幕机7层启停控制*)"},"RNQAC07X00_PC           AT%M4470.0     :BOOL; (*风幕机7层启停控制*)"]
["风幕机","RNQ","M","08X00","程序控制",{"$f":"IF(OR(I240=\"REAL\",I240=\"DWORD\",I240=\"DINT\"),(IF(OR(I241=\"REAL\",I241=\"DWORD\",I241=\"DINT\"),F240+4+MOD(F240,4),F240+4)),(IF(OR(I241=\"REAL\",I241=\"DWORD\",I241=\"DINT\"),F240+4+MOD(F240,4),F240+2)))&\".0\"","v":"4472.0"},null,"验证通过","BOOL","风幕机8层启停控制",{"$f":"B241&VLOOKUP(A241,List!$B$3:$D$445,2,FALSE)&D241&\"_\"&VLOOKUP(E241,List!$K$2:$M$447,2,FALSE)","v":"RNQAC08X00_PC"},"RNQAC08X00_PC AT%M4472.0 :BOOL; (*风幕机8层启停控制*)","RNQAC08X00_PC           AT%M4472.0     :BOOL; (*风幕机8层启停控制*)"]
["水幕机","RNQ","M","B3X00","程序控制","4474.0",null,"验证通过","BOOL","水幕机B3层启停控制",{"$f":"B242&VLOOKUP(A242,List!$B$3:$D$445,2,FALSE)&D242&\"_\"&VLOOKUP(E242,List!$K$2:$M$447,2,FALSE)","v":"RNQWACB3X00_PC"},"RNQWACB3X00_PC AT%M4474.0 :BOOL; (*水幕机B3层启停控制*)","RNQWACB3X00_PC          AT%M4474.0     :BOOL; (*水幕机B3层启停控制*)"]
["水幕机","RNQ","M","B2X00","程序控制","4476.0",null,"验证通过","BOOL","水幕机B2层启停控制",{"$f":"B243&VLOOKUP(A243,List!$B$3:$D$445,2,FALSE)&D243&\"_\"&VLOOKUP(E243,List!$K$2:$M$447,2,FALSE)","v":"RNQWACB2X00_PC"},"RNQWACB2X00_PC AT%M4476.0 :BOOL; (*水幕机B2层启停控制*)","RNQWACB2X00_PC          AT%M4476.0     :BOOL; (*水幕机B2层启停控制*)"]
["水幕机","RNQ","M","B1X00","程序控制","4478.0",null,"验证通过","BOOL","水幕机B1层启停控制",{"$f":"B244&VLOOKUP(A244,List!$B$3:$D$445,2,FALSE)&D244&\"_\"&VLOOKUP(E244,List!$K$2:$M$447,2,FALSE)","v":"RNQWACB1X00_PC"},"RNQWACB1X00_PC AT%M4478.0 :BOOL; (*水幕机B1层启停控制*)","RNQWACB1X00_PC          AT%M4478.0     :BOOL; (*水幕机B1层启停控制*)"]
["水幕机","RNQ","M","01X00","程序控制","4480.0",null,"验证通过","BOOL","水幕机1层启停控制",{"$f":"B245&VLOOKUP(A245,List!$B$3:$D$445,2,FALSE)&D245&\"_\"&VLOOKUP(E245,List!$K$2:$M$447,2,FALSE)","v":"RNQWAC01X00_PC"},"RNQWAC01X00_PC AT%M4480.0 :BOOL; (*水幕机1层启停控制*)","RNQWAC01X00_PC          AT%M4480.0     :BOOL; (*水幕机1层启停控制*)"]
["水幕机","RNQ","M","02X00","程序控制","4482.0",null,"验证通过","BOOL","水幕机2层启停控制",{"$f":"B246&VLOOKUP(A246,List!$B$3:$D$445,2,FALSE)&D246&\"_\"&VLOOKUP(E246,List!$K$2:$M$447,2,FALSE)","v":"RNQWAC02X00_PC"},"RNQWAC02X00_PC AT%M4482.0 :BOOL; (*水幕机2层启停控制*)","RNQWAC02X00_PC          AT%M4482.0     :BOOL; (*水幕机2层启停控制*)"]
["水幕机","RNQ","M","03X00","程序控制","4484.0",null,"验证通过","BOOL","水幕机3层启停控制",{"$f":"B247&VLOOKUP(A247,List!$B$3:$D$445,2,FALSE)&D247&\"_\"&VLOOKUP(E247,List!$K$2:$M$447,2,FALSE)","v":"RNQWAC03X00_PC"},"RNQWAC03X00_PC AT%M4484.0 :BOOL; (*水幕机3层启停控制*)","RNQWAC03X00_PC          AT%M4484.0     :BOOL; (*水幕机3层启停控制*)"]
["水幕机","RNQ","M","04X00","程序控制","4486.0",null,"验证通过","BOOL","水幕机4层启停控制",{"$f":"B248&VLOOKUP(A248,List!$B$3:$D$445,2,FALSE)&D248&\"_\"&VLOOKUP(E248,List!$K$2:$M$447,2,FALSE)","v":"RNQWAC04X00_PC"},"RNQWAC04X00_PC AT%M4486.0 :BOOL; (*水幕机4层启停控制*)","RNQWAC04X00_PC          AT%M4486.0     :BOOL; (*水幕机4层启停控制*)"]
["水幕机","RNQ","M","05X00","程序控制","4488.0",null,"验证通过","BOOL","水幕机5层启停控制",{"$f":"B249&VLOOKUP(A249,List!$B$3:$D$445,2,FALSE)&D249&\"_\"&VLOOKUP(E249,List!$K$2:$M$447,2,FALSE)","v":"RNQWAC05X00_PC"},"RNQWAC05X00_PC AT%M4488.0 :BOOL; (*水幕机5层启停控制*)","RNQWAC05X00_PC          AT%M4488.0     :BOOL; (*水幕机5层启停控制*)"]
["水幕机","RNQ","M","06X00","程序控制","4490.0",null,{"$f":"IF((IF(OR(I250=\"INT\",I250=\"WORD\",I250=\"BOOL\"),MOD(F250,2),MOD(F250,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","水幕机6层启停控制",{"$f":"B250&VLOOKUP(A250,List!$B$3:$D$445,2,FALSE)&D250&\"_\"&VLOOKUP(E250,List!$K$2:$M$447,2,FALSE)","v":"RNQWAC06X00_PC"},{"$f":"K250&\" \"&\"AT%\"&C250&F250&\" \"&\":\"&I250&\";\"&\" \"&\"(*\"&J250&\"*)\"","v":"RNQWAC06X00_PC AT%M4490.0 :BOOL; (*水幕机6层启停控制*)"},{"$f":"REPLACE(REPLACE(L250,SEARCH(\"AT%\",L250),,REPT(\" \",25-SEARCH(\"AT%\",L250))),SEARCH(\":\",REPLACE(L250,SEARCH(\"AT%\",L250),,REPT(\" \",25-SEARCH(\"AT%\",L250)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L250,SEARCH(\"AT%\",L250),,REPT(\" \",25-SEARCH(\"AT%\",L250))))))","v":"RNQWAC06X00_PC          AT%M4490.0     :BOOL; (*水幕机6层启停控制*)"}]
["水幕机","RNQ","M","07X00","程序控制","4492.0",null,"验证通过","BOOL","水幕机7层启停控制",{"$f":"B251&VLOOKUP(A251,List!$B$3:$D$445,2,FALSE)&D251&\"_\"&VLOOKUP(E251,List!$K$2:$M$447,2,FALSE)","v":"RNQWAC07X00_PC"},"RNQWAC07X00_PC AT%M4492.0 :BOOL; (*水幕机7层启停控制*)","RNQWAC07X00_PC          AT%M4492.0     :BOOL; (*水幕机7层启停控制*)"]
["水幕机","RNQ","M","08X00","程序控制","4494.0",null,"验证通过","BOOL","水幕机8层启停控制",{"$f":"B252&VLOOKUP(A252,List!$B$3:$D$445,2,FALSE)&D252&\"_\"&VLOOKUP(E252,List!$K$2:$M$447,2,FALSE)","v":"RNQWAC08X00_PC"},"RNQWAC08X00_PC AT%M4494.0 :BOOL; (*水幕机8层启停控制*)","RNQWAC08X00_PC          AT%M4494.0     :BOOL; (*水幕机8层启停控制*)"]
["冷水机组",{"$nulls":6},"验证通过","BOOL",null,{"$f":"B253&VLOOKUP(A253,List!$B$3:$D$445,2,FALSE)&D253&\"_\"&VLOOKUP(E253,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":7},"验证通过","BOOL",null,{"$f":"B254&VLOOKUP(A254,List!$B$3:$D$445,2,FALSE)&D254&\"_\"&VLOOKUP(E254,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":7},"验证通过","BOOL",null,{"$f":"B255&VLOOKUP(A255,List!$B$3:$D$445,2,FALSE)&D255&\"_\"&VLOOKUP(E255,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":7},"验证通过","BOOL",null,{"$f":"B256&VLOOKUP(A256,List!$B$3:$D$445,2,FALSE)&D256&\"_\"&VLOOKUP(E256,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":7},"验证通过","BOOL",null,{"$f":"B257&VLOOKUP(A257,List!$B$3:$D$445,2,FALSE)&D257&\"_\"&VLOOKUP(E257,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[]
[{"$nulls":10},{"$f":"B259&VLOOKUP(A259,List!$B$3:$D$445,2,FALSE)&D239&\"_\"&VLOOKUP(E259,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"K259&\" \"&\"AT%\"&C259&F259&\" \"&\":\"&I259&\";\"&\" \"&\"(*\"&J259&\"*)\"","v":{"$error":"#N/A"}},{"$f":"REPLACE(REPLACE(L259,SEARCH(\"AT%\",L259),,REPT(\" \",25-SEARCH(\"AT%\",L259))),SEARCH(\":\",REPLACE(L259,SEARCH(\"AT%\",L259),,REPT(\" \",25-SEARCH(\"AT%\",L259)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L259,SEARCH(\"AT%\",L259),,REPT(\" \",25-SEARCH(\"AT%\",L259))))))","v":{"$error":"#N/A"}}]
["OPCDA"]
["照明控制箱","L","M","B3X0A","启停控制","100.0",null,{"$f":"IF((IF(OR(I261=\"INT\",I261=\"WORD\",I261=\"BOOL\"),MOD(F261,2),MOD(F261,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A261&D261&\"-\"&E261","v":"照明控制箱B3X0A-启停控制"},{"$f":"B261&VLOOKUP(A261,List!$B$3:$D$445,2,FALSE)&D261&\"_\"&VLOOKUP(E261,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0A_C"},"LLCBB3X0A_C AT%M100.0 :BOOL; (*照明控制箱B3X0A-启停控制*)","LLCBB3X0A_C             AT%M100.0      :BOOL; (*照明控制箱B3X0A-启停控制*)"]
["照明控制箱","L","M","B2X0A","启停控制",{"$f":"IF(OR(I261=\"REAL\",I261=\"DWORD\",I261=\"DINT\"),(IF(OR(I262=\"REAL\",I262=\"DWORD\",I262=\"DINT\"),F261+4+MOD(F261,4),F261+4)),(IF(OR(I262=\"REAL\",I262=\"DWORD\",I262=\"DINT\"),F261+4+MOD(F261,4),F261+2)))&\".0\"","v":"102.0"},null,"验证通过","BOOL",{"$f":"A262&D262&\"-\"&E262","v":"照明控制箱B2X0A-启停控制"},{"$f":"B262&VLOOKUP(A262,List!$B$3:$D$445,2,FALSE)&D262&\"_\"&VLOOKUP(E262,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0A_C"},"LLCBB2X0A_C AT%M102.0 :BOOL; (*照明控制箱B2X0A-启停控制*)","LLCBB2X0A_C             AT%M102.0      :BOOL; (*照明控制箱B2X0A-启停控制*)"]
["照明控制箱","L","M","B1X0A","启停控制","104.0",null,"验证通过","BOOL","照明控制箱B1X0A-启停控制",{"$f":"B263&VLOOKUP(A263,List!$B$3:$D$445,2,FALSE)&D263&\"_\"&VLOOKUP(E263,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0A_C"},"LLCBB1X0A_C AT%M104.0 :BOOL; (*照明控制箱B1X0A-启停控制*)","LLCBB1X0A_C             AT%M104.0      :BOOL; (*照明控制箱B1X0A-启停控制*)"]
["照明控制箱","L","M","01X0A","启停控制","106.0",null,"验证通过","BOOL","照明控制箱01X0A-启停控制",{"$f":"B264&VLOOKUP(A264,List!$B$3:$D$445,2,FALSE)&D264&\"_\"&VLOOKUP(E264,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0A_C"},"LLCB01X0A_C AT%M106.0 :BOOL; (*照明控制箱01X0A-启停控制*)","LLCB01X0A_C             AT%M106.0      :BOOL; (*照明控制箱01X0A-启停控制*)"]
["照明控制箱","L","M","02X0A","启停控制","108.0",null,"验证通过","BOOL","照明控制箱02X0A-启停控制",{"$f":"B265&VLOOKUP(A265,List!$B$3:$D$445,2,FALSE)&D265&\"_\"&VLOOKUP(E265,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0A_C"},"LLCB02X0A_C AT%M108.0 :BOOL; (*照明控制箱02X0A-启停控制*)","LLCB02X0A_C             AT%M108.0      :BOOL; (*照明控制箱02X0A-启停控制*)"]
["照明控制箱","L","M","03X0A","启停控制","110.0",null,"验证通过","BOOL","照明控制箱03X0A-启停控制",{"$f":"B266&VLOOKUP(A266,List!$B$3:$D$445,2,FALSE)&D266&\"_\"&VLOOKUP(E266,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0A_C"},"LLCB03X0A_C AT%M110.0 :BOOL; (*照明控制箱03X0A-启停控制*)","LLCB03X0A_C             AT%M110.0      :BOOL; (*照明控制箱03X0A-启停控制*)"]
["照明控制箱","L","M","04X0A","启停控制","112.0",null,"验证通过","BOOL","照明控制箱04X0A-启停控制",{"$f":"B267&VLOOKUP(A267,List!$B$3:$D$445,2,FALSE)&D267&\"_\"&VLOOKUP(E267,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0A_C"},"LLCB04X0A_C AT%M112.0 :BOOL; (*照明控制箱04X0A-启停控制*)","LLCB04X0A_C             AT%M112.0      :BOOL; (*照明控制箱04X0A-启停控制*)"]
["照明控制箱","L","M","05X0A","启停控制","114.0",null,"验证通过","BOOL","照明控制箱05X0A-启停控制",{"$f":"B268&VLOOKUP(A268,List!$B$3:$D$445,2,FALSE)&D268&\"_\"&VLOOKUP(E268,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0A_C"},"LLCB05X0A_C AT%M114.0 :BOOL; (*照明控制箱05X0A-启停控制*)","LLCB05X0A_C             AT%M114.0      :BOOL; (*照明控制箱05X0A-启停控制*)"]
["照明控制箱","L","M","06X0A","启停控制","116.0",null,"验证通过","BOOL","照明控制箱06X0A-启停控制",{"$f":"B269&VLOOKUP(A269,List!$B$3:$D$445,2,FALSE)&D269&\"_\"&VLOOKUP(E269,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0A_C"},"LLCB06X0A_C AT%M116.0 :BOOL; (*照明控制箱06X0A-启停控制*)","LLCB06X0A_C             AT%M116.0      :BOOL; (*照明控制箱06X0A-启停控制*)"]
["照明控制箱","L","M","07X0A","启停控制","118.0",null,{"$f":"IF((IF(OR(I270=\"INT\",I270=\"WORD\",I270=\"BOOL\"),MOD(F270,2),MOD(F270,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A270&D270&\"-\"&E270","v":"照明控制箱07X0A-启停控制"},{"$f":"B270&VLOOKUP(A270,List!$B$3:$D$445,2,FALSE)&D270&\"_\"&VLOOKUP(E270,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0A_C"},{"$f":"K270&\" \"&\"AT%\"&C270&F270&\" \"&\":\"&I270&\";\"&\" \"&\"(*\"&J270&\"*)\"","v":"LLCB07X0A_C AT%M118.0 :BOOL; (*照明控制箱07X0A-启停控制*)"},{"$f":"REPLACE(REPLACE(L270,SEARCH(\"AT%\",L270),,REPT(\" \",25-SEARCH(\"AT%\",L270))),SEARCH(\":\",REPLACE(L270,SEARCH(\"AT%\",L270),,REPT(\" \",25-SEARCH(\"AT%\",L270)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L270,SEARCH(\"AT%\",L270),,REPT(\" \",25-SEARCH(\"AT%\",L270))))))","v":"LLCB07X0A_C             AT%M118.0      :BOOL; (*照明控制箱07X0A-启停控制*)"}]
["照明控制箱","L","M","08X0A","启停控制","120.0",null,"验证通过","BOOL","照明控制箱08X0A-启停控制",{"$f":"B271&VLOOKUP(A271,List!$B$3:$D$445,2,FALSE)&D271&\"_\"&VLOOKUP(E271,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0A_C"},"LLCB08X0A_C AT%M120.0 :BOOL; (*照明控制箱08X0A-启停控制*)","LLCB08X0A_C             AT%M120.0      :BOOL; (*照明控制箱08X0A-启停控制*)"]
["照明控制箱","L","M","B3X0B","启停控制","122.0",null,"验证通过","BOOL","照明控制箱B3X0B-启停控制",{"$f":"B272&VLOOKUP(A272,List!$B$3:$D$445,2,FALSE)&D272&\"_\"&VLOOKUP(E272,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0B_C"},"LLCBB3X0B_C AT%M122.0 :BOOL; (*照明控制箱B3X0B-启停控制*)","LLCBB3X0B_C             AT%M122.0      :BOOL; (*照明控制箱B3X0B-启停控制*)"]
["照明控制箱","L","M","B2X0B","启停控制","124.0",null,"验证通过","BOOL","照明控制箱B2X0B-启停控制",{"$f":"B273&VLOOKUP(A273,List!$B$3:$D$445,2,FALSE)&D273&\"_\"&VLOOKUP(E273,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0B_C"},"LLCBB2X0B_C AT%M124.0 :BOOL; (*照明控制箱B2X0B-启停控制*)","LLCBB2X0B_C             AT%M124.0      :BOOL; (*照明控制箱B2X0B-启停控制*)"]
["照明控制箱","L","M","B1X0B","启停控制","126.0",null,"验证通过","BOOL","照明控制箱B1X0B-启停控制",{"$f":"B274&VLOOKUP(A274,List!$B$3:$D$445,2,FALSE)&D274&\"_\"&VLOOKUP(E274,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0B_C"},"LLCBB1X0B_C AT%M126.0 :BOOL; (*照明控制箱B1X0B-启停控制*)","LLCBB1X0B_C             AT%M126.0      :BOOL; (*照明控制箱B1X0B-启停控制*)"]
["照明控制箱","L","M","01X0B","启停控制","128.0",null,"验证通过","BOOL","照明控制箱01X0B-启停控制",{"$f":"B275&VLOOKUP(A275,List!$B$3:$D$445,2,FALSE)&D275&\"_\"&VLOOKUP(E275,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0B_C"},"LLCB01X0B_C AT%M128.0 :BOOL; (*照明控制箱01X0B-启停控制*)","LLCB01X0B_C             AT%M128.0      :BOOL; (*照明控制箱01X0B-启停控制*)"]
["照明控制箱","L","M","02X0B","启停控制","130.0",null,"验证通过","BOOL","照明控制箱02X0B-启停控制",{"$f":"B276&VLOOKUP(A276,List!$B$3:$D$445,2,FALSE)&D276&\"_\"&VLOOKUP(E276,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0B_C"},"LLCB02X0B_C AT%M130.0 :BOOL; (*照明控制箱02X0B-启停控制*)","LLCB02X0B_C             AT%M130.0      :BOOL; (*照明控制箱02X0B-启停控制*)"]
["照明控制箱","L","M","03X0B","启停控制","132.0",null,"验证通过","BOOL","照明控制箱03X0B-启停控制",{"$f":"B277&VLOOKUP(A277,List!$B$3:$D$445,2,FALSE)&D277&\"_\"&VLOOKUP(E277,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0B_C"},"LLCB03X0B_C AT%M132.0 :BOOL; (*照明控制箱03X0B-启停控制*)","LLCB03X0B_C             AT%M132.0      :BOOL; (*照明控制箱03X0B-启停控制*)"]
["照明控制箱","L","M","04X0B","启停控制","134.0",null,"验证通过","BOOL","照明控制箱04X0B-启停控制",{"$f":"B278&VLOOKUP(A278,List!$B$3:$D$445,2,FALSE)&D278&\"_\"&VLOOKUP(E278,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0B_C"},"LLCB04X0B_C AT%M134.0 :BOOL; (*照明控制箱04X0B-启停控制*)","LLCB04X0B_C             AT%M134.0      :BOOL; (*照明控制箱04X0B-启停控制*)"]
["照明控制箱","L","M","05X0B","启停控制","136.0",null,"验证通过","BOOL","照明控制箱05X0B-启停控制",{"$f":"B279&VLOOKUP(A279,List!$B$3:$D$445,2,FALSE)&D279&\"_\"&VLOOKUP(E279,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0B_C"},"LLCB05X0B_C AT%M136.0 :BOOL; (*照明控制箱05X0B-启停控制*)","LLCB05X0B_C             AT%M136.0      :BOOL; (*照明控制箱05X0B-启停控制*)"]
["照明控制箱","L","M","06X0B","启停控制","138.0",null,"验证通过","BOOL","照明控制箱06X0B-启停控制",{"$f":"B280&VLOOKUP(A280,List!$B$3:$D$445,2,FALSE)&D280&\"_\"&VLOOKUP(E280,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0B_C"},"LLCB06X0B_C AT%M138.0 :BOOL; (*照明控制箱06X0B-启停控制*)","LLCB06X0B_C             AT%M138.0      :BOOL; (*照明控制箱06X0B-启停控制*)"]
["照明控制箱","L","M","07X0B","启停控制","140.0",null,{"$f":"IF((IF(OR(I281=\"INT\",I281=\"WORD\",I281=\"BOOL\"),MOD(F281,2),MOD(F281,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A281&D281&\"-\"&E281","v":"照明控制箱07X0B-启停控制"},{"$f":"B281&VLOOKUP(A281,List!$B$3:$D$445,2,FALSE)&D281&\"_\"&VLOOKUP(E281,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0B_C"},{"$f":"K281&\" \"&\"AT%\"&C281&F281&\" \"&\":\"&I281&\";\"&\" \"&\"(*\"&J281&\"*)\"","v":"LLCB07X0B_C AT%M140.0 :BOOL; (*照明控制箱07X0B-启停控制*)"},{"$f":"REPLACE(REPLACE(L281,SEARCH(\"AT%\",L281),,REPT(\" \",25-SEARCH(\"AT%\",L281))),SEARCH(\":\",REPLACE(L281,SEARCH(\"AT%\",L281),,REPT(\" \",25-SEARCH(\"AT%\",L281)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L281,SEARCH(\"AT%\",L281),,REPT(\" \",25-SEARCH(\"AT%\",L281))))))","v":"LLCB07X0B_C             AT%M140.0      :BOOL; (*照明控制箱07X0B-启停控制*)"}]
["照明控制箱","L","M","08X0B","启停控制","142.0",null,"验证通过","BOOL","照明控制箱08X0B-启停控制",{"$f":"B282&VLOOKUP(A282,List!$B$3:$D$445,2,FALSE)&D282&\"_\"&VLOOKUP(E282,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0B_C"},"LLCB08X0B_C AT%M142.0 :BOOL; (*照明控制箱08X0B-启停控制*)","LLCB08X0B_C             AT%M142.0      :BOOL; (*照明控制箱08X0B-启停控制*)"]
["照明控制箱","L","M","B3X0C","启停控制","144.0",null,"验证通过","BOOL","照明控制箱B3X0C-启停控制",{"$f":"B283&VLOOKUP(A283,List!$B$3:$D$445,2,FALSE)&D283&\"_\"&VLOOKUP(E283,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0C_C"},"LLCBB3X0C_C AT%M144.0 :BOOL; (*照明控制箱B3X0C-启停控制*)","LLCBB3X0C_C             AT%M144.0      :BOOL; (*照明控制箱B3X0C-启停控制*)"]
["照明控制箱","L","M","B2X0C","启停控制","146.0",null,"验证通过","BOOL","照明控制箱B2X0C-启停控制",{"$f":"B284&VLOOKUP(A284,List!$B$3:$D$445,2,FALSE)&D284&\"_\"&VLOOKUP(E284,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0C_C"},"LLCBB2X0C_C AT%M146.0 :BOOL; (*照明控制箱B2X0C-启停控制*)","LLCBB2X0C_C             AT%M146.0      :BOOL; (*照明控制箱B2X0C-启停控制*)"]
["照明控制箱","L","M","B1X0C","启停控制","148.0",null,"验证通过","BOOL","照明控制箱B1X0C-启停控制",{"$f":"B285&VLOOKUP(A285,List!$B$3:$D$445,2,FALSE)&D285&\"_\"&VLOOKUP(E285,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0C_C"},"LLCBB1X0C_C AT%M148.0 :BOOL; (*照明控制箱B1X0C-启停控制*)","LLCBB1X0C_C             AT%M148.0      :BOOL; (*照明控制箱B1X0C-启停控制*)"]
["照明控制箱","L","M","01X0C","启停控制","150.0",null,"验证通过","BOOL","照明控制箱01X0C-启停控制",{"$f":"B286&VLOOKUP(A286,List!$B$3:$D$445,2,FALSE)&D286&\"_\"&VLOOKUP(E286,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0C_C"},"LLCB01X0C_C AT%M150.0 :BOOL; (*照明控制箱01X0C-启停控制*)","LLCB01X0C_C             AT%M150.0      :BOOL; (*照明控制箱01X0C-启停控制*)"]
["照明控制箱","L","M","02X0C","启停控制","152.0",null,"验证通过","BOOL","照明控制箱02X0C-启停控制",{"$f":"B287&VLOOKUP(A287,List!$B$3:$D$445,2,FALSE)&D287&\"_\"&VLOOKUP(E287,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0C_C"},"LLCB02X0C_C AT%M152.0 :BOOL; (*照明控制箱02X0C-启停控制*)","LLCB02X0C_C             AT%M152.0      :BOOL; (*照明控制箱02X0C-启停控制*)"]
["照明控制箱","L","M","03X0C","启停控制","154.0",null,"验证通过","BOOL","照明控制箱03X0C-启停控制",{"$f":"B288&VLOOKUP(A288,List!$B$3:$D$445,2,FALSE)&D288&\"_\"&VLOOKUP(E288,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0C_C"},"LLCB03X0C_C AT%M154.0 :BOOL; (*照明控制箱03X0C-启停控制*)","LLCB03X0C_C             AT%M154.0      :BOOL; (*照明控制箱03X0C-启停控制*)"]
["照明控制箱","L","M","04X0C","启停控制","156.0",null,"验证通过","BOOL","照明控制箱04X0C-启停控制",{"$f":"B289&VLOOKUP(A289,List!$B$3:$D$445,2,FALSE)&D289&\"_\"&VLOOKUP(E289,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0C_C"},"LLCB04X0C_C AT%M156.0 :BOOL; (*照明控制箱04X0C-启停控制*)","LLCB04X0C_C             AT%M156.0      :BOOL; (*照明控制箱04X0C-启停控制*)"]
["照明控制箱","L","M","05X0C","启停控制","158.0",null,"验证通过","BOOL","照明控制箱05X0C-启停控制",{"$f":"B290&VLOOKUP(A290,List!$B$3:$D$445,2,FALSE)&D290&\"_\"&VLOOKUP(E290,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0C_C"},"LLCB05X0C_C AT%M158.0 :BOOL; (*照明控制箱05X0C-启停控制*)","LLCB05X0C_C             AT%M158.0      :BOOL; (*照明控制箱05X0C-启停控制*)"]
["照明控制箱","L","M","06X0C","启停控制","160.0",null,"验证通过","BOOL","照明控制箱06X0C-启停控制",{"$f":"B291&VLOOKUP(A291,List!$B$3:$D$445,2,FALSE)&D291&\"_\"&VLOOKUP(E291,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0C_C"},"LLCB06X0C_C AT%M160.0 :BOOL; (*照明控制箱06X0C-启停控制*)","LLCB06X0C_C             AT%M160.0      :BOOL; (*照明控制箱06X0C-启停控制*)"]
["照明控制箱","L","M","07X0C","启停控制","162.0",null,{"$f":"IF((IF(OR(I292=\"INT\",I292=\"WORD\",I292=\"BOOL\"),MOD(F292,2),MOD(F292,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A292&D292&\"-\"&E292","v":"照明控制箱07X0C-启停控制"},{"$f":"B292&VLOOKUP(A292,List!$B$3:$D$445,2,FALSE)&D292&\"_\"&VLOOKUP(E292,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0C_C"},{"$f":"K292&\" \"&\"AT%\"&C292&F292&\" \"&\":\"&I292&\";\"&\" \"&\"(*\"&J292&\"*)\"","v":"LLCB07X0C_C AT%M162.0 :BOOL; (*照明控制箱07X0C-启停控制*)"},{"$f":"REPLACE(REPLACE(L292,SEARCH(\"AT%\",L292),,REPT(\" \",25-SEARCH(\"AT%\",L292))),SEARCH(\":\",REPLACE(L292,SEARCH(\"AT%\",L292),,REPT(\" \",25-SEARCH(\"AT%\",L292)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L292,SEARCH(\"AT%\",L292),,REPT(\" \",25-SEARCH(\"AT%\",L292))))))","v":"LLCB07X0C_C             AT%M162.0      :BOOL; (*照明控制箱07X0C-启停控制*)"}]
["照明控制箱","L","M","08X0C","启停控制","164.0",null,"验证通过","BOOL","照明控制箱08X0C-启停控制",{"$f":"B293&VLOOKUP(A293,List!$B$3:$D$445,2,FALSE)&D293&\"_\"&VLOOKUP(E293,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0C_C"},"LLCB08X0C_C AT%M164.0 :BOOL; (*照明控制箱08X0C-启停控制*)","LLCB08X0C_C             AT%M164.0      :BOOL; (*照明控制箱08X0C-启停控制*)"]
["照明控制箱","L","M","B3X0D","启停控制","166.0",null,"验证通过","BOOL","照明控制箱B3X0D-启停控制",{"$f":"B294&VLOOKUP(A294,List!$B$3:$D$445,2,FALSE)&D294&\"_\"&VLOOKUP(E294,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0D_C"},"LLCBB3X0D_C AT%M166.0 :BOOL; (*照明控制箱B3X0D-启停控制*)","LLCBB3X0D_C             AT%M166.0      :BOOL; (*照明控制箱B3X0D-启停控制*)"]
["照明控制箱","L","M","B2X0D","启停控制","168.0",null,"验证通过","BOOL","照明控制箱B2X0D-启停控制",{"$f":"B295&VLOOKUP(A295,List!$B$3:$D$445,2,FALSE)&D295&\"_\"&VLOOKUP(E295,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0D_C"},"LLCBB2X0D_C AT%M168.0 :BOOL; (*照明控制箱B2X0D-启停控制*)","LLCBB2X0D_C             AT%M168.0      :BOOL; (*照明控制箱B2X0D-启停控制*)"]
["照明控制箱","L","M","B1X0D","启停控制","170.0",null,"验证通过","BOOL","照明控制箱B1X0D-启停控制",{"$f":"B296&VLOOKUP(A296,List!$B$3:$D$445,2,FALSE)&D296&\"_\"&VLOOKUP(E296,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0D_C"},"LLCBB1X0D_C AT%M170.0 :BOOL; (*照明控制箱B1X0D-启停控制*)","LLCBB1X0D_C             AT%M170.0      :BOOL; (*照明控制箱B1X0D-启停控制*)"]
["照明控制箱","L","M","01X0D","启停控制","172.0",null,"验证通过","BOOL","照明控制箱01X0D-启停控制",{"$f":"B297&VLOOKUP(A297,List!$B$3:$D$445,2,FALSE)&D297&\"_\"&VLOOKUP(E297,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0D_C"},"LLCB01X0D_C AT%M172.0 :BOOL; (*照明控制箱01X0D-启停控制*)","LLCB01X0D_C             AT%M172.0      :BOOL; (*照明控制箱01X0D-启停控制*)"]
["照明控制箱","L","M","02X0D","启停控制","174.0",null,"验证通过","BOOL","照明控制箱02X0D-启停控制",{"$f":"B298&VLOOKUP(A298,List!$B$3:$D$445,2,FALSE)&D298&\"_\"&VLOOKUP(E298,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0D_C"},"LLCB02X0D_C AT%M174.0 :BOOL; (*照明控制箱02X0D-启停控制*)","LLCB02X0D_C             AT%M174.0      :BOOL; (*照明控制箱02X0D-启停控制*)"]
["照明控制箱","L","M","03X0D","启停控制","176.0",null,"验证通过","BOOL","照明控制箱03X0D-启停控制",{"$f":"B299&VLOOKUP(A299,List!$B$3:$D$445,2,FALSE)&D299&\"_\"&VLOOKUP(E299,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0D_C"},"LLCB03X0D_C AT%M176.0 :BOOL; (*照明控制箱03X0D-启停控制*)","LLCB03X0D_C             AT%M176.0      :BOOL; (*照明控制箱03X0D-启停控制*)"]
["照明控制箱","L","M","04X0D","启停控制","178.0",null,"验证通过","BOOL","照明控制箱04X0D-启停控制",{"$f":"B300&VLOOKUP(A300,List!$B$3:$D$445,2,FALSE)&D300&\"_\"&VLOOKUP(E300,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0D_C"},"LLCB04X0D_C AT%M178.0 :BOOL; (*照明控制箱04X0D-启停控制*)","LLCB04X0D_C             AT%M178.0      :BOOL; (*照明控制箱04X0D-启停控制*)"]
["照明控制箱","L","M","05X0D","启停控制","180.0",null,"验证通过","BOOL","照明控制箱05X0D-启停控制",{"$f":"B301&VLOOKUP(A301,List!$B$3:$D$445,2,FALSE)&D301&\"_\"&VLOOKUP(E301,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0D_C"},"LLCB05X0D_C AT%M180.0 :BOOL; (*照明控制箱05X0D-启停控制*)","LLCB05X0D_C             AT%M180.0      :BOOL; (*照明控制箱05X0D-启停控制*)"]
["照明控制箱","L","M","06X0D","启停控制","182.0",null,"验证通过","BOOL","照明控制箱06X0D-启停控制",{"$f":"B302&VLOOKUP(A302,List!$B$3:$D$445,2,FALSE)&D302&\"_\"&VLOOKUP(E302,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0D_C"},"LLCB06X0D_C AT%M182.0 :BOOL; (*照明控制箱06X0D-启停控制*)","LLCB06X0D_C             AT%M182.0      :BOOL; (*照明控制箱06X0D-启停控制*)"]
["照明控制箱","L","M","07X0D","启停控制","184.0",null,{"$f":"IF((IF(OR(I303=\"INT\",I303=\"WORD\",I303=\"BOOL\"),MOD(F303,2),MOD(F303,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A303&D303&\"-\"&E303","v":"照明控制箱07X0D-启停控制"},{"$f":"B303&VLOOKUP(A303,List!$B$3:$D$445,2,FALSE)&D303&\"_\"&VLOOKUP(E303,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0D_C"},{"$f":"K303&\" \"&\"AT%\"&C303&F303&\" \"&\":\"&I303&\";\"&\" \"&\"(*\"&J303&\"*)\"","v":"LLCB07X0D_C AT%M184.0 :BOOL; (*照明控制箱07X0D-启停控制*)"},{"$f":"REPLACE(REPLACE(L303,SEARCH(\"AT%\",L303),,REPT(\" \",25-SEARCH(\"AT%\",L303))),SEARCH(\":\",REPLACE(L303,SEARCH(\"AT%\",L303),,REPT(\" \",25-SEARCH(\"AT%\",L303)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L303,SEARCH(\"AT%\",L303),,REPT(\" \",25-SEARCH(\"AT%\",L303))))))","v":"LLCB07X0D_C             AT%M184.0      :BOOL; (*照明控制箱07X0D-启停控制*)"}]
["照明控制箱","L","M","08X0D","启停控制","186.0",null,"验证通过","BOOL","照明控制箱08X0D-启停控制",{"$f":"B304&VLOOKUP(A304,List!$B$3:$D$445,2,FALSE)&D304&\"_\"&VLOOKUP(E304,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0D_C"},"LLCB08X0D_C AT%M186.0 :BOOL; (*照明控制箱08X0D-启停控制*)","LLCB08X0D_C             AT%M186.0      :BOOL; (*照明控制箱08X0D-启停控制*)"]
["照明控制箱","L","M","B3X0E","启停控制","188.0",null,"验证通过","BOOL","照明控制箱B3X0E-启停控制",{"$f":"B305&VLOOKUP(A305,List!$B$3:$D$445,2,FALSE)&D305&\"_\"&VLOOKUP(E305,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0E_C"},"LLCBB3X0E_C AT%M188.0 :BOOL; (*照明控制箱B3X0E-启停控制*)","LLCBB3X0E_C             AT%M188.0      :BOOL; (*照明控制箱B3X0E-启停控制*)"]
["照明控制箱","L","M","B2X0E","启停控制","190.0",null,"验证通过","BOOL","照明控制箱B2X0E-启停控制",{"$f":"B306&VLOOKUP(A306,List!$B$3:$D$445,2,FALSE)&D306&\"_\"&VLOOKUP(E306,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0E_C"},"LLCBB2X0E_C AT%M190.0 :BOOL; (*照明控制箱B2X0E-启停控制*)","LLCBB2X0E_C             AT%M190.0      :BOOL; (*照明控制箱B2X0E-启停控制*)"]
["照明控制箱","L","M","B1X0E","启停控制","192.0",null,"验证通过","BOOL","照明控制箱B1X0E-启停控制",{"$f":"B307&VLOOKUP(A307,List!$B$3:$D$445,2,FALSE)&D307&\"_\"&VLOOKUP(E307,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0E_C"},"LLCBB1X0E_C AT%M192.0 :BOOL; (*照明控制箱B1X0E-启停控制*)","LLCBB1X0E_C             AT%M192.0      :BOOL; (*照明控制箱B1X0E-启停控制*)"]
["照明控制箱","L","M","01X0E","启停控制","194.0",null,"验证通过","BOOL","照明控制箱01X0E-启停控制",{"$f":"B308&VLOOKUP(A308,List!$B$3:$D$445,2,FALSE)&D308&\"_\"&VLOOKUP(E308,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0E_C"},"LLCB01X0E_C AT%M194.0 :BOOL; (*照明控制箱01X0E-启停控制*)","LLCB01X0E_C             AT%M194.0      :BOOL; (*照明控制箱01X0E-启停控制*)"]
["照明控制箱","L","M","02X0E","启停控制","196.0",null,"验证通过","BOOL","照明控制箱02X0E-启停控制",{"$f":"B309&VLOOKUP(A309,List!$B$3:$D$445,2,FALSE)&D309&\"_\"&VLOOKUP(E309,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0E_C"},"LLCB02X0E_C AT%M196.0 :BOOL; (*照明控制箱02X0E-启停控制*)","LLCB02X0E_C             AT%M196.0      :BOOL; (*照明控制箱02X0E-启停控制*)"]
["照明控制箱","L","M","03X0E","启停控制","198.0",null,"验证通过","BOOL","照明控制箱03X0E-启停控制",{"$f":"B310&VLOOKUP(A310,List!$B$3:$D$445,2,FALSE)&D310&\"_\"&VLOOKUP(E310,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0E_C"},"LLCB03X0E_C AT%M198.0 :BOOL; (*照明控制箱03X0E-启停控制*)","LLCB03X0E_C             AT%M198.0      :BOOL; (*照明控制箱03X0E-启停控制*)"]
["照明控制箱","L","M","04X0E","启停控制","200.0",null,"验证通过","BOOL","照明控制箱04X0E-启停控制",{"$f":"B311&VLOOKUP(A311,List!$B$3:$D$445,2,FALSE)&D311&\"_\"&VLOOKUP(E311,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0E_C"},"LLCB04X0E_C AT%M200.0 :BOOL; (*照明控制箱04X0E-启停控制*)","LLCB04X0E_C             AT%M200.0      :BOOL; (*照明控制箱04X0E-启停控制*)"]
["照明控制箱","L","M","05X0E","启停控制","202.0",null,"验证通过","BOOL","照明控制箱05X0E-启停控制",{"$f":"B312&VLOOKUP(A312,List!$B$3:$D$445,2,FALSE)&D312&\"_\"&VLOOKUP(E312,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0E_C"},"LLCB05X0E_C AT%M202.0 :BOOL; (*照明控制箱05X0E-启停控制*)","LLCB05X0E_C             AT%M202.0      :BOOL; (*照明控制箱05X0E-启停控制*)"]
["照明控制箱","L","M","06X0E","启停控制","204.0",null,"验证通过","BOOL","照明控制箱06X0E-启停控制",{"$f":"B313&VLOOKUP(A313,List!$B$3:$D$445,2,FALSE)&D313&\"_\"&VLOOKUP(E313,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0E_C"},"LLCB06X0E_C AT%M204.0 :BOOL; (*照明控制箱06X0E-启停控制*)","LLCB06X0E_C             AT%M204.0      :BOOL; (*照明控制箱06X0E-启停控制*)"]
["照明控制箱","L","M","07X0E","启停控制","206.0",null,"验证通过","BOOL","照明控制箱07X0E-启停控制",{"$f":"B314&VLOOKUP(A314,List!$B$3:$D$445,2,FALSE)&D314&\"_\"&VLOOKUP(E314,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0E_C"},"LLCB07X0E_C AT%M206.0 :BOOL; (*照明控制箱07X0E-启停控制*)","LLCB07X0E_C             AT%M206.0      :BOOL; (*照明控制箱07X0E-启停控制*)"]
["照明控制箱","L","M","08X0E","启停控制","208.0",null,"验证通过","BOOL","照明控制箱08X0E-启停控制",{"$f":"B315&VLOOKUP(A315,List!$B$3:$D$445,2,FALSE)&D315&\"_\"&VLOOKUP(E315,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0E_C"},"LLCB08X0E_C AT%M208.0 :BOOL; (*照明控制箱08X0E-启停控制*)","LLCB08X0E_C             AT%M208.0      :BOOL; (*照明控制箱08X0E-启停控制*)"]
["照明控制箱","L","M","B3X0F","启停控制","210.0",null,"验证通过","BOOL","照明控制箱B3X0F-启停控制",{"$f":"B316&VLOOKUP(A316,List!$B$3:$D$445,2,FALSE)&D316&\"_\"&VLOOKUP(E316,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0F_C"},"LLCBB3X0F_C AT%M210.0 :BOOL; (*照明控制箱B3X0F-启停控制*)","LLCBB3X0F_C             AT%M210.0      :BOOL; (*照明控制箱B3X0F-启停控制*)"]
["照明控制箱","L","M","B2X0F","启停控制","212.0",null,"验证通过","BOOL","照明控制箱B2X0F-启停控制",{"$f":"B317&VLOOKUP(A317,List!$B$3:$D$445,2,FALSE)&D317&\"_\"&VLOOKUP(E317,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0F_C"},"LLCBB2X0F_C AT%M212.0 :BOOL; (*照明控制箱B2X0F-启停控制*)","LLCBB2X0F_C             AT%M212.0      :BOOL; (*照明控制箱B2X0F-启停控制*)"]
["照明控制箱","L","M","B1X0F","启停控制","214.0",null,"验证通过","BOOL","照明控制箱B1X0F-启停控制",{"$f":"B318&VLOOKUP(A318,List!$B$3:$D$445,2,FALSE)&D318&\"_\"&VLOOKUP(E318,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0F_C"},"LLCBB1X0F_C AT%M214.0 :BOOL; (*照明控制箱B1X0F-启停控制*)","LLCBB1X0F_C             AT%M214.0      :BOOL; (*照明控制箱B1X0F-启停控制*)"]
["照明控制箱","L","M","01X0F","启停控制","216.0",null,"验证通过","BOOL","照明控制箱01X0F-启停控制",{"$f":"B319&VLOOKUP(A319,List!$B$3:$D$445,2,FALSE)&D319&\"_\"&VLOOKUP(E319,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0F_C"},"LLCB01X0F_C AT%M216.0 :BOOL; (*照明控制箱01X0F-启停控制*)","LLCB01X0F_C             AT%M216.0      :BOOL; (*照明控制箱01X0F-启停控制*)"]
["照明控制箱","L","M","02X0F","启停控制","218.0",null,"验证通过","BOOL","照明控制箱02X0F-启停控制",{"$f":"B320&VLOOKUP(A320,List!$B$3:$D$445,2,FALSE)&D320&\"_\"&VLOOKUP(E320,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0F_C"},"LLCB02X0F_C AT%M218.0 :BOOL; (*照明控制箱02X0F-启停控制*)","LLCB02X0F_C             AT%M218.0      :BOOL; (*照明控制箱02X0F-启停控制*)"]
["照明控制箱","L","M","03X0F","启停控制","220.0",null,"验证通过","BOOL","照明控制箱03X0F-启停控制",{"$f":"B321&VLOOKUP(A321,List!$B$3:$D$445,2,FALSE)&D321&\"_\"&VLOOKUP(E321,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0F_C"},"LLCB03X0F_C AT%M220.0 :BOOL; (*照明控制箱03X0F-启停控制*)","LLCB03X0F_C             AT%M220.0      :BOOL; (*照明控制箱03X0F-启停控制*)"]
["照明控制箱","L","M","04X0F","启停控制","222.0",null,"验证通过","BOOL","照明控制箱04X0F-启停控制",{"$f":"B322&VLOOKUP(A322,List!$B$3:$D$445,2,FALSE)&D322&\"_\"&VLOOKUP(E322,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0F_C"},"LLCB04X0F_C AT%M222.0 :BOOL; (*照明控制箱04X0F-启停控制*)","LLCB04X0F_C             AT%M222.0      :BOOL; (*照明控制箱04X0F-启停控制*)"]
["照明控制箱","L","M","05X0F","启停控制","224.0",null,"验证通过","BOOL","照明控制箱05X0F-启停控制",{"$f":"B323&VLOOKUP(A323,List!$B$3:$D$445,2,FALSE)&D323&\"_\"&VLOOKUP(E323,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0F_C"},"LLCB05X0F_C AT%M224.0 :BOOL; (*照明控制箱05X0F-启停控制*)","LLCB05X0F_C             AT%M224.0      :BOOL; (*照明控制箱05X0F-启停控制*)"]
["照明控制箱","L","M","06X0F","启停控制","226.0",null,"验证通过","BOOL","照明控制箱06X0F-启停控制",{"$f":"B324&VLOOKUP(A324,List!$B$3:$D$445,2,FALSE)&D324&\"_\"&VLOOKUP(E324,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0F_C"},"LLCB06X0F_C AT%M226.0 :BOOL; (*照明控制箱06X0F-启停控制*)","LLCB06X0F_C             AT%M226.0      :BOOL; (*照明控制箱06X0F-启停控制*)"]
["照明控制箱","L","M","07X0F","启停控制","228.0",null,{"$f":"IF((IF(OR(I325=\"INT\",I325=\"WORD\",I325=\"BOOL\"),MOD(F325,2),MOD(F325,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A325&D325&\"-\"&E325","v":"照明控制箱07X0F-启停控制"},{"$f":"B325&VLOOKUP(A325,List!$B$3:$D$445,2,FALSE)&D325&\"_\"&VLOOKUP(E325,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0F_C"},{"$f":"K325&\" \"&\"AT%\"&C325&F325&\" \"&\":\"&I325&\";\"&\" \"&\"(*\"&J325&\"*)\"","v":"LLCB07X0F_C AT%M228.0 :BOOL; (*照明控制箱07X0F-启停控制*)"},{"$f":"REPLACE(REPLACE(L325,SEARCH(\"AT%\",L325),,REPT(\" \",25-SEARCH(\"AT%\",L325))),SEARCH(\":\",REPLACE(L325,SEARCH(\"AT%\",L325),,REPT(\" \",25-SEARCH(\"AT%\",L325)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L325,SEARCH(\"AT%\",L325),,REPT(\" \",25-SEARCH(\"AT%\",L325))))))","v":"LLCB07X0F_C             AT%M228.0      :BOOL; (*照明控制箱07X0F-启停控制*)"}]
["照明控制箱","L","M","08X0F","启停控制","230.0",null,"验证通过","BOOL","照明控制箱08X0F-启停控制",{"$f":"B326&VLOOKUP(A326,List!$B$3:$D$445,2,FALSE)&D326&\"_\"&VLOOKUP(E326,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0F_C"},"LLCB08X0F_C AT%M230.0 :BOOL; (*照明控制箱08X0F-启停控制*)","LLCB08X0F_C             AT%M230.0      :BOOL; (*照明控制箱08X0F-启停控制*)"]
["照明控制箱","L","M","B3X0G","启停控制","232.0",null,"验证通过","BOOL","照明控制箱B3X0G-启停控制",{"$f":"B327&VLOOKUP(A327,List!$B$3:$D$445,2,FALSE)&D327&\"_\"&VLOOKUP(E327,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0G_C"},"LLCBB3X0G_C AT%M232.0 :BOOL; (*照明控制箱B3X0G-启停控制*)","LLCBB3X0G_C             AT%M232.0      :BOOL; (*照明控制箱B3X0G-启停控制*)"]
["照明控制箱","L","M","B2X0G","启停控制","234.0",null,"验证通过","BOOL","照明控制箱B2X0G-启停控制",{"$f":"B328&VLOOKUP(A328,List!$B$3:$D$445,2,FALSE)&D328&\"_\"&VLOOKUP(E328,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0G_C"},"LLCBB2X0G_C AT%M234.0 :BOOL; (*照明控制箱B2X0G-启停控制*)","LLCBB2X0G_C             AT%M234.0      :BOOL; (*照明控制箱B2X0G-启停控制*)"]
["照明控制箱","L","M","B1X0G","启停控制","236.0",null,"验证通过","BOOL","照明控制箱B1X0G-启停控制",{"$f":"B329&VLOOKUP(A329,List!$B$3:$D$445,2,FALSE)&D329&\"_\"&VLOOKUP(E329,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0G_C"},"LLCBB1X0G_C AT%M236.0 :BOOL; (*照明控制箱B1X0G-启停控制*)","LLCBB1X0G_C             AT%M236.0      :BOOL; (*照明控制箱B1X0G-启停控制*)"]
["照明控制箱","L","M","01X0G","启停控制","238.0",null,"验证通过","BOOL","照明控制箱01X0G-启停控制",{"$f":"B330&VLOOKUP(A330,List!$B$3:$D$445,2,FALSE)&D330&\"_\"&VLOOKUP(E330,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0G_C"},"LLCB01X0G_C AT%M238.0 :BOOL; (*照明控制箱01X0G-启停控制*)","LLCB01X0G_C             AT%M238.0      :BOOL; (*照明控制箱01X0G-启停控制*)"]
["照明控制箱","L","M","02X0G","启停控制","240.0",null,"验证通过","BOOL","照明控制箱02X0G-启停控制",{"$f":"B331&VLOOKUP(A331,List!$B$3:$D$445,2,FALSE)&D331&\"_\"&VLOOKUP(E331,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0G_C"},"LLCB02X0G_C AT%M240.0 :BOOL; (*照明控制箱02X0G-启停控制*)","LLCB02X0G_C             AT%M240.0      :BOOL; (*照明控制箱02X0G-启停控制*)"]
["照明控制箱","L","M","03X0G","启停控制","242.0",null,"验证通过","BOOL","照明控制箱03X0G-启停控制",{"$f":"B332&VLOOKUP(A332,List!$B$3:$D$445,2,FALSE)&D332&\"_\"&VLOOKUP(E332,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0G_C"},"LLCB03X0G_C AT%M242.0 :BOOL; (*照明控制箱03X0G-启停控制*)","LLCB03X0G_C             AT%M242.0      :BOOL; (*照明控制箱03X0G-启停控制*)"]
["照明控制箱","L","M","04X0G","启停控制","244.0",null,"验证通过","BOOL","照明控制箱04X0G-启停控制",{"$f":"B333&VLOOKUP(A333,List!$B$3:$D$445,2,FALSE)&D333&\"_\"&VLOOKUP(E333,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0G_C"},"LLCB04X0G_C AT%M244.0 :BOOL; (*照明控制箱04X0G-启停控制*)","LLCB04X0G_C             AT%M244.0      :BOOL; (*照明控制箱04X0G-启停控制*)"]
["照明控制箱","L","M","05X0G","启停控制","246.0",null,"验证通过","BOOL","照明控制箱05X0G-启停控制",{"$f":"B334&VLOOKUP(A334,List!$B$3:$D$445,2,FALSE)&D334&\"_\"&VLOOKUP(E334,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0G_C"},"LLCB05X0G_C AT%M246.0 :BOOL; (*照明控制箱05X0G-启停控制*)","LLCB05X0G_C             AT%M246.0      :BOOL; (*照明控制箱05X0G-启停控制*)"]
["照明控制箱","L","M","06X0G","启停控制","248.0",null,"验证通过","BOOL","照明控制箱06X0G-启停控制",{"$f":"B335&VLOOKUP(A335,List!$B$3:$D$445,2,FALSE)&D335&\"_\"&VLOOKUP(E335,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0G_C"},{"$f":"K335&\" \"&\"AT%\"&C335&F335&\" \"&\":\"&I335&\";\"&\" \"&\"(*\"&J335&\"*)\"","v":"LLCB06X0G_C AT%M248.0 :BOOL; (*照明控制箱06X0G-启停控制*)"},{"$f":"REPLACE(REPLACE(L335,SEARCH(\"AT%\",L335),,REPT(\" \",25-SEARCH(\"AT%\",L335))),SEARCH(\":\",REPLACE(L335,SEARCH(\"AT%\",L335),,REPT(\" \",25-SEARCH(\"AT%\",L335)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L335,SEARCH(\"AT%\",L335),,REPT(\" \",25-SEARCH(\"AT%\",L335))))))","v":"LLCB06X0G_C             AT%M248.0      :BOOL; (*照明控制箱06X0G-启停控制*)"}]
["照明控制箱","L","M","07X0G","启停控制","250.0",null,"验证通过","BOOL","照明控制箱07X0G-启停控制",{"$f":"B336&VLOOKUP(A336,List!$B$3:$D$445,2,FALSE)&D336&\"_\"&VLOOKUP(E336,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0G_C"},"LLCB07X0G_C AT%M250.0 :BOOL; (*照明控制箱07X0G-启停控制*)","LLCB07X0G_C             AT%M250.0      :BOOL; (*照明控制箱07X0G-启停控制*)"]
["照明控制箱","L","M","08X0G","启停控制","252.0",null,"验证通过","BOOL","照明控制箱08X0G-启停控制",{"$f":"B337&VLOOKUP(A337,List!$B$3:$D$445,2,FALSE)&D337&\"_\"&VLOOKUP(E337,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0G_C"},"LLCB08X0G_C AT%M252.0 :BOOL; (*照明控制箱08X0G-启停控制*)","LLCB08X0G_C             AT%M252.0      :BOOL; (*照明控制箱08X0G-启停控制*)"]
["照明控制箱","L","M","B3X0H","启停控制","254.0",null,"验证通过","BOOL","照明控制箱B3X0H-启停控制",{"$f":"B338&VLOOKUP(A338,List!$B$3:$D$445,2,FALSE)&D338&\"_\"&VLOOKUP(E338,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0H_C"},"LLCBB3X0H_C AT%M254.0 :BOOL; (*照明控制箱B3X0H-启停控制*)","LLCBB3X0H_C             AT%M254.0      :BOOL; (*照明控制箱B3X0H-启停控制*)"]
["照明控制箱","L","M","B2X0H","启停控制","256.0",null,"验证通过","BOOL","照明控制箱B2X0H-启停控制",{"$f":"B339&VLOOKUP(A339,List!$B$3:$D$445,2,FALSE)&D339&\"_\"&VLOOKUP(E339,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0H_C"},"LLCBB2X0H_C AT%M256.0 :BOOL; (*照明控制箱B2X0H-启停控制*)","LLCBB2X0H_C             AT%M256.0      :BOOL; (*照明控制箱B2X0H-启停控制*)"]
["照明控制箱","L","M","B1X0H","启停控制",{"$f":"IF(OR(I339=\"REAL\",I339=\"DWORD\",I339=\"DINT\"),(IF(OR(I340=\"REAL\",I340=\"DWORD\",I340=\"DINT\"),F339+4+MOD(F339,4),F339+4)),(IF(OR(I340=\"REAL\",I340=\"DWORD\",I340=\"DINT\"),F339+4+MOD(F339,4),F339+2)))&\".0\"","v":"258.0"},null,"验证通过","BOOL",{"$f":"A340&D340&\"-\"&E340","v":"照明控制箱B1X0H-启停控制"},{"$f":"B340&VLOOKUP(A340,List!$B$3:$D$445,2,FALSE)&D340&\"_\"&VLOOKUP(E340,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0H_C"},"LLCBB1X0H_C AT%M258.0 :BOOL; (*照明控制箱B1X0H-启停控制*)","LLCBB1X0H_C             AT%M258.0      :BOOL; (*照明控制箱B1X0H-启停控制*)"]
["照明控制箱","L","M","01X0H","启停控制","260.0",null,"验证通过","BOOL","照明控制箱01X0H-启停控制",{"$f":"B341&VLOOKUP(A341,List!$B$3:$D$445,2,FALSE)&D341&\"_\"&VLOOKUP(E341,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0H_C"},"LLCB01X0H_C AT%M260.0 :BOOL; (*照明控制箱01X0H-启停控制*)","LLCB01X0H_C             AT%M260.0      :BOOL; (*照明控制箱01X0H-启停控制*)"]
["照明控制箱","L","M","02X0H","启停控制","262.0",null,"验证通过","BOOL","照明控制箱02X0H-启停控制",{"$f":"B342&VLOOKUP(A342,List!$B$3:$D$445,2,FALSE)&D342&\"_\"&VLOOKUP(E342,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0H_C"},"LLCB02X0H_C AT%M262.0 :BOOL; (*照明控制箱02X0H-启停控制*)","LLCB02X0H_C             AT%M262.0      :BOOL; (*照明控制箱02X0H-启停控制*)"]
["照明控制箱","L","M","03X0H","启停控制","264.0",null,"验证通过","BOOL","照明控制箱03X0H-启停控制",{"$f":"B343&VLOOKUP(A343,List!$B$3:$D$445,2,FALSE)&D343&\"_\"&VLOOKUP(E343,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0H_C"},"LLCB03X0H_C AT%M264.0 :BOOL; (*照明控制箱03X0H-启停控制*)","LLCB03X0H_C             AT%M264.0      :BOOL; (*照明控制箱03X0H-启停控制*)"]
["照明控制箱","L","M","04X0H","启停控制","266.0",null,"验证通过","BOOL","照明控制箱04X0H-启停控制",{"$f":"B344&VLOOKUP(A344,List!$B$3:$D$445,2,FALSE)&D344&\"_\"&VLOOKUP(E344,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0H_C"},"LLCB04X0H_C AT%M266.0 :BOOL; (*照明控制箱04X0H-启停控制*)","LLCB04X0H_C             AT%M266.0      :BOOL; (*照明控制箱04X0H-启停控制*)"]
["照明控制箱","L","M","05X0H","启停控制","268.0",null,"验证通过","BOOL","照明控制箱05X0H-启停控制",{"$f":"B345&VLOOKUP(A345,List!$B$3:$D$445,2,FALSE)&D345&\"_\"&VLOOKUP(E345,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0H_C"},"LLCB05X0H_C AT%M268.0 :BOOL; (*照明控制箱05X0H-启停控制*)","LLCB05X0H_C             AT%M268.0      :BOOL; (*照明控制箱05X0H-启停控制*)"]
["照明控制箱","L","M","06X0H","启停控制","270.0",null,"验证通过","BOOL","照明控制箱06X0H-启停控制",{"$f":"B346&VLOOKUP(A346,List!$B$3:$D$445,2,FALSE)&D346&\"_\"&VLOOKUP(E346,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0H_C"},"LLCB06X0H_C AT%M270.0 :BOOL; (*照明控制箱06X0H-启停控制*)","LLCB06X0H_C             AT%M270.0      :BOOL; (*照明控制箱06X0H-启停控制*)"]
["照明控制箱","L","M","07X0H","启停控制","272.0",null,{"$f":"IF((IF(OR(I347=\"INT\",I347=\"WORD\",I347=\"BOOL\"),MOD(F347,2),MOD(F347,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A347&D347&\"-\"&E347","v":"照明控制箱07X0H-启停控制"},{"$f":"B347&VLOOKUP(A347,List!$B$3:$D$445,2,FALSE)&D347&\"_\"&VLOOKUP(E347,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0H_C"},{"$f":"K347&\" \"&\"AT%\"&C347&F347&\" \"&\":\"&I347&\";\"&\" \"&\"(*\"&J347&\"*)\"","v":"LLCB07X0H_C AT%M272.0 :BOOL; (*照明控制箱07X0H-启停控制*)"},{"$f":"REPLACE(REPLACE(L347,SEARCH(\"AT%\",L347),,REPT(\" \",25-SEARCH(\"AT%\",L347))),SEARCH(\":\",REPLACE(L347,SEARCH(\"AT%\",L347),,REPT(\" \",25-SEARCH(\"AT%\",L347)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L347,SEARCH(\"AT%\",L347),,REPT(\" \",25-SEARCH(\"AT%\",L347))))))","v":"LLCB07X0H_C             AT%M272.0      :BOOL; (*照明控制箱07X0H-启停控制*)"}]
["照明控制箱","L","M","08X0H","启停控制","274.0",null,"验证通过","BOOL","照明控制箱08X0H-启停控制",{"$f":"B348&VLOOKUP(A348,List!$B$3:$D$445,2,FALSE)&D348&\"_\"&VLOOKUP(E348,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0H_C"},"LLCB08X0H_C AT%M274.0 :BOOL; (*照明控制箱08X0H-启停控制*)","LLCB08X0H_C             AT%M274.0      :BOOL; (*照明控制箱08X0H-启停控制*)"]
["照明控制箱","L","M","B3X0A","定时控制","276.0",null,"验证通过","BOOL","照明控制箱B3X0A-定时控制",{"$f":"B349&VLOOKUP(A349,List!$B$3:$D$445,2,FALSE)&D349&\"_\"&VLOOKUP(E349,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0A_TC"},{"$f":"K349&\" \"&\"AT%\"&C349&F349&\" \"&\":\"&I349&\";\"&\" \"&\"(*\"&J349&\"*)\"","v":"LLCBB3X0A_TC AT%M276.0 :BOOL; (*照明控制箱B3X0A-定时控制*)"},{"$f":"REPLACE(REPLACE(L349,SEARCH(\"AT%\",L349),,REPT(\" \",25-SEARCH(\"AT%\",L349))),SEARCH(\":\",REPLACE(L349,SEARCH(\"AT%\",L349),,REPT(\" \",25-SEARCH(\"AT%\",L349)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L349,SEARCH(\"AT%\",L349),,REPT(\" \",25-SEARCH(\"AT%\",L349))))))","v":"LLCBB3X0A_TC            AT%M276.0      :BOOL; (*照明控制箱B3X0A-定时控制*)"}]
["照明控制箱","L","M","B2X0A","定时控制","278.0",null,{"$f":"IF((IF(OR(I350=\"INT\",I350=\"WORD\",I350=\"BOOL\"),MOD(F350,2),MOD(F350,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A350&D350&\"-\"&E350","v":"照明控制箱B2X0A-定时控制"},{"$f":"B350&VLOOKUP(A350,List!$B$3:$D$445,2,FALSE)&D350&\"_\"&VLOOKUP(E350,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0A_TC"},"LLCBB2X0A_TC AT%M278.0 :BOOL; (*照明控制箱B2X0A-定时控制*)","LLCBB2X0A_TC            AT%M278.0      :BOOL; (*照明控制箱B2X0A-定时控制*)"]
["照明控制箱","L","M","B1X0A","定时控制","280.0",null,"验证通过","BOOL","照明控制箱B1X0A-定时控制",{"$f":"B351&VLOOKUP(A351,List!$B$3:$D$445,2,FALSE)&D351&\"_\"&VLOOKUP(E351,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0A_TC"},"LLCBB1X0A_TC AT%M280.0 :BOOL; (*照明控制箱B1X0A-定时控制*)","LLCBB1X0A_TC            AT%M280.0      :BOOL; (*照明控制箱B1X0A-定时控制*)"]
["照明控制箱","L","M","01X0A","定时控制","282.0",null,"验证通过","BOOL","照明控制箱01X0A-定时控制",{"$f":"B352&VLOOKUP(A352,List!$B$3:$D$445,2,FALSE)&D352&\"_\"&VLOOKUP(E352,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0A_TC"},"LLCB01X0A_TC AT%M282.0 :BOOL; (*照明控制箱01X0A-定时控制*)","LLCB01X0A_TC            AT%M282.0      :BOOL; (*照明控制箱01X0A-定时控制*)"]
["照明控制箱","L","M","02X0A","定时控制","284.0",null,"验证通过","BOOL","照明控制箱02X0A-定时控制",{"$f":"B353&VLOOKUP(A353,List!$B$3:$D$445,2,FALSE)&D353&\"_\"&VLOOKUP(E353,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0A_TC"},"LLCB02X0A_TC AT%M284.0 :BOOL; (*照明控制箱02X0A-定时控制*)","LLCB02X0A_TC            AT%M284.0      :BOOL; (*照明控制箱02X0A-定时控制*)"]
["照明控制箱","L","M","03X0A","定时控制","286.0",null,"验证通过","BOOL","照明控制箱03X0A-定时控制",{"$f":"B354&VLOOKUP(A354,List!$B$3:$D$445,2,FALSE)&D354&\"_\"&VLOOKUP(E354,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0A_TC"},"LLCB03X0A_TC AT%M286.0 :BOOL; (*照明控制箱03X0A-定时控制*)","LLCB03X0A_TC            AT%M286.0      :BOOL; (*照明控制箱03X0A-定时控制*)"]
["照明控制箱","L","M","04X0A","定时控制","288.0",null,"验证通过","BOOL","照明控制箱04X0A-定时控制",{"$f":"B355&VLOOKUP(A355,List!$B$3:$D$445,2,FALSE)&D355&\"_\"&VLOOKUP(E355,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0A_TC"},"LLCB04X0A_TC AT%M288.0 :BOOL; (*照明控制箱04X0A-定时控制*)","LLCB04X0A_TC            AT%M288.0      :BOOL; (*照明控制箱04X0A-定时控制*)"]
["照明控制箱","L","M","05X0A","定时控制","290.0",null,"验证通过","BOOL","照明控制箱05X0A-定时控制",{"$f":"B356&VLOOKUP(A356,List!$B$3:$D$445,2,FALSE)&D356&\"_\"&VLOOKUP(E356,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0A_TC"},"LLCB05X0A_TC AT%M290.0 :BOOL; (*照明控制箱05X0A-定时控制*)","LLCB05X0A_TC            AT%M290.0      :BOOL; (*照明控制箱05X0A-定时控制*)"]
["照明控制箱","L","M","06X0A","定时控制","292.0",null,"验证通过","BOOL","照明控制箱06X0A-定时控制",{"$f":"B357&VLOOKUP(A357,List!$B$3:$D$445,2,FALSE)&D357&\"_\"&VLOOKUP(E357,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0A_TC"},"LLCB06X0A_TC AT%M292.0 :BOOL; (*照明控制箱06X0A-定时控制*)","LLCB06X0A_TC            AT%M292.0      :BOOL; (*照明控制箱06X0A-定时控制*)"]
["照明控制箱","L","M","07X0A","定时控制","294.0",null,{"$f":"IF((IF(OR(I358=\"INT\",I358=\"WORD\",I358=\"BOOL\"),MOD(F358,2),MOD(F358,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A358&D358&\"-\"&E358","v":"照明控制箱07X0A-定时控制"},{"$f":"B358&VLOOKUP(A358,List!$B$3:$D$445,2,FALSE)&D358&\"_\"&VLOOKUP(E358,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0A_TC"},{"$f":"K358&\" \"&\"AT%\"&C358&F358&\" \"&\":\"&I358&\";\"&\" \"&\"(*\"&J358&\"*)\"","v":"LLCB07X0A_TC AT%M294.0 :BOOL; (*照明控制箱07X0A-定时控制*)"},{"$f":"REPLACE(REPLACE(L358,SEARCH(\"AT%\",L358),,REPT(\" \",25-SEARCH(\"AT%\",L358))),SEARCH(\":\",REPLACE(L358,SEARCH(\"AT%\",L358),,REPT(\" \",25-SEARCH(\"AT%\",L358)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L358,SEARCH(\"AT%\",L358),,REPT(\" \",25-SEARCH(\"AT%\",L358))))))","v":"LLCB07X0A_TC            AT%M294.0      :BOOL; (*照明控制箱07X0A-定时控制*)"}]
["照明控制箱","L","M","08X0A","定时控制","296.0",null,"验证通过","BOOL","照明控制箱08X0A-定时控制",{"$f":"B359&VLOOKUP(A359,List!$B$3:$D$445,2,FALSE)&D359&\"_\"&VLOOKUP(E359,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0A_TC"},"LLCB08X0A_TC AT%M296.0 :BOOL; (*照明控制箱08X0A-定时控制*)","LLCB08X0A_TC            AT%M296.0      :BOOL; (*照明控制箱08X0A-定时控制*)"]
["照明控制箱","L","M","B3X0B","定时控制","298.0",null,"验证通过","BOOL","照明控制箱B3X0B-定时控制",{"$f":"B360&VLOOKUP(A360,List!$B$3:$D$445,2,FALSE)&D360&\"_\"&VLOOKUP(E360,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0B_TC"},"LLCBB3X0B_TC AT%M298.0 :BOOL; (*照明控制箱B3X0B-定时控制*)","LLCBB3X0B_TC            AT%M298.0      :BOOL; (*照明控制箱B3X0B-定时控制*)"]
["照明控制箱","L","M","B2X0B","定时控制","300.0",null,"验证通过","BOOL","照明控制箱B2X0B-定时控制",{"$f":"B361&VLOOKUP(A361,List!$B$3:$D$445,2,FALSE)&D361&\"_\"&VLOOKUP(E361,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0B_TC"},"LLCBB2X0B_TC AT%M300.0 :BOOL; (*照明控制箱B2X0B-定时控制*)","LLCBB2X0B_TC            AT%M300.0      :BOOL; (*照明控制箱B2X0B-定时控制*)"]
["照明控制箱","L","M","B1X0B","定时控制","302.0",null,"验证通过","BOOL","照明控制箱B1X0B-定时控制",{"$f":"B362&VLOOKUP(A362,List!$B$3:$D$445,2,FALSE)&D362&\"_\"&VLOOKUP(E362,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0B_TC"},"LLCBB1X0B_TC AT%M302.0 :BOOL; (*照明控制箱B1X0B-定时控制*)","LLCBB1X0B_TC            AT%M302.0      :BOOL; (*照明控制箱B1X0B-定时控制*)"]
["照明控制箱","L","M","01X0B","定时控制","304.0",null,"验证通过","BOOL","照明控制箱01X0B-定时控制",{"$f":"B363&VLOOKUP(A363,List!$B$3:$D$445,2,FALSE)&D363&\"_\"&VLOOKUP(E363,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0B_TC"},"LLCB01X0B_TC AT%M304.0 :BOOL; (*照明控制箱01X0B-定时控制*)","LLCB01X0B_TC            AT%M304.0      :BOOL; (*照明控制箱01X0B-定时控制*)"]
["照明控制箱","L","M","02X0B","定时控制","306.0",null,"验证通过","BOOL","照明控制箱02X0B-定时控制",{"$f":"B364&VLOOKUP(A364,List!$B$3:$D$445,2,FALSE)&D364&\"_\"&VLOOKUP(E364,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0B_TC"},"LLCB02X0B_TC AT%M306.0 :BOOL; (*照明控制箱02X0B-定时控制*)","LLCB02X0B_TC            AT%M306.0      :BOOL; (*照明控制箱02X0B-定时控制*)"]
["照明控制箱","L","M","03X0B","定时控制","308.0",null,"验证通过","BOOL","照明控制箱03X0B-定时控制",{"$f":"B365&VLOOKUP(A365,List!$B$3:$D$445,2,FALSE)&D365&\"_\"&VLOOKUP(E365,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0B_TC"},"LLCB03X0B_TC AT%M308.0 :BOOL; (*照明控制箱03X0B-定时控制*)","LLCB03X0B_TC            AT%M308.0      :BOOL; (*照明控制箱03X0B-定时控制*)"]
["照明控制箱","L","M","04X0B","定时控制","310.0",null,"验证通过","BOOL","照明控制箱04X0B-定时控制",{"$f":"B366&VLOOKUP(A366,List!$B$3:$D$445,2,FALSE)&D366&\"_\"&VLOOKUP(E366,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0B_TC"},"LLCB04X0B_TC AT%M310.0 :BOOL; (*照明控制箱04X0B-定时控制*)","LLCB04X0B_TC            AT%M310.0      :BOOL; (*照明控制箱04X0B-定时控制*)"]
["照明控制箱","L","M","05X0B","定时控制","312.0",null,"验证通过","BOOL","照明控制箱05X0B-定时控制",{"$f":"B367&VLOOKUP(A367,List!$B$3:$D$445,2,FALSE)&D367&\"_\"&VLOOKUP(E367,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0B_TC"},"LLCB05X0B_TC AT%M312.0 :BOOL; (*照明控制箱05X0B-定时控制*)","LLCB05X0B_TC            AT%M312.0      :BOOL; (*照明控制箱05X0B-定时控制*)"]
["照明控制箱","L","M","06X0B","定时控制","314.0",null,"验证通过","BOOL","照明控制箱06X0B-定时控制",{"$f":"B368&VLOOKUP(A368,List!$B$3:$D$445,2,FALSE)&D368&\"_\"&VLOOKUP(E368,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0B_TC"},"LLCB06X0B_TC AT%M314.0 :BOOL; (*照明控制箱06X0B-定时控制*)","LLCB06X0B_TC            AT%M314.0      :BOOL; (*照明控制箱06X0B-定时控制*)"]
["照明控制箱","L","M","07X0B","定时控制","316.0",null,{"$f":"IF((IF(OR(I369=\"INT\",I369=\"WORD\",I369=\"BOOL\"),MOD(F369,2),MOD(F369,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A369&D369&\"-\"&E369","v":"照明控制箱07X0B-定时控制"},{"$f":"B369&VLOOKUP(A369,List!$B$3:$D$445,2,FALSE)&D369&\"_\"&VLOOKUP(E369,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0B_TC"},{"$f":"K369&\" \"&\"AT%\"&C369&F369&\" \"&\":\"&I369&\";\"&\" \"&\"(*\"&J369&\"*)\"","v":"LLCB07X0B_TC AT%M316.0 :BOOL; (*照明控制箱07X0B-定时控制*)"},{"$f":"REPLACE(REPLACE(L369,SEARCH(\"AT%\",L369),,REPT(\" \",25-SEARCH(\"AT%\",L369))),SEARCH(\":\",REPLACE(L369,SEARCH(\"AT%\",L369),,REPT(\" \",25-SEARCH(\"AT%\",L369)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L369,SEARCH(\"AT%\",L369),,REPT(\" \",25-SEARCH(\"AT%\",L369))))))","v":"LLCB07X0B_TC            AT%M316.0      :BOOL; (*照明控制箱07X0B-定时控制*)"}]
["照明控制箱","L","M","08X0B","定时控制","318.0",null,"验证通过","BOOL","照明控制箱08X0B-定时控制",{"$f":"B370&VLOOKUP(A370,List!$B$3:$D$445,2,FALSE)&D370&\"_\"&VLOOKUP(E370,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0B_TC"},"LLCB08X0B_TC AT%M318.0 :BOOL; (*照明控制箱08X0B-定时控制*)","LLCB08X0B_TC            AT%M318.0      :BOOL; (*照明控制箱08X0B-定时控制*)"]
["照明控制箱","L","M","B3X0C","定时控制","320.0",null,"验证通过","BOOL","照明控制箱B3X0C-定时控制",{"$f":"B371&VLOOKUP(A371,List!$B$3:$D$445,2,FALSE)&D371&\"_\"&VLOOKUP(E371,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0C_TC"},"LLCBB3X0C_TC AT%M320.0 :BOOL; (*照明控制箱B3X0C-定时控制*)","LLCBB3X0C_TC            AT%M320.0      :BOOL; (*照明控制箱B3X0C-定时控制*)"]
["照明控制箱","L","M","B2X0C","定时控制","322.0",null,"验证通过","BOOL","照明控制箱B2X0C-定时控制",{"$f":"B372&VLOOKUP(A372,List!$B$3:$D$445,2,FALSE)&D372&\"_\"&VLOOKUP(E372,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0C_TC"},"LLCBB2X0C_TC AT%M322.0 :BOOL; (*照明控制箱B2X0C-定时控制*)","LLCBB2X0C_TC            AT%M322.0      :BOOL; (*照明控制箱B2X0C-定时控制*)"]
["照明控制箱","L","M","B1X0C","定时控制","324.0",null,"验证通过","BOOL","照明控制箱B1X0C-定时控制",{"$f":"B373&VLOOKUP(A373,List!$B$3:$D$445,2,FALSE)&D373&\"_\"&VLOOKUP(E373,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0C_TC"},"LLCBB1X0C_TC AT%M324.0 :BOOL; (*照明控制箱B1X0C-定时控制*)","LLCBB1X0C_TC            AT%M324.0      :BOOL; (*照明控制箱B1X0C-定时控制*)"]
["照明控制箱","L","M","01X0C","定时控制","326.0",null,"验证通过","BOOL","照明控制箱01X0C-定时控制",{"$f":"B374&VLOOKUP(A374,List!$B$3:$D$445,2,FALSE)&D374&\"_\"&VLOOKUP(E374,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0C_TC"},"LLCB01X0C_TC AT%M326.0 :BOOL; (*照明控制箱01X0C-定时控制*)","LLCB01X0C_TC            AT%M326.0      :BOOL; (*照明控制箱01X0C-定时控制*)"]
["照明控制箱","L","M","02X0C","定时控制","328.0",null,"验证通过","BOOL","照明控制箱02X0C-定时控制",{"$f":"B375&VLOOKUP(A375,List!$B$3:$D$445,2,FALSE)&D375&\"_\"&VLOOKUP(E375,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0C_TC"},"LLCB02X0C_TC AT%M328.0 :BOOL; (*照明控制箱02X0C-定时控制*)","LLCB02X0C_TC            AT%M328.0      :BOOL; (*照明控制箱02X0C-定时控制*)"]
["照明控制箱","L","M","03X0C","定时控制","330.0",null,"验证通过","BOOL","照明控制箱03X0C-定时控制",{"$f":"B376&VLOOKUP(A376,List!$B$3:$D$445,2,FALSE)&D376&\"_\"&VLOOKUP(E376,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0C_TC"},"LLCB03X0C_TC AT%M330.0 :BOOL; (*照明控制箱03X0C-定时控制*)","LLCB03X0C_TC            AT%M330.0      :BOOL; (*照明控制箱03X0C-定时控制*)"]
["照明控制箱","L","M","04X0C","定时控制","332.0",null,"验证通过","BOOL","照明控制箱04X0C-定时控制",{"$f":"B377&VLOOKUP(A377,List!$B$3:$D$445,2,FALSE)&D377&\"_\"&VLOOKUP(E377,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0C_TC"},"LLCB04X0C_TC AT%M332.0 :BOOL; (*照明控制箱04X0C-定时控制*)","LLCB04X0C_TC            AT%M332.0      :BOOL; (*照明控制箱04X0C-定时控制*)"]
["照明控制箱","L","M","05X0C","定时控制","334.0",null,"验证通过","BOOL","照明控制箱05X0C-定时控制",{"$f":"B378&VLOOKUP(A378,List!$B$3:$D$445,2,FALSE)&D378&\"_\"&VLOOKUP(E378,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0C_TC"},"LLCB05X0C_TC AT%M334.0 :BOOL; (*照明控制箱05X0C-定时控制*)","LLCB05X0C_TC            AT%M334.0      :BOOL; (*照明控制箱05X0C-定时控制*)"]
["照明控制箱","L","M","06X0C","定时控制","336.0",null,"验证通过","BOOL","照明控制箱06X0C-定时控制",{"$f":"B379&VLOOKUP(A379,List!$B$3:$D$445,2,FALSE)&D379&\"_\"&VLOOKUP(E379,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0C_TC"},"LLCB06X0C_TC AT%M336.0 :BOOL; (*照明控制箱06X0C-定时控制*)","LLCB06X0C_TC            AT%M336.0      :BOOL; (*照明控制箱06X0C-定时控制*)"]
["照明控制箱","L","M","07X0C","定时控制","338.0",null,{"$f":"IF((IF(OR(I380=\"INT\",I380=\"WORD\",I380=\"BOOL\"),MOD(F380,2),MOD(F380,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A380&D380&\"-\"&E380","v":"照明控制箱07X0C-定时控制"},{"$f":"B380&VLOOKUP(A380,List!$B$3:$D$445,2,FALSE)&D380&\"_\"&VLOOKUP(E380,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0C_TC"},{"$f":"K380&\" \"&\"AT%\"&C380&F380&\" \"&\":\"&I380&\";\"&\" \"&\"(*\"&J380&\"*)\"","v":"LLCB07X0C_TC AT%M338.0 :BOOL; (*照明控制箱07X0C-定时控制*)"},{"$f":"REPLACE(REPLACE(L380,SEARCH(\"AT%\",L380),,REPT(\" \",25-SEARCH(\"AT%\",L380))),SEARCH(\":\",REPLACE(L380,SEARCH(\"AT%\",L380),,REPT(\" \",25-SEARCH(\"AT%\",L380)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L380,SEARCH(\"AT%\",L380),,REPT(\" \",25-SEARCH(\"AT%\",L380))))))","v":"LLCB07X0C_TC            AT%M338.0      :BOOL; (*照明控制箱07X0C-定时控制*)"}]
["照明控制箱","L","M","08X0C","定时控制","340.0",null,"验证通过","BOOL","照明控制箱08X0C-定时控制",{"$f":"B381&VLOOKUP(A381,List!$B$3:$D$445,2,FALSE)&D381&\"_\"&VLOOKUP(E381,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0C_TC"},"LLCB08X0C_TC AT%M340.0 :BOOL; (*照明控制箱08X0C-定时控制*)","LLCB08X0C_TC            AT%M340.0      :BOOL; (*照明控制箱08X0C-定时控制*)"]
["照明控制箱","L","M","B3X0D","定时控制","342.0",null,"验证通过","BOOL","照明控制箱B3X0D-定时控制",{"$f":"B382&VLOOKUP(A382,List!$B$3:$D$445,2,FALSE)&D382&\"_\"&VLOOKUP(E382,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0D_TC"},"LLCBB3X0D_TC AT%M342.0 :BOOL; (*照明控制箱B3X0D-定时控制*)","LLCBB3X0D_TC            AT%M342.0      :BOOL; (*照明控制箱B3X0D-定时控制*)"]
["照明控制箱","L","M","B2X0D","定时控制","344.0",null,"验证通过","BOOL","照明控制箱B2X0D-定时控制",{"$f":"B383&VLOOKUP(A383,List!$B$3:$D$445,2,FALSE)&D383&\"_\"&VLOOKUP(E383,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0D_TC"},{"$f":"K383&\" \"&\"AT%\"&C383&F383&\" \"&\":\"&I383&\";\"&\" \"&\"(*\"&J383&\"*)\"","v":"LLCBB2X0D_TC AT%M344.0 :BOOL; (*照明控制箱B2X0D-定时控制*)"},{"$f":"REPLACE(REPLACE(L383,SEARCH(\"AT%\",L383),,REPT(\" \",25-SEARCH(\"AT%\",L383))),SEARCH(\":\",REPLACE(L383,SEARCH(\"AT%\",L383),,REPT(\" \",25-SEARCH(\"AT%\",L383)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L383,SEARCH(\"AT%\",L383),,REPT(\" \",25-SEARCH(\"AT%\",L383))))))","v":"LLCBB2X0D_TC            AT%M344.0      :BOOL; (*照明控制箱B2X0D-定时控制*)"}]
["照明控制箱","L","M","B1X0D","定时控制","346.0",null,"验证通过","BOOL","照明控制箱B1X0D-定时控制",{"$f":"B384&VLOOKUP(A384,List!$B$3:$D$445,2,FALSE)&D384&\"_\"&VLOOKUP(E384,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0D_TC"},"LLCBB1X0D_TC AT%M346.0 :BOOL; (*照明控制箱B1X0D-定时控制*)","LLCBB1X0D_TC            AT%M346.0      :BOOL; (*照明控制箱B1X0D-定时控制*)"]
["照明控制箱","L","M","01X0D","定时控制","348.0",null,"验证通过","BOOL","照明控制箱01X0D-定时控制",{"$f":"B385&VLOOKUP(A385,List!$B$3:$D$445,2,FALSE)&D385&\"_\"&VLOOKUP(E385,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0D_TC"},"LLCB01X0D_TC AT%M348.0 :BOOL; (*照明控制箱01X0D-定时控制*)","LLCB01X0D_TC            AT%M348.0      :BOOL; (*照明控制箱01X0D-定时控制*)"]
["照明控制箱","L","M","02X0D","定时控制","350.0",null,"验证通过","BOOL","照明控制箱02X0D-定时控制",{"$f":"B386&VLOOKUP(A386,List!$B$3:$D$445,2,FALSE)&D386&\"_\"&VLOOKUP(E386,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0D_TC"},"LLCB02X0D_TC AT%M350.0 :BOOL; (*照明控制箱02X0D-定时控制*)","LLCB02X0D_TC            AT%M350.0      :BOOL; (*照明控制箱02X0D-定时控制*)"]
["照明控制箱","L","M","03X0D","定时控制","352.0",null,"验证通过","BOOL","照明控制箱03X0D-定时控制",{"$f":"B387&VLOOKUP(A387,List!$B$3:$D$445,2,FALSE)&D387&\"_\"&VLOOKUP(E387,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0D_TC"},"LLCB03X0D_TC AT%M352.0 :BOOL; (*照明控制箱03X0D-定时控制*)","LLCB03X0D_TC            AT%M352.0      :BOOL; (*照明控制箱03X0D-定时控制*)"]
["照明控制箱","L","M","04X0D","定时控制","354.0",null,"验证通过","BOOL","照明控制箱04X0D-定时控制",{"$f":"B388&VLOOKUP(A388,List!$B$3:$D$445,2,FALSE)&D388&\"_\"&VLOOKUP(E388,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0D_TC"},"LLCB04X0D_TC AT%M354.0 :BOOL; (*照明控制箱04X0D-定时控制*)","LLCB04X0D_TC            AT%M354.0      :BOOL; (*照明控制箱04X0D-定时控制*)"]
["照明控制箱","L","M","05X0D","定时控制","356.0",null,"验证通过","BOOL","照明控制箱05X0D-定时控制",{"$f":"B389&VLOOKUP(A389,List!$B$3:$D$445,2,FALSE)&D389&\"_\"&VLOOKUP(E389,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0D_TC"},"LLCB05X0D_TC AT%M356.0 :BOOL; (*照明控制箱05X0D-定时控制*)","LLCB05X0D_TC            AT%M356.0      :BOOL; (*照明控制箱05X0D-定时控制*)"]
["照明控制箱","L","M","06X0D","定时控制","358.0",null,"验证通过","BOOL","照明控制箱06X0D-定时控制",{"$f":"B390&VLOOKUP(A390,List!$B$3:$D$445,2,FALSE)&D390&\"_\"&VLOOKUP(E390,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0D_TC"},"LLCB06X0D_TC AT%M358.0 :BOOL; (*照明控制箱06X0D-定时控制*)","LLCB06X0D_TC            AT%M358.0      :BOOL; (*照明控制箱06X0D-定时控制*)"]
["照明控制箱","L","M","07X0D","定时控制","360.0",null,{"$f":"IF((IF(OR(I391=\"INT\",I391=\"WORD\",I391=\"BOOL\"),MOD(F391,2),MOD(F391,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A391&D391&\"-\"&E391","v":"照明控制箱07X0D-定时控制"},{"$f":"B391&VLOOKUP(A391,List!$B$3:$D$445,2,FALSE)&D391&\"_\"&VLOOKUP(E391,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0D_TC"},{"$f":"K391&\" \"&\"AT%\"&C391&F391&\" \"&\":\"&I391&\";\"&\" \"&\"(*\"&J391&\"*)\"","v":"LLCB07X0D_TC AT%M360.0 :BOOL; (*照明控制箱07X0D-定时控制*)"},{"$f":"REPLACE(REPLACE(L391,SEARCH(\"AT%\",L391),,REPT(\" \",25-SEARCH(\"AT%\",L391))),SEARCH(\":\",REPLACE(L391,SEARCH(\"AT%\",L391),,REPT(\" \",25-SEARCH(\"AT%\",L391)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L391,SEARCH(\"AT%\",L391),,REPT(\" \",25-SEARCH(\"AT%\",L391))))))","v":"LLCB07X0D_TC            AT%M360.0      :BOOL; (*照明控制箱07X0D-定时控制*)"}]
["照明控制箱","L","M","08X0D","定时控制","362.0",null,"验证通过","BOOL","照明控制箱08X0D-定时控制",{"$f":"B392&VLOOKUP(A392,List!$B$3:$D$445,2,FALSE)&D392&\"_\"&VLOOKUP(E392,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0D_TC"},"LLCB08X0D_TC AT%M362.0 :BOOL; (*照明控制箱08X0D-定时控制*)","LLCB08X0D_TC            AT%M362.0      :BOOL; (*照明控制箱08X0D-定时控制*)"]
["照明控制箱","L","M","B3X0E","定时控制","364.0",null,"验证通过","BOOL","照明控制箱B3X0E-定时控制",{"$f":"B393&VLOOKUP(A393,List!$B$3:$D$445,2,FALSE)&D393&\"_\"&VLOOKUP(E393,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0E_TC"},"LLCBB3X0E_TC AT%M364.0 :BOOL; (*照明控制箱B3X0E-定时控制*)","LLCBB3X0E_TC            AT%M364.0      :BOOL; (*照明控制箱B3X0E-定时控制*)"]
["照明控制箱","L","M","B2X0E","定时控制","366.0",null,"验证通过","BOOL","照明控制箱B2X0E-定时控制",{"$f":"B394&VLOOKUP(A394,List!$B$3:$D$445,2,FALSE)&D394&\"_\"&VLOOKUP(E394,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0E_TC"},"LLCBB2X0E_TC AT%M366.0 :BOOL; (*照明控制箱B2X0E-定时控制*)","LLCBB2X0E_TC            AT%M366.0      :BOOL; (*照明控制箱B2X0E-定时控制*)"]
["照明控制箱","L","M","B1X0E","定时控制","368.0",null,"验证通过","BOOL","照明控制箱B1X0E-定时控制",{"$f":"B395&VLOOKUP(A395,List!$B$3:$D$445,2,FALSE)&D395&\"_\"&VLOOKUP(E395,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0E_TC"},"LLCBB1X0E_TC AT%M368.0 :BOOL; (*照明控制箱B1X0E-定时控制*)","LLCBB1X0E_TC            AT%M368.0      :BOOL; (*照明控制箱B1X0E-定时控制*)"]
["照明控制箱","L","M","01X0E","定时控制","370.0",null,"验证通过","BOOL","照明控制箱01X0E-定时控制",{"$f":"B396&VLOOKUP(A396,List!$B$3:$D$445,2,FALSE)&D396&\"_\"&VLOOKUP(E396,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0E_TC"},"LLCB01X0E_TC AT%M370.0 :BOOL; (*照明控制箱01X0E-定时控制*)","LLCB01X0E_TC            AT%M370.0      :BOOL; (*照明控制箱01X0E-定时控制*)"]
["照明控制箱","L","M","02X0E","定时控制","372.0",null,"验证通过","BOOL","照明控制箱02X0E-定时控制",{"$f":"B397&VLOOKUP(A397,List!$B$3:$D$445,2,FALSE)&D397&\"_\"&VLOOKUP(E397,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0E_TC"},"LLCB02X0E_TC AT%M372.0 :BOOL; (*照明控制箱02X0E-定时控制*)","LLCB02X0E_TC            AT%M372.0      :BOOL; (*照明控制箱02X0E-定时控制*)"]
["照明控制箱","L","M","03X0E","定时控制","374.0",null,"验证通过","BOOL","照明控制箱03X0E-定时控制",{"$f":"B398&VLOOKUP(A398,List!$B$3:$D$445,2,FALSE)&D398&\"_\"&VLOOKUP(E398,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0E_TC"},"LLCB03X0E_TC AT%M374.0 :BOOL; (*照明控制箱03X0E-定时控制*)","LLCB03X0E_TC            AT%M374.0      :BOOL; (*照明控制箱03X0E-定时控制*)"]
["照明控制箱","L","M","04X0E","定时控制","376.0",null,"验证通过","BOOL","照明控制箱04X0E-定时控制",{"$f":"B399&VLOOKUP(A399,List!$B$3:$D$445,2,FALSE)&D399&\"_\"&VLOOKUP(E399,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0E_TC"},"LLCB04X0E_TC AT%M376.0 :BOOL; (*照明控制箱04X0E-定时控制*)","LLCB04X0E_TC            AT%M376.0      :BOOL; (*照明控制箱04X0E-定时控制*)"]
["照明控制箱","L","M","05X0E","定时控制","378.0",null,"验证通过","BOOL","照明控制箱05X0E-定时控制",{"$f":"B400&VLOOKUP(A400,List!$B$3:$D$445,2,FALSE)&D400&\"_\"&VLOOKUP(E400,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0E_TC"},"LLCB05X0E_TC AT%M378.0 :BOOL; (*照明控制箱05X0E-定时控制*)","LLCB05X0E_TC            AT%M378.0      :BOOL; (*照明控制箱05X0E-定时控制*)"]
["照明控制箱","L","M","06X0E","定时控制","380.0",null,"验证通过","BOOL","照明控制箱06X0E-定时控制",{"$f":"B401&VLOOKUP(A401,List!$B$3:$D$445,2,FALSE)&D401&\"_\"&VLOOKUP(E401,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0E_TC"},"LLCB06X0E_TC AT%M380.0 :BOOL; (*照明控制箱06X0E-定时控制*)","LLCB06X0E_TC            AT%M380.0      :BOOL; (*照明控制箱06X0E-定时控制*)"]
["照明控制箱","L","M","07X0E","定时控制","382.0",null,{"$f":"IF((IF(OR(I402=\"INT\",I402=\"WORD\",I402=\"BOOL\"),MOD(F402,2),MOD(F402,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A402&D402&\"-\"&E402","v":"照明控制箱07X0E-定时控制"},{"$f":"B402&VLOOKUP(A402,List!$B$3:$D$445,2,FALSE)&D402&\"_\"&VLOOKUP(E402,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0E_TC"},{"$f":"K402&\" \"&\"AT%\"&C402&F402&\" \"&\":\"&I402&\";\"&\" \"&\"(*\"&J402&\"*)\"","v":"LLCB07X0E_TC AT%M382.0 :BOOL; (*照明控制箱07X0E-定时控制*)"},{"$f":"REPLACE(REPLACE(L402,SEARCH(\"AT%\",L402),,REPT(\" \",25-SEARCH(\"AT%\",L402))),SEARCH(\":\",REPLACE(L402,SEARCH(\"AT%\",L402),,REPT(\" \",25-SEARCH(\"AT%\",L402)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L402,SEARCH(\"AT%\",L402),,REPT(\" \",25-SEARCH(\"AT%\",L402))))))","v":"LLCB07X0E_TC            AT%M382.0      :BOOL; (*照明控制箱07X0E-定时控制*)"}]
["照明控制箱","L","M","08X0E","定时控制","384.0",null,"验证通过","BOOL","照明控制箱08X0E-定时控制",{"$f":"B403&VLOOKUP(A403,List!$B$3:$D$445,2,FALSE)&D403&\"_\"&VLOOKUP(E403,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0E_TC"},"LLCB08X0E_TC AT%M384.0 :BOOL; (*照明控制箱08X0E-定时控制*)","LLCB08X0E_TC            AT%M384.0      :BOOL; (*照明控制箱08X0E-定时控制*)"]
["照明控制箱","L","M","B3X0F","定时控制",{"$f":"IF(OR(I403=\"REAL\",I403=\"DWORD\",I403=\"DINT\"),(IF(OR(I404=\"REAL\",I404=\"DWORD\",I404=\"DINT\"),F403+4+MOD(F403,4),F403+4)),(IF(OR(I404=\"REAL\",I404=\"DWORD\",I404=\"DINT\"),F403+4+MOD(F403,4),F403+2)))&\".0\"","v":"386.0"},null,"验证通过","BOOL","照明控制箱B3X0F-定时控制",{"$f":"B404&VLOOKUP(A404,List!$B$3:$D$445,2,FALSE)&D404&\"_\"&VLOOKUP(E404,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0F_TC"},"LLCBB3X0F_TC AT%M386.0 :BOOL; (*照明控制箱B3X0F-定时控制*)","LLCBB3X0F_TC            AT%M386.0      :BOOL; (*照明控制箱B3X0F-定时控制*)"]
["照明控制箱","L","M","B2X0F","定时控制","388.0",null,"验证通过","BOOL","照明控制箱B2X0F-定时控制",{"$f":"B405&VLOOKUP(A405,List!$B$3:$D$445,2,FALSE)&D405&\"_\"&VLOOKUP(E405,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0F_TC"},"LLCBB2X0F_TC AT%M388.0 :BOOL; (*照明控制箱B2X0F-定时控制*)","LLCBB2X0F_TC            AT%M388.0      :BOOL; (*照明控制箱B2X0F-定时控制*)"]
["照明控制箱","L","M","B1X0F","定时控制","390.0",null,"验证通过","BOOL","照明控制箱B1X0F-定时控制",{"$f":"B406&VLOOKUP(A406,List!$B$3:$D$445,2,FALSE)&D406&\"_\"&VLOOKUP(E406,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0F_TC"},"LLCBB1X0F_TC AT%M390.0 :BOOL; (*照明控制箱B1X0F-定时控制*)","LLCBB1X0F_TC            AT%M390.0      :BOOL; (*照明控制箱B1X0F-定时控制*)"]
["照明控制箱","L","M","01X0F","定时控制","392.0",null,"验证通过","BOOL","照明控制箱01X0F-定时控制",{"$f":"B407&VLOOKUP(A407,List!$B$3:$D$445,2,FALSE)&D407&\"_\"&VLOOKUP(E407,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0F_TC"},"LLCB01X0F_TC AT%M392.0 :BOOL; (*照明控制箱01X0F-定时控制*)","LLCB01X0F_TC            AT%M392.0      :BOOL; (*照明控制箱01X0F-定时控制*)"]
["照明控制箱","L","M","02X0F","定时控制","394.0",null,"验证通过","BOOL","照明控制箱02X0F-定时控制",{"$f":"B408&VLOOKUP(A408,List!$B$3:$D$445,2,FALSE)&D408&\"_\"&VLOOKUP(E408,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0F_TC"},"LLCB02X0F_TC AT%M394.0 :BOOL; (*照明控制箱02X0F-定时控制*)","LLCB02X0F_TC            AT%M394.0      :BOOL; (*照明控制箱02X0F-定时控制*)"]
["照明控制箱","L","M","03X0F","定时控制","396.0",null,"验证通过","BOOL","照明控制箱03X0F-定时控制",{"$f":"B409&VLOOKUP(A409,List!$B$3:$D$445,2,FALSE)&D409&\"_\"&VLOOKUP(E409,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0F_TC"},"LLCB03X0F_TC AT%M396.0 :BOOL; (*照明控制箱03X0F-定时控制*)","LLCB03X0F_TC            AT%M396.0      :BOOL; (*照明控制箱03X0F-定时控制*)"]
["照明控制箱","L","M","04X0F","定时控制","398.0",null,"验证通过","BOOL","照明控制箱04X0F-定时控制",{"$f":"B410&VLOOKUP(A410,List!$B$3:$D$445,2,FALSE)&D410&\"_\"&VLOOKUP(E410,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0F_TC"},"LLCB04X0F_TC AT%M398.0 :BOOL; (*照明控制箱04X0F-定时控制*)","LLCB04X0F_TC            AT%M398.0      :BOOL; (*照明控制箱04X0F-定时控制*)"]
["照明控制箱","L","M","05X0F","定时控制","400.0",null,"验证通过","BOOL","照明控制箱05X0F-定时控制",{"$f":"B411&VLOOKUP(A411,List!$B$3:$D$445,2,FALSE)&D411&\"_\"&VLOOKUP(E411,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0F_TC"},"LLCB05X0F_TC AT%M400.0 :BOOL; (*照明控制箱05X0F-定时控制*)","LLCB05X0F_TC            AT%M400.0      :BOOL; (*照明控制箱05X0F-定时控制*)"]
["照明控制箱","L","M","06X0F","定时控制","402.0",null,"验证通过","BOOL","照明控制箱06X0F-定时控制",{"$f":"B412&VLOOKUP(A412,List!$B$3:$D$445,2,FALSE)&D412&\"_\"&VLOOKUP(E412,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0F_TC"},"LLCB06X0F_TC AT%M402.0 :BOOL; (*照明控制箱06X0F-定时控制*)","LLCB06X0F_TC            AT%M402.0      :BOOL; (*照明控制箱06X0F-定时控制*)"]
["照明控制箱","L","M","07X0F","定时控制","404.0",null,{"$f":"IF((IF(OR(I413=\"INT\",I413=\"WORD\",I413=\"BOOL\"),MOD(F413,2),MOD(F413,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A413&D413&\"-\"&E413","v":"照明控制箱07X0F-定时控制"},{"$f":"B413&VLOOKUP(A413,List!$B$3:$D$445,2,FALSE)&D413&\"_\"&VLOOKUP(E413,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0F_TC"},{"$f":"K413&\" \"&\"AT%\"&C413&F413&\" \"&\":\"&I413&\";\"&\" \"&\"(*\"&J413&\"*)\"","v":"LLCB07X0F_TC AT%M404.0 :BOOL; (*照明控制箱07X0F-定时控制*)"},{"$f":"REPLACE(REPLACE(L413,SEARCH(\"AT%\",L413),,REPT(\" \",25-SEARCH(\"AT%\",L413))),SEARCH(\":\",REPLACE(L413,SEARCH(\"AT%\",L413),,REPT(\" \",25-SEARCH(\"AT%\",L413)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L413,SEARCH(\"AT%\",L413),,REPT(\" \",25-SEARCH(\"AT%\",L413))))))","v":"LLCB07X0F_TC            AT%M404.0      :BOOL; (*照明控制箱07X0F-定时控制*)"}]
["照明控制箱","L","M","08X0F","定时控制","406.0",null,"验证通过","BOOL","照明控制箱08X0F-定时控制",{"$f":"B414&VLOOKUP(A414,List!$B$3:$D$445,2,FALSE)&D414&\"_\"&VLOOKUP(E414,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0F_TC"},"LLCB08X0F_TC AT%M406.0 :BOOL; (*照明控制箱08X0F-定时控制*)","LLCB08X0F_TC            AT%M406.0      :BOOL; (*照明控制箱08X0F-定时控制*)"]
["照明控制箱","L","M","B3X0G","定时控制","408.0",null,"验证通过","BOOL","照明控制箱B3X0G-定时控制",{"$f":"B415&VLOOKUP(A415,List!$B$3:$D$445,2,FALSE)&D415&\"_\"&VLOOKUP(E415,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0G_TC"},"LLCBB3X0G_TC AT%M408.0 :BOOL; (*照明控制箱B3X0G-定时控制*)","LLCBB3X0G_TC            AT%M408.0      :BOOL; (*照明控制箱B3X0G-定时控制*)"]
["照明控制箱","L","M","B2X0G","定时控制","410.0",null,"验证通过","BOOL","照明控制箱B2X0G-定时控制",{"$f":"B416&VLOOKUP(A416,List!$B$3:$D$445,2,FALSE)&D416&\"_\"&VLOOKUP(E416,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0G_TC"},"LLCBB2X0G_TC AT%M410.0 :BOOL; (*照明控制箱B2X0G-定时控制*)","LLCBB2X0G_TC            AT%M410.0      :BOOL; (*照明控制箱B2X0G-定时控制*)"]
["照明控制箱","L","M","B1X0G","定时控制","412.0",null,"验证通过","BOOL","照明控制箱B1X0G-定时控制",{"$f":"B417&VLOOKUP(A417,List!$B$3:$D$445,2,FALSE)&D417&\"_\"&VLOOKUP(E417,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0G_TC"},"LLCBB1X0G_TC AT%M412.0 :BOOL; (*照明控制箱B1X0G-定时控制*)","LLCBB1X0G_TC            AT%M412.0      :BOOL; (*照明控制箱B1X0G-定时控制*)"]
["照明控制箱","L","M","01X0G","定时控制","414.0",null,"验证通过","BOOL","照明控制箱01X0G-定时控制",{"$f":"B418&VLOOKUP(A418,List!$B$3:$D$445,2,FALSE)&D418&\"_\"&VLOOKUP(E418,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0G_TC"},"LLCB01X0G_TC AT%M414.0 :BOOL; (*照明控制箱01X0G-定时控制*)","LLCB01X0G_TC            AT%M414.0      :BOOL; (*照明控制箱01X0G-定时控制*)"]
["照明控制箱","L","M","02X0G","定时控制","416.0",null,"验证通过","BOOL","照明控制箱02X0G-定时控制",{"$f":"B419&VLOOKUP(A419,List!$B$3:$D$445,2,FALSE)&D419&\"_\"&VLOOKUP(E419,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0G_TC"},"LLCB02X0G_TC AT%M416.0 :BOOL; (*照明控制箱02X0G-定时控制*)","LLCB02X0G_TC            AT%M416.0      :BOOL; (*照明控制箱02X0G-定时控制*)"]
["照明控制箱","L","M","03X0G","定时控制","418.0",null,"验证通过","BOOL","照明控制箱03X0G-定时控制",{"$f":"B420&VLOOKUP(A420,List!$B$3:$D$445,2,FALSE)&D420&\"_\"&VLOOKUP(E420,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0G_TC"},"LLCB03X0G_TC AT%M418.0 :BOOL; (*照明控制箱03X0G-定时控制*)","LLCB03X0G_TC            AT%M418.0      :BOOL; (*照明控制箱03X0G-定时控制*)"]
["照明控制箱","L","M","04X0G","定时控制","420.0",null,"验证通过","BOOL","照明控制箱04X0G-定时控制",{"$f":"B421&VLOOKUP(A421,List!$B$3:$D$445,2,FALSE)&D421&\"_\"&VLOOKUP(E421,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0G_TC"},"LLCB04X0G_TC AT%M420.0 :BOOL; (*照明控制箱04X0G-定时控制*)","LLCB04X0G_TC            AT%M420.0      :BOOL; (*照明控制箱04X0G-定时控制*)"]
["照明控制箱","L","M","05X0G","定时控制","422.0",null,"验证通过","BOOL","照明控制箱05X0G-定时控制",{"$f":"B422&VLOOKUP(A422,List!$B$3:$D$445,2,FALSE)&D422&\"_\"&VLOOKUP(E422,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0G_TC"},"LLCB05X0G_TC AT%M422.0 :BOOL; (*照明控制箱05X0G-定时控制*)","LLCB05X0G_TC            AT%M422.0      :BOOL; (*照明控制箱05X0G-定时控制*)"]
["照明控制箱","L","M","06X0G","定时控制","424.0",null,"验证通过","BOOL","照明控制箱06X0G-定时控制",{"$f":"B423&VLOOKUP(A423,List!$B$3:$D$445,2,FALSE)&D423&\"_\"&VLOOKUP(E423,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0G_TC"},"LLCB06X0G_TC AT%M424.0 :BOOL; (*照明控制箱06X0G-定时控制*)","LLCB06X0G_TC            AT%M424.0      :BOOL; (*照明控制箱06X0G-定时控制*)"]
["照明控制箱","L","M","07X0G","定时控制","426.0",null,{"$f":"IF((IF(OR(I424=\"INT\",I424=\"WORD\",I424=\"BOOL\"),MOD(F424,2),MOD(F424,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A424&D424&\"-\"&E424","v":"照明控制箱07X0G-定时控制"},{"$f":"B424&VLOOKUP(A424,List!$B$3:$D$445,2,FALSE)&D424&\"_\"&VLOOKUP(E424,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0G_TC"},{"$f":"K424&\" \"&\"AT%\"&C424&F424&\" \"&\":\"&I424&\";\"&\" \"&\"(*\"&J424&\"*)\"","v":"LLCB07X0G_TC AT%M426.0 :BOOL; (*照明控制箱07X0G-定时控制*)"},{"$f":"REPLACE(REPLACE(L424,SEARCH(\"AT%\",L424),,REPT(\" \",25-SEARCH(\"AT%\",L424))),SEARCH(\":\",REPLACE(L424,SEARCH(\"AT%\",L424),,REPT(\" \",25-SEARCH(\"AT%\",L424)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L424,SEARCH(\"AT%\",L424),,REPT(\" \",25-SEARCH(\"AT%\",L424))))))","v":"LLCB07X0G_TC            AT%M426.0      :BOOL; (*照明控制箱07X0G-定时控制*)"}]
["照明控制箱","L","M","08X0G","定时控制","428.0",null,"验证通过","BOOL","照明控制箱08X0G-定时控制",{"$f":"B425&VLOOKUP(A425,List!$B$3:$D$445,2,FALSE)&D425&\"_\"&VLOOKUP(E425,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0G_TC"},"LLCB08X0G_TC AT%M428.0 :BOOL; (*照明控制箱08X0G-定时控制*)","LLCB08X0G_TC            AT%M428.0      :BOOL; (*照明控制箱08X0G-定时控制*)"]
["照明控制箱","L","M","B3X0H","定时控制","430.0",null,"验证通过","BOOL","照明控制箱B3X0H-定时控制",{"$f":"B426&VLOOKUP(A426,List!$B$3:$D$445,2,FALSE)&D426&\"_\"&VLOOKUP(E426,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0H_TC"},"LLCBB3X0H_TC AT%M430.0 :BOOL; (*照明控制箱B3X0H-定时控制*)","LLCBB3X0H_TC            AT%M430.0      :BOOL; (*照明控制箱B3X0H-定时控制*)"]
["照明控制箱","L","M","B2X0H","定时控制","432.0",null,"验证通过","BOOL","照明控制箱B2X0H-定时控制",{"$f":"B427&VLOOKUP(A427,List!$B$3:$D$445,2,FALSE)&D427&\"_\"&VLOOKUP(E427,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0H_TC"},"LLCBB2X0H_TC AT%M432.0 :BOOL; (*照明控制箱B2X0H-定时控制*)","LLCBB2X0H_TC            AT%M432.0      :BOOL; (*照明控制箱B2X0H-定时控制*)"]
["照明控制箱","L","M","B1X0H","定时控制","434.0",null,{"$f":"IF((IF(OR(I428=\"INT\",I428=\"WORD\",I428=\"BOOL\"),MOD(F428,2),MOD(F428,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A428&D428&\"-\"&E428","v":"照明控制箱B1X0H-定时控制"},{"$f":"B428&VLOOKUP(A428,List!$B$3:$D$445,2,FALSE)&D428&\"_\"&VLOOKUP(E428,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0H_TC"},"LLCBB1X0H_TC AT%M434.0 :BOOL; (*照明控制箱B1X0H-定时控制*)","LLCBB1X0H_TC            AT%M434.0      :BOOL; (*照明控制箱B1X0H-定时控制*)"]
["照明控制箱","L","M","01X0H","定时控制","436.0",null,"验证通过","BOOL","照明控制箱01X0H-定时控制",{"$f":"B429&VLOOKUP(A429,List!$B$3:$D$445,2,FALSE)&D429&\"_\"&VLOOKUP(E429,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0H_TC"},"LLCB01X0H_TC AT%M436.0 :BOOL; (*照明控制箱01X0H-定时控制*)","LLCB01X0H_TC            AT%M436.0      :BOOL; (*照明控制箱01X0H-定时控制*)"]
["照明控制箱","L","M","02X0H","定时控制","438.0",null,"验证通过","BOOL","照明控制箱02X0H-定时控制",{"$f":"B430&VLOOKUP(A430,List!$B$3:$D$445,2,FALSE)&D430&\"_\"&VLOOKUP(E430,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0H_TC"},"LLCB02X0H_TC AT%M438.0 :BOOL; (*照明控制箱02X0H-定时控制*)","LLCB02X0H_TC            AT%M438.0      :BOOL; (*照明控制箱02X0H-定时控制*)"]
["照明控制箱","L","M","03X0H","定时控制","440.0",null,"验证通过","BOOL","照明控制箱03X0H-定时控制",{"$f":"B431&VLOOKUP(A431,List!$B$3:$D$445,2,FALSE)&D431&\"_\"&VLOOKUP(E431,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0H_TC"},"LLCB03X0H_TC AT%M440.0 :BOOL; (*照明控制箱03X0H-定时控制*)","LLCB03X0H_TC            AT%M440.0      :BOOL; (*照明控制箱03X0H-定时控制*)"]
["照明控制箱","L","M","04X0H","定时控制","442.0",null,"验证通过","BOOL","照明控制箱04X0H-定时控制",{"$f":"B432&VLOOKUP(A432,List!$B$3:$D$445,2,FALSE)&D432&\"_\"&VLOOKUP(E432,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0H_TC"},"LLCB04X0H_TC AT%M442.0 :BOOL; (*照明控制箱04X0H-定时控制*)","LLCB04X0H_TC            AT%M442.0      :BOOL; (*照明控制箱04X0H-定时控制*)"]
["照明控制箱","L","M","05X0H","定时控制","444.0",null,"验证通过","BOOL","照明控制箱05X0H-定时控制",{"$f":"B433&VLOOKUP(A433,List!$B$3:$D$445,2,FALSE)&D433&\"_\"&VLOOKUP(E433,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0H_TC"},"LLCB05X0H_TC AT%M444.0 :BOOL; (*照明控制箱05X0H-定时控制*)","LLCB05X0H_TC            AT%M444.0      :BOOL; (*照明控制箱05X0H-定时控制*)"]
["照明控制箱","L","M","06X0H","定时控制","446.0",null,"验证通过","BOOL","照明控制箱06X0H-定时控制",{"$f":"B434&VLOOKUP(A434,List!$B$3:$D$445,2,FALSE)&D434&\"_\"&VLOOKUP(E434,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0H_TC"},"LLCB06X0H_TC AT%M446.0 :BOOL; (*照明控制箱06X0H-定时控制*)","LLCB06X0H_TC            AT%M446.0      :BOOL; (*照明控制箱06X0H-定时控制*)"]
["照明控制箱","L","M","07X0H","定时控制","448.0",null,{"$f":"IF((IF(OR(I435=\"INT\",I435=\"WORD\",I435=\"BOOL\"),MOD(F435,2),MOD(F435,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A435&D435&\"-\"&E435","v":"照明控制箱07X0H-定时控制"},{"$f":"B435&VLOOKUP(A435,List!$B$3:$D$445,2,FALSE)&D435&\"_\"&VLOOKUP(E435,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0H_TC"},{"$f":"K435&\" \"&\"AT%\"&C435&F435&\" \"&\":\"&I435&\";\"&\" \"&\"(*\"&J435&\"*)\"","v":"LLCB07X0H_TC AT%M448.0 :BOOL; (*照明控制箱07X0H-定时控制*)"},{"$f":"REPLACE(REPLACE(L435,SEARCH(\"AT%\",L435),,REPT(\" \",25-SEARCH(\"AT%\",L435))),SEARCH(\":\",REPLACE(L435,SEARCH(\"AT%\",L435),,REPT(\" \",25-SEARCH(\"AT%\",L435)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L435,SEARCH(\"AT%\",L435),,REPT(\" \",25-SEARCH(\"AT%\",L435))))))","v":"LLCB07X0H_TC            AT%M448.0      :BOOL; (*照明控制箱07X0H-定时控制*)"}]
["照明控制箱","L","M","08X0H","定时控制","450.0",null,"验证通过","BOOL","照明控制箱08X0H-定时控制",{"$f":"B436&VLOOKUP(A436,List!$B$3:$D$445,2,FALSE)&D436&\"_\"&VLOOKUP(E436,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0H_TC"},"LLCB08X0H_TC AT%M450.0 :BOOL; (*照明控制箱08X0H-定时控制*)","LLCB08X0H_TC            AT%M450.0      :BOOL; (*照明控制箱08X0H-定时控制*)"]
["照明控制箱","L","M","B3X0A","定时模式","452.0",null,"验证通过","BOOL","照明控制箱B3X0A-定时模式",{"$f":"B437&VLOOKUP(A437,List!$B$3:$D$445,2,FALSE)&D437&\"_\"&VLOOKUP(E437,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0A_TM"},"LLCBB3X0A_TM AT%M452.0 :BOOL; (*照明控制箱B3X0A-定时模式*)","LLCBB3X0A_TM            AT%M452.0      :BOOL; (*照明控制箱B3X0A-定时模式*)"]
["照明控制箱","L","M","B2X0A","定时模式","454.0",null,"验证通过","BOOL","照明控制箱B2X0A-定时模式",{"$f":"B438&VLOOKUP(A438,List!$B$3:$D$445,2,FALSE)&D438&\"_\"&VLOOKUP(E438,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0A_TM"},"LLCBB2X0A_TM AT%M454.0 :BOOL; (*照明控制箱B2X0A-定时模式*)","LLCBB2X0A_TM            AT%M454.0      :BOOL; (*照明控制箱B2X0A-定时模式*)"]
["照明控制箱","L","M","B1X0A","定时模式","456.0",null,"验证通过","BOOL","照明控制箱B1X0A-定时模式",{"$f":"B439&VLOOKUP(A439,List!$B$3:$D$445,2,FALSE)&D439&\"_\"&VLOOKUP(E439,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0A_TM"},"LLCBB1X0A_TM AT%M456.0 :BOOL; (*照明控制箱B1X0A-定时模式*)","LLCBB1X0A_TM            AT%M456.0      :BOOL; (*照明控制箱B1X0A-定时模式*)"]
["照明控制箱","L","M","01X0A","定时模式","458.0",null,"验证通过","BOOL","照明控制箱01X0A-定时模式",{"$f":"B440&VLOOKUP(A440,List!$B$3:$D$445,2,FALSE)&D440&\"_\"&VLOOKUP(E440,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0A_TM"},"LLCB01X0A_TM AT%M458.0 :BOOL; (*照明控制箱01X0A-定时模式*)","LLCB01X0A_TM            AT%M458.0      :BOOL; (*照明控制箱01X0A-定时模式*)"]
["照明控制箱","L","M","02X0A","定时模式","460.0",null,"验证通过","BOOL","照明控制箱02X0A-定时模式",{"$f":"B441&VLOOKUP(A441,List!$B$3:$D$445,2,FALSE)&D441&\"_\"&VLOOKUP(E441,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0A_TM"},"LLCB02X0A_TM AT%M460.0 :BOOL; (*照明控制箱02X0A-定时模式*)","LLCB02X0A_TM            AT%M460.0      :BOOL; (*照明控制箱02X0A-定时模式*)"]
["照明控制箱","L","M","03X0A","定时模式","462.0",null,"验证通过","BOOL","照明控制箱03X0A-定时模式",{"$f":"B442&VLOOKUP(A442,List!$B$3:$D$445,2,FALSE)&D442&\"_\"&VLOOKUP(E442,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0A_TM"},"LLCB03X0A_TM AT%M462.0 :BOOL; (*照明控制箱03X0A-定时模式*)","LLCB03X0A_TM            AT%M462.0      :BOOL; (*照明控制箱03X0A-定时模式*)"]
["照明控制箱","L","M","04X0A","定时模式","464.0",null,"验证通过","BOOL","照明控制箱04X0A-定时模式",{"$f":"B443&VLOOKUP(A443,List!$B$3:$D$445,2,FALSE)&D443&\"_\"&VLOOKUP(E443,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0A_TM"},"LLCB04X0A_TM AT%M464.0 :BOOL; (*照明控制箱04X0A-定时模式*)","LLCB04X0A_TM            AT%M464.0      :BOOL; (*照明控制箱04X0A-定时模式*)"]
["照明控制箱","L","M","05X0A","定时模式","466.0",null,"验证通过","BOOL","照明控制箱05X0A-定时模式",{"$f":"B444&VLOOKUP(A444,List!$B$3:$D$445,2,FALSE)&D444&\"_\"&VLOOKUP(E444,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0A_TM"},"LLCB05X0A_TM AT%M466.0 :BOOL; (*照明控制箱05X0A-定时模式*)","LLCB05X0A_TM            AT%M466.0      :BOOL; (*照明控制箱05X0A-定时模式*)"]
["照明控制箱","L","M","06X0A","定时模式","468.0",null,"验证通过","BOOL","照明控制箱06X0A-定时模式",{"$f":"B445&VLOOKUP(A445,List!$B$3:$D$445,2,FALSE)&D445&\"_\"&VLOOKUP(E445,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0A_TM"},"LLCB06X0A_TM AT%M468.0 :BOOL; (*照明控制箱06X0A-定时模式*)","LLCB06X0A_TM            AT%M468.0      :BOOL; (*照明控制箱06X0A-定时模式*)"]
["照明控制箱","L","M","07X0A","定时模式","470.0",null,{"$f":"IF((IF(OR(I446=\"INT\",I446=\"WORD\",I446=\"BOOL\"),MOD(F446,2),MOD(F446,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A446&D446&\"-\"&E446","v":"照明控制箱07X0A-定时模式"},{"$f":"B446&VLOOKUP(A446,List!$B$3:$D$445,2,FALSE)&D446&\"_\"&VLOOKUP(E446,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0A_TM"},{"$f":"K446&\" \"&\"AT%\"&C446&F446&\" \"&\":\"&I446&\";\"&\" \"&\"(*\"&J446&\"*)\"","v":"LLCB07X0A_TM AT%M470.0 :BOOL; (*照明控制箱07X0A-定时模式*)"},{"$f":"REPLACE(REPLACE(L446,SEARCH(\"AT%\",L446),,REPT(\" \",25-SEARCH(\"AT%\",L446))),SEARCH(\":\",REPLACE(L446,SEARCH(\"AT%\",L446),,REPT(\" \",25-SEARCH(\"AT%\",L446)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L446,SEARCH(\"AT%\",L446),,REPT(\" \",25-SEARCH(\"AT%\",L446))))))","v":"LLCB07X0A_TM            AT%M470.0      :BOOL; (*照明控制箱07X0A-定时模式*)"}]
["照明控制箱","L","M","08X0A","定时模式","472.0",null,"验证通过","BOOL","照明控制箱08X0A-定时模式",{"$f":"B447&VLOOKUP(A447,List!$B$3:$D$445,2,FALSE)&D447&\"_\"&VLOOKUP(E447,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0A_TM"},"LLCB08X0A_TM AT%M472.0 :BOOL; (*照明控制箱08X0A-定时模式*)","LLCB08X0A_TM            AT%M472.0      :BOOL; (*照明控制箱08X0A-定时模式*)"]
["照明控制箱","L","M","B3X0B","定时模式","474.0",null,"验证通过","BOOL","照明控制箱B3X0B-定时模式",{"$f":"B448&VLOOKUP(A448,List!$B$3:$D$445,2,FALSE)&D448&\"_\"&VLOOKUP(E448,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0B_TM"},"LLCBB3X0B_TM AT%M474.0 :BOOL; (*照明控制箱B3X0B-定时模式*)","LLCBB3X0B_TM            AT%M474.0      :BOOL; (*照明控制箱B3X0B-定时模式*)"]
["照明控制箱","L","M","B2X0B","定时模式","476.0",null,"验证通过","BOOL","照明控制箱B2X0B-定时模式",{"$f":"B449&VLOOKUP(A449,List!$B$3:$D$445,2,FALSE)&D449&\"_\"&VLOOKUP(E449,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0B_TM"},"LLCBB2X0B_TM AT%M476.0 :BOOL; (*照明控制箱B2X0B-定时模式*)","LLCBB2X0B_TM            AT%M476.0      :BOOL; (*照明控制箱B2X0B-定时模式*)"]
["照明控制箱","L","M","B1X0B","定时模式","478.0",null,"验证通过","BOOL","照明控制箱B1X0B-定时模式",{"$f":"B450&VLOOKUP(A450,List!$B$3:$D$445,2,FALSE)&D450&\"_\"&VLOOKUP(E450,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0B_TM"},"LLCBB1X0B_TM AT%M478.0 :BOOL; (*照明控制箱B1X0B-定时模式*)","LLCBB1X0B_TM            AT%M478.0      :BOOL; (*照明控制箱B1X0B-定时模式*)"]
["照明控制箱","L","M","01X0B","定时模式","480.0",null,"验证通过","BOOL","照明控制箱01X0B-定时模式",{"$f":"B451&VLOOKUP(A451,List!$B$3:$D$445,2,FALSE)&D451&\"_\"&VLOOKUP(E451,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0B_TM"},"LLCB01X0B_TM AT%M480.0 :BOOL; (*照明控制箱01X0B-定时模式*)","LLCB01X0B_TM            AT%M480.0      :BOOL; (*照明控制箱01X0B-定时模式*)"]
["照明控制箱","L","M","02X0B","定时模式","482.0",null,"验证通过","BOOL","照明控制箱02X0B-定时模式",{"$f":"B452&VLOOKUP(A452,List!$B$3:$D$445,2,FALSE)&D452&\"_\"&VLOOKUP(E452,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0B_TM"},"LLCB02X0B_TM AT%M482.0 :BOOL; (*照明控制箱02X0B-定时模式*)","LLCB02X0B_TM            AT%M482.0      :BOOL; (*照明控制箱02X0B-定时模式*)"]
["照明控制箱","L","M","03X0B","定时模式","484.0",null,"验证通过","BOOL","照明控制箱03X0B-定时模式",{"$f":"B453&VLOOKUP(A453,List!$B$3:$D$445,2,FALSE)&D453&\"_\"&VLOOKUP(E453,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0B_TM"},"LLCB03X0B_TM AT%M484.0 :BOOL; (*照明控制箱03X0B-定时模式*)","LLCB03X0B_TM            AT%M484.0      :BOOL; (*照明控制箱03X0B-定时模式*)"]
["照明控制箱","L","M","04X0B","定时模式","486.0",null,"验证通过","BOOL","照明控制箱04X0B-定时模式",{"$f":"B454&VLOOKUP(A454,List!$B$3:$D$445,2,FALSE)&D454&\"_\"&VLOOKUP(E454,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0B_TM"},"LLCB04X0B_TM AT%M486.0 :BOOL; (*照明控制箱04X0B-定时模式*)","LLCB04X0B_TM            AT%M486.0      :BOOL; (*照明控制箱04X0B-定时模式*)"]
["照明控制箱","L","M","05X0B","定时模式","488.0",null,"验证通过","BOOL","照明控制箱05X0B-定时模式",{"$f":"B455&VLOOKUP(A455,List!$B$3:$D$445,2,FALSE)&D455&\"_\"&VLOOKUP(E455,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0B_TM"},"LLCB05X0B_TM AT%M488.0 :BOOL; (*照明控制箱05X0B-定时模式*)","LLCB05X0B_TM            AT%M488.0      :BOOL; (*照明控制箱05X0B-定时模式*)"]
["照明控制箱","L","M","06X0B","定时模式","490.0",null,"验证通过","BOOL","照明控制箱06X0B-定时模式",{"$f":"B456&VLOOKUP(A456,List!$B$3:$D$445,2,FALSE)&D456&\"_\"&VLOOKUP(E456,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0B_TM"},"LLCB06X0B_TM AT%M490.0 :BOOL; (*照明控制箱06X0B-定时模式*)","LLCB06X0B_TM            AT%M490.0      :BOOL; (*照明控制箱06X0B-定时模式*)"]
["照明控制箱","L","M","07X0B","定时模式","492.0",null,{"$f":"IF((IF(OR(I457=\"INT\",I457=\"WORD\",I457=\"BOOL\"),MOD(F457,2),MOD(F457,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A457&D457&\"-\"&E457","v":"照明控制箱07X0B-定时模式"},{"$f":"B457&VLOOKUP(A457,List!$B$3:$D$445,2,FALSE)&D457&\"_\"&VLOOKUP(E457,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0B_TM"},{"$f":"K457&\" \"&\"AT%\"&C457&F457&\" \"&\":\"&I457&\";\"&\" \"&\"(*\"&J457&\"*)\"","v":"LLCB07X0B_TM AT%M492.0 :BOOL; (*照明控制箱07X0B-定时模式*)"},{"$f":"REPLACE(REPLACE(L457,SEARCH(\"AT%\",L457),,REPT(\" \",25-SEARCH(\"AT%\",L457))),SEARCH(\":\",REPLACE(L457,SEARCH(\"AT%\",L457),,REPT(\" \",25-SEARCH(\"AT%\",L457)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L457,SEARCH(\"AT%\",L457),,REPT(\" \",25-SEARCH(\"AT%\",L457))))))","v":"LLCB07X0B_TM            AT%M492.0      :BOOL; (*照明控制箱07X0B-定时模式*)"}]
["照明控制箱","L","M","08X0B","定时模式","494.0",null,"验证通过","BOOL","照明控制箱08X0B-定时模式",{"$f":"B458&VLOOKUP(A458,List!$B$3:$D$445,2,FALSE)&D458&\"_\"&VLOOKUP(E458,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0B_TM"},"LLCB08X0B_TM AT%M494.0 :BOOL; (*照明控制箱08X0B-定时模式*)","LLCB08X0B_TM            AT%M494.0      :BOOL; (*照明控制箱08X0B-定时模式*)"]
["照明控制箱","L","M","B3X0C","定时模式","496.0",null,"验证通过","BOOL","照明控制箱B3X0C-定时模式",{"$f":"B459&VLOOKUP(A459,List!$B$3:$D$445,2,FALSE)&D459&\"_\"&VLOOKUP(E459,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0C_TM"},"LLCBB3X0C_TM AT%M496.0 :BOOL; (*照明控制箱B3X0C-定时模式*)","LLCBB3X0C_TM            AT%M496.0      :BOOL; (*照明控制箱B3X0C-定时模式*)"]
["照明控制箱","L","M","B2X0C","定时模式","498.0",null,"验证通过","BOOL","照明控制箱B2X0C-定时模式",{"$f":"B460&VLOOKUP(A460,List!$B$3:$D$445,2,FALSE)&D460&\"_\"&VLOOKUP(E460,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0C_TM"},"LLCBB2X0C_TM AT%M498.0 :BOOL; (*照明控制箱B2X0C-定时模式*)","LLCBB2X0C_TM            AT%M498.0      :BOOL; (*照明控制箱B2X0C-定时模式*)"]
["照明控制箱","L","M","B1X0C","定时模式","500.0",null,"验证通过","BOOL","照明控制箱B1X0C-定时模式",{"$f":"B461&VLOOKUP(A461,List!$B$3:$D$445,2,FALSE)&D461&\"_\"&VLOOKUP(E461,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0C_TM"},{"$f":"K461&\" \"&\"AT%\"&C461&F461&\" \"&\":\"&I461&\";\"&\" \"&\"(*\"&J461&\"*)\"","v":"LLCBB1X0C_TM AT%M500.0 :BOOL; (*照明控制箱B1X0C-定时模式*)"},{"$f":"REPLACE(REPLACE(L461,SEARCH(\"AT%\",L461),,REPT(\" \",25-SEARCH(\"AT%\",L461))),SEARCH(\":\",REPLACE(L461,SEARCH(\"AT%\",L461),,REPT(\" \",25-SEARCH(\"AT%\",L461)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L461,SEARCH(\"AT%\",L461),,REPT(\" \",25-SEARCH(\"AT%\",L461))))))","v":"LLCBB1X0C_TM            AT%M500.0      :BOOL; (*照明控制箱B1X0C-定时模式*)"}]
["照明控制箱","L","M","01X0C","定时模式","502.0",null,"验证通过","BOOL","照明控制箱01X0C-定时模式",{"$f":"B462&VLOOKUP(A462,List!$B$3:$D$445,2,FALSE)&D462&\"_\"&VLOOKUP(E462,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0C_TM"},"LLCB01X0C_TM AT%M502.0 :BOOL; (*照明控制箱01X0C-定时模式*)","LLCB01X0C_TM            AT%M502.0      :BOOL; (*照明控制箱01X0C-定时模式*)"]
["照明控制箱","L","M","02X0C","定时模式","504.0",null,"验证通过","BOOL","照明控制箱02X0C-定时模式",{"$f":"B463&VLOOKUP(A463,List!$B$3:$D$445,2,FALSE)&D463&\"_\"&VLOOKUP(E463,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0C_TM"},"LLCB02X0C_TM AT%M504.0 :BOOL; (*照明控制箱02X0C-定时模式*)","LLCB02X0C_TM            AT%M504.0      :BOOL; (*照明控制箱02X0C-定时模式*)"]
["照明控制箱","L","M","03X0C","定时模式","506.0",null,"验证通过","BOOL","照明控制箱03X0C-定时模式",{"$f":"B464&VLOOKUP(A464,List!$B$3:$D$445,2,FALSE)&D464&\"_\"&VLOOKUP(E464,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0C_TM"},"LLCB03X0C_TM AT%M506.0 :BOOL; (*照明控制箱03X0C-定时模式*)","LLCB03X0C_TM            AT%M506.0      :BOOL; (*照明控制箱03X0C-定时模式*)"]
["照明控制箱","L","M","04X0C","定时模式","508.0",null,"验证通过","BOOL","照明控制箱04X0C-定时模式",{"$f":"B465&VLOOKUP(A465,List!$B$3:$D$445,2,FALSE)&D465&\"_\"&VLOOKUP(E465,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0C_TM"},"LLCB04X0C_TM AT%M508.0 :BOOL; (*照明控制箱04X0C-定时模式*)","LLCB04X0C_TM            AT%M508.0      :BOOL; (*照明控制箱04X0C-定时模式*)"]
["照明控制箱","L","M","05X0C","定时模式","510.0",null,"验证通过","BOOL","照明控制箱05X0C-定时模式",{"$f":"B466&VLOOKUP(A466,List!$B$3:$D$445,2,FALSE)&D466&\"_\"&VLOOKUP(E466,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0C_TM"},"LLCB05X0C_TM AT%M510.0 :BOOL; (*照明控制箱05X0C-定时模式*)","LLCB05X0C_TM            AT%M510.0      :BOOL; (*照明控制箱05X0C-定时模式*)"]
["照明控制箱","L","M","06X0C","定时模式","512.0",null,"验证通过","BOOL","照明控制箱06X0C-定时模式",{"$f":"B467&VLOOKUP(A467,List!$B$3:$D$445,2,FALSE)&D467&\"_\"&VLOOKUP(E467,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0C_TM"},"LLCB06X0C_TM AT%M512.0 :BOOL; (*照明控制箱06X0C-定时模式*)","LLCB06X0C_TM            AT%M512.0      :BOOL; (*照明控制箱06X0C-定时模式*)"]
["照明控制箱","L","M","07X0C","定时模式",{"$f":"IF(OR(I467=\"REAL\",I467=\"DWORD\",I467=\"DINT\"),(IF(OR(I468=\"REAL\",I468=\"DWORD\",I468=\"DINT\"),F467+4+MOD(F467,4),F467+4)),(IF(OR(I468=\"REAL\",I468=\"DWORD\",I468=\"DINT\"),F467+4+MOD(F467,4),F467+2)))&\".0\"","v":"514.0"},null,{"$f":"IF((IF(OR(I468=\"INT\",I468=\"WORD\",I468=\"BOOL\"),MOD(F468,2),MOD(F468,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A468&D468&\"-\"&E468","v":"照明控制箱07X0C-定时模式"},{"$f":"B468&VLOOKUP(A468,List!$B$3:$D$445,2,FALSE)&D468&\"_\"&VLOOKUP(E468,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0C_TM"},{"$f":"K468&\" \"&\"AT%\"&C468&F468&\" \"&\":\"&I468&\";\"&\" \"&\"(*\"&J468&\"*)\"","v":"LLCB07X0C_TM AT%M514.0 :BOOL; (*照明控制箱07X0C-定时模式*)"},{"$f":"REPLACE(REPLACE(L468,SEARCH(\"AT%\",L468),,REPT(\" \",25-SEARCH(\"AT%\",L468))),SEARCH(\":\",REPLACE(L468,SEARCH(\"AT%\",L468),,REPT(\" \",25-SEARCH(\"AT%\",L468)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L468,SEARCH(\"AT%\",L468),,REPT(\" \",25-SEARCH(\"AT%\",L468))))))","v":"LLCB07X0C_TM            AT%M514.0      :BOOL; (*照明控制箱07X0C-定时模式*)"}]
["照明控制箱","L","M","08X0C","定时模式","516.0",null,"验证通过","BOOL","照明控制箱08X0C-定时模式",{"$f":"B469&VLOOKUP(A469,List!$B$3:$D$445,2,FALSE)&D469&\"_\"&VLOOKUP(E469,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0C_TM"},"LLCB08X0C_TM AT%M516.0 :BOOL; (*照明控制箱08X0C-定时模式*)","LLCB08X0C_TM            AT%M516.0      :BOOL; (*照明控制箱08X0C-定时模式*)"]
["照明控制箱","L","M","B3X0D","定时模式","518.0",null,"验证通过","BOOL","照明控制箱B3X0D-定时模式",{"$f":"B470&VLOOKUP(A470,List!$B$3:$D$445,2,FALSE)&D470&\"_\"&VLOOKUP(E470,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0D_TM"},"LLCBB3X0D_TM AT%M518.0 :BOOL; (*照明控制箱B3X0D-定时模式*)","LLCBB3X0D_TM            AT%M518.0      :BOOL; (*照明控制箱B3X0D-定时模式*)"]
["照明控制箱","L","M","B2X0D","定时模式","520.0",null,"验证通过","BOOL","照明控制箱B2X0D-定时模式",{"$f":"B471&VLOOKUP(A471,List!$B$3:$D$445,2,FALSE)&D471&\"_\"&VLOOKUP(E471,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0D_TM"},"LLCBB2X0D_TM AT%M520.0 :BOOL; (*照明控制箱B2X0D-定时模式*)","LLCBB2X0D_TM            AT%M520.0      :BOOL; (*照明控制箱B2X0D-定时模式*)"]
["照明控制箱","L","M","B1X0D","定时模式","522.0",null,"验证通过","BOOL","照明控制箱B1X0D-定时模式",{"$f":"B472&VLOOKUP(A472,List!$B$3:$D$445,2,FALSE)&D472&\"_\"&VLOOKUP(E472,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0D_TM"},"LLCBB1X0D_TM AT%M522.0 :BOOL; (*照明控制箱B1X0D-定时模式*)","LLCBB1X0D_TM            AT%M522.0      :BOOL; (*照明控制箱B1X0D-定时模式*)"]
["照明控制箱","L","M","01X0D","定时模式","524.0",null,"验证通过","BOOL","照明控制箱01X0D-定时模式",{"$f":"B473&VLOOKUP(A473,List!$B$3:$D$445,2,FALSE)&D473&\"_\"&VLOOKUP(E473,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0D_TM"},"LLCB01X0D_TM AT%M524.0 :BOOL; (*照明控制箱01X0D-定时模式*)","LLCB01X0D_TM            AT%M524.0      :BOOL; (*照明控制箱01X0D-定时模式*)"]
["照明控制箱","L","M","02X0D","定时模式","526.0",null,"验证通过","BOOL","照明控制箱02X0D-定时模式",{"$f":"B474&VLOOKUP(A474,List!$B$3:$D$445,2,FALSE)&D474&\"_\"&VLOOKUP(E474,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0D_TM"},"LLCB02X0D_TM AT%M526.0 :BOOL; (*照明控制箱02X0D-定时模式*)","LLCB02X0D_TM            AT%M526.0      :BOOL; (*照明控制箱02X0D-定时模式*)"]
["照明控制箱","L","M","03X0D","定时模式","528.0",null,"验证通过","BOOL","照明控制箱03X0D-定时模式",{"$f":"B475&VLOOKUP(A475,List!$B$3:$D$445,2,FALSE)&D475&\"_\"&VLOOKUP(E475,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0D_TM"},"LLCB03X0D_TM AT%M528.0 :BOOL; (*照明控制箱03X0D-定时模式*)","LLCB03X0D_TM            AT%M528.0      :BOOL; (*照明控制箱03X0D-定时模式*)"]
["照明控制箱","L","M","04X0D","定时模式","530.0",null,"验证通过","BOOL","照明控制箱04X0D-定时模式",{"$f":"B476&VLOOKUP(A476,List!$B$3:$D$445,2,FALSE)&D476&\"_\"&VLOOKUP(E476,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0D_TM"},"LLCB04X0D_TM AT%M530.0 :BOOL; (*照明控制箱04X0D-定时模式*)","LLCB04X0D_TM            AT%M530.0      :BOOL; (*照明控制箱04X0D-定时模式*)"]
["照明控制箱","L","M","05X0D","定时模式","532.0",null,"验证通过","BOOL","照明控制箱05X0D-定时模式",{"$f":"B477&VLOOKUP(A477,List!$B$3:$D$445,2,FALSE)&D477&\"_\"&VLOOKUP(E477,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0D_TM"},"LLCB05X0D_TM AT%M532.0 :BOOL; (*照明控制箱05X0D-定时模式*)","LLCB05X0D_TM            AT%M532.0      :BOOL; (*照明控制箱05X0D-定时模式*)"]
["照明控制箱","L","M","06X0D","定时模式","534.0",null,"验证通过","BOOL","照明控制箱06X0D-定时模式",{"$f":"B478&VLOOKUP(A478,List!$B$3:$D$445,2,FALSE)&D478&\"_\"&VLOOKUP(E478,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0D_TM"},"LLCB06X0D_TM AT%M534.0 :BOOL; (*照明控制箱06X0D-定时模式*)","LLCB06X0D_TM            AT%M534.0      :BOOL; (*照明控制箱06X0D-定时模式*)"]
["照明控制箱","L","M","07X0D","定时模式","536.0",null,{"$f":"IF((IF(OR(I479=\"INT\",I479=\"WORD\",I479=\"BOOL\"),MOD(F479,2),MOD(F479,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A479&D479&\"-\"&E479","v":"照明控制箱07X0D-定时模式"},{"$f":"B479&VLOOKUP(A479,List!$B$3:$D$445,2,FALSE)&D479&\"_\"&VLOOKUP(E479,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0D_TM"},{"$f":"K479&\" \"&\"AT%\"&C479&F479&\" \"&\":\"&I479&\";\"&\" \"&\"(*\"&J479&\"*)\"","v":"LLCB07X0D_TM AT%M536.0 :BOOL; (*照明控制箱07X0D-定时模式*)"},{"$f":"REPLACE(REPLACE(L479,SEARCH(\"AT%\",L479),,REPT(\" \",25-SEARCH(\"AT%\",L479))),SEARCH(\":\",REPLACE(L479,SEARCH(\"AT%\",L479),,REPT(\" \",25-SEARCH(\"AT%\",L479)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L479,SEARCH(\"AT%\",L479),,REPT(\" \",25-SEARCH(\"AT%\",L479))))))","v":"LLCB07X0D_TM            AT%M536.0      :BOOL; (*照明控制箱07X0D-定时模式*)"}]
["照明控制箱","L","M","08X0D","定时模式","538.0",null,"验证通过","BOOL","照明控制箱08X0D-定时模式",{"$f":"B480&VLOOKUP(A480,List!$B$3:$D$445,2,FALSE)&D480&\"_\"&VLOOKUP(E480,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0D_TM"},"LLCB08X0D_TM AT%M538.0 :BOOL; (*照明控制箱08X0D-定时模式*)","LLCB08X0D_TM            AT%M538.0      :BOOL; (*照明控制箱08X0D-定时模式*)"]
["照明控制箱","L","M","B3X0E","定时模式","540.0",null,"验证通过","BOOL","照明控制箱B3X0E-定时模式",{"$f":"B481&VLOOKUP(A481,List!$B$3:$D$445,2,FALSE)&D481&\"_\"&VLOOKUP(E481,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0E_TM"},"LLCBB3X0E_TM AT%M540.0 :BOOL; (*照明控制箱B3X0E-定时模式*)","LLCBB3X0E_TM            AT%M540.0      :BOOL; (*照明控制箱B3X0E-定时模式*)"]
["照明控制箱","L","M","B2X0E","定时模式","542.0",null,"验证通过","BOOL","照明控制箱B2X0E-定时模式",{"$f":"B482&VLOOKUP(A482,List!$B$3:$D$445,2,FALSE)&D482&\"_\"&VLOOKUP(E482,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0E_TM"},"LLCBB2X0E_TM AT%M542.0 :BOOL; (*照明控制箱B2X0E-定时模式*)","LLCBB2X0E_TM            AT%M542.0      :BOOL; (*照明控制箱B2X0E-定时模式*)"]
["照明控制箱","L","M","B1X0E","定时模式","544.0",null,"验证通过","BOOL","照明控制箱B1X0E-定时模式",{"$f":"B483&VLOOKUP(A483,List!$B$3:$D$445,2,FALSE)&D483&\"_\"&VLOOKUP(E483,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0E_TM"},"LLCBB1X0E_TM AT%M544.0 :BOOL; (*照明控制箱B1X0E-定时模式*)","LLCBB1X0E_TM            AT%M544.0      :BOOL; (*照明控制箱B1X0E-定时模式*)"]
["照明控制箱","L","M","01X0E","定时模式","546.0",null,"验证通过","BOOL","照明控制箱01X0E-定时模式",{"$f":"B484&VLOOKUP(A484,List!$B$3:$D$445,2,FALSE)&D484&\"_\"&VLOOKUP(E484,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0E_TM"},"LLCB01X0E_TM AT%M546.0 :BOOL; (*照明控制箱01X0E-定时模式*)","LLCB01X0E_TM            AT%M546.0      :BOOL; (*照明控制箱01X0E-定时模式*)"]
["照明控制箱","L","M","02X0E","定时模式","548.0",null,"验证通过","BOOL","照明控制箱02X0E-定时模式",{"$f":"B485&VLOOKUP(A485,List!$B$3:$D$445,2,FALSE)&D485&\"_\"&VLOOKUP(E485,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0E_TM"},"LLCB02X0E_TM AT%M548.0 :BOOL; (*照明控制箱02X0E-定时模式*)","LLCB02X0E_TM            AT%M548.0      :BOOL; (*照明控制箱02X0E-定时模式*)"]
["照明控制箱","L","M","03X0E","定时模式","550.0",null,"验证通过","BOOL","照明控制箱03X0E-定时模式",{"$f":"B486&VLOOKUP(A486,List!$B$3:$D$445,2,FALSE)&D486&\"_\"&VLOOKUP(E486,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0E_TM"},"LLCB03X0E_TM AT%M550.0 :BOOL; (*照明控制箱03X0E-定时模式*)","LLCB03X0E_TM            AT%M550.0      :BOOL; (*照明控制箱03X0E-定时模式*)"]
["照明控制箱","L","M","04X0E","定时模式","552.0",null,"验证通过","BOOL","照明控制箱04X0E-定时模式",{"$f":"B487&VLOOKUP(A487,List!$B$3:$D$445,2,FALSE)&D487&\"_\"&VLOOKUP(E487,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0E_TM"},"LLCB04X0E_TM AT%M552.0 :BOOL; (*照明控制箱04X0E-定时模式*)","LLCB04X0E_TM            AT%M552.0      :BOOL; (*照明控制箱04X0E-定时模式*)"]
["照明控制箱","L","M","05X0E","定时模式","554.0",null,"验证通过","BOOL","照明控制箱05X0E-定时模式",{"$f":"B488&VLOOKUP(A488,List!$B$3:$D$445,2,FALSE)&D488&\"_\"&VLOOKUP(E488,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0E_TM"},"LLCB05X0E_TM AT%M554.0 :BOOL; (*照明控制箱05X0E-定时模式*)","LLCB05X0E_TM            AT%M554.0      :BOOL; (*照明控制箱05X0E-定时模式*)"]
["照明控制箱","L","M","06X0E","定时模式","556.0",null,"验证通过","BOOL","照明控制箱06X0E-定时模式",{"$f":"B489&VLOOKUP(A489,List!$B$3:$D$445,2,FALSE)&D489&\"_\"&VLOOKUP(E489,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0E_TM"},"LLCB06X0E_TM AT%M556.0 :BOOL; (*照明控制箱06X0E-定时模式*)","LLCB06X0E_TM            AT%M556.0      :BOOL; (*照明控制箱06X0E-定时模式*)"]
["照明控制箱","L","M","07X0E","定时模式","558.0",null,{"$f":"IF((IF(OR(I490=\"INT\",I490=\"WORD\",I490=\"BOOL\"),MOD(F490,2),MOD(F490,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A490&D490&\"-\"&E490","v":"照明控制箱07X0E-定时模式"},{"$f":"B490&VLOOKUP(A490,List!$B$3:$D$445,2,FALSE)&D490&\"_\"&VLOOKUP(E490,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0E_TM"},{"$f":"K490&\" \"&\"AT%\"&C490&F490&\" \"&\":\"&I490&\";\"&\" \"&\"(*\"&J490&\"*)\"","v":"LLCB07X0E_TM AT%M558.0 :BOOL; (*照明控制箱07X0E-定时模式*)"},{"$f":"REPLACE(REPLACE(L490,SEARCH(\"AT%\",L490),,REPT(\" \",25-SEARCH(\"AT%\",L490))),SEARCH(\":\",REPLACE(L490,SEARCH(\"AT%\",L490),,REPT(\" \",25-SEARCH(\"AT%\",L490)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L490,SEARCH(\"AT%\",L490),,REPT(\" \",25-SEARCH(\"AT%\",L490))))))","v":"LLCB07X0E_TM            AT%M558.0      :BOOL; (*照明控制箱07X0E-定时模式*)"}]
["照明控制箱","L","M","08X0E","定时模式","560.0",null,"验证通过","BOOL","照明控制箱08X0E-定时模式",{"$f":"B491&VLOOKUP(A491,List!$B$3:$D$445,2,FALSE)&D491&\"_\"&VLOOKUP(E491,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0E_TM"},"LLCB08X0E_TM AT%M560.0 :BOOL; (*照明控制箱08X0E-定时模式*)","LLCB08X0E_TM            AT%M560.0      :BOOL; (*照明控制箱08X0E-定时模式*)"]
["照明控制箱","L","M","B3X0F","定时模式","562.0",null,"验证通过","BOOL","照明控制箱B3X0F-定时模式",{"$f":"B492&VLOOKUP(A492,List!$B$3:$D$445,2,FALSE)&D492&\"_\"&VLOOKUP(E492,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0F_TM"},"LLCBB3X0F_TM AT%M562.0 :BOOL; (*照明控制箱B3X0F-定时模式*)","LLCBB3X0F_TM            AT%M562.0      :BOOL; (*照明控制箱B3X0F-定时模式*)"]
["照明控制箱","L","M","B2X0F","定时模式","564.0",null,"验证通过","BOOL","照明控制箱B2X0F-定时模式",{"$f":"B493&VLOOKUP(A493,List!$B$3:$D$445,2,FALSE)&D493&\"_\"&VLOOKUP(E493,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0F_TM"},"LLCBB2X0F_TM AT%M564.0 :BOOL; (*照明控制箱B2X0F-定时模式*)","LLCBB2X0F_TM            AT%M564.0      :BOOL; (*照明控制箱B2X0F-定时模式*)"]
["照明控制箱","L","M","B1X0F","定时模式","566.0",null,"验证通过","BOOL","照明控制箱B1X0F-定时模式",{"$f":"B494&VLOOKUP(A494,List!$B$3:$D$445,2,FALSE)&D494&\"_\"&VLOOKUP(E494,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0F_TM"},"LLCBB1X0F_TM AT%M566.0 :BOOL; (*照明控制箱B1X0F-定时模式*)","LLCBB1X0F_TM            AT%M566.0      :BOOL; (*照明控制箱B1X0F-定时模式*)"]
["照明控制箱","L","M","01X0F","定时模式","568.0",null,"验证通过","BOOL","照明控制箱01X0F-定时模式",{"$f":"B495&VLOOKUP(A495,List!$B$3:$D$445,2,FALSE)&D495&\"_\"&VLOOKUP(E495,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0F_TM"},"LLCB01X0F_TM AT%M568.0 :BOOL; (*照明控制箱01X0F-定时模式*)","LLCB01X0F_TM            AT%M568.0      :BOOL; (*照明控制箱01X0F-定时模式*)"]
["照明控制箱","L","M","02X0F","定时模式","570.0",null,"验证通过","BOOL","照明控制箱02X0F-定时模式",{"$f":"B496&VLOOKUP(A496,List!$B$3:$D$445,2,FALSE)&D496&\"_\"&VLOOKUP(E496,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0F_TM"},"LLCB02X0F_TM AT%M570.0 :BOOL; (*照明控制箱02X0F-定时模式*)","LLCB02X0F_TM            AT%M570.0      :BOOL; (*照明控制箱02X0F-定时模式*)"]
["照明控制箱","L","M","03X0F","定时模式","572.0",null,"验证通过","BOOL","照明控制箱03X0F-定时模式",{"$f":"B497&VLOOKUP(A497,List!$B$3:$D$445,2,FALSE)&D497&\"_\"&VLOOKUP(E497,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0F_TM"},"LLCB03X0F_TM AT%M572.0 :BOOL; (*照明控制箱03X0F-定时模式*)","LLCB03X0F_TM            AT%M572.0      :BOOL; (*照明控制箱03X0F-定时模式*)"]
["照明控制箱","L","M","04X0F","定时模式","574.0",null,"验证通过","BOOL","照明控制箱04X0F-定时模式",{"$f":"B498&VLOOKUP(A498,List!$B$3:$D$445,2,FALSE)&D498&\"_\"&VLOOKUP(E498,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0F_TM"},"LLCB04X0F_TM AT%M574.0 :BOOL; (*照明控制箱04X0F-定时模式*)","LLCB04X0F_TM            AT%M574.0      :BOOL; (*照明控制箱04X0F-定时模式*)"]
["照明控制箱","L","M","05X0F","定时模式","576.0",null,"验证通过","BOOL","照明控制箱05X0F-定时模式",{"$f":"B499&VLOOKUP(A499,List!$B$3:$D$445,2,FALSE)&D499&\"_\"&VLOOKUP(E499,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0F_TM"},{"$f":"K499&\" \"&\"AT%\"&C499&F499&\" \"&\":\"&I499&\";\"&\" \"&\"(*\"&J499&\"*)\"","v":"LLCB05X0F_TM AT%M576.0 :BOOL; (*照明控制箱05X0F-定时模式*)"},{"$f":"REPLACE(REPLACE(L499,SEARCH(\"AT%\",L499),,REPT(\" \",25-SEARCH(\"AT%\",L499))),SEARCH(\":\",REPLACE(L499,SEARCH(\"AT%\",L499),,REPT(\" \",25-SEARCH(\"AT%\",L499)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L499,SEARCH(\"AT%\",L499),,REPT(\" \",25-SEARCH(\"AT%\",L499))))))","v":"LLCB05X0F_TM            AT%M576.0      :BOOL; (*照明控制箱05X0F-定时模式*)"}]
["照明控制箱","L","M","06X0F","定时模式","578.0",null,"验证通过","BOOL","照明控制箱06X0F-定时模式",{"$f":"B500&VLOOKUP(A500,List!$B$3:$D$445,2,FALSE)&D500&\"_\"&VLOOKUP(E500,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0F_TM"},"LLCB06X0F_TM AT%M578.0 :BOOL; (*照明控制箱06X0F-定时模式*)","LLCB06X0F_TM            AT%M578.0      :BOOL; (*照明控制箱06X0F-定时模式*)"]
["照明控制箱","L","M","07X0F","定时模式","580.0",null,{"$f":"IF((IF(OR(I501=\"INT\",I501=\"WORD\",I501=\"BOOL\"),MOD(F501,2),MOD(F501,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A501&D501&\"-\"&E501","v":"照明控制箱07X0F-定时模式"},{"$f":"B501&VLOOKUP(A501,List!$B$3:$D$445,2,FALSE)&D501&\"_\"&VLOOKUP(E501,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0F_TM"},{"$f":"K501&\" \"&\"AT%\"&C501&F501&\" \"&\":\"&I501&\";\"&\" \"&\"(*\"&J501&\"*)\"","v":"LLCB07X0F_TM AT%M580.0 :BOOL; (*照明控制箱07X0F-定时模式*)"},{"$f":"REPLACE(REPLACE(L501,SEARCH(\"AT%\",L501),,REPT(\" \",25-SEARCH(\"AT%\",L501))),SEARCH(\":\",REPLACE(L501,SEARCH(\"AT%\",L501),,REPT(\" \",25-SEARCH(\"AT%\",L501)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L501,SEARCH(\"AT%\",L501),,REPT(\" \",25-SEARCH(\"AT%\",L501))))))","v":"LLCB07X0F_TM            AT%M580.0      :BOOL; (*照明控制箱07X0F-定时模式*)"}]
["照明控制箱","L","M","08X0F","定时模式","582.0",null,"验证通过","BOOL","照明控制箱08X0F-定时模式",{"$f":"B502&VLOOKUP(A502,List!$B$3:$D$445,2,FALSE)&D502&\"_\"&VLOOKUP(E502,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0F_TM"},"LLCB08X0F_TM AT%M582.0 :BOOL; (*照明控制箱08X0F-定时模式*)","LLCB08X0F_TM            AT%M582.0      :BOOL; (*照明控制箱08X0F-定时模式*)"]
["照明控制箱","L","M","B3X0G","定时模式","584.0",null,"验证通过","BOOL","照明控制箱B3X0G-定时模式",{"$f":"B503&VLOOKUP(A503,List!$B$3:$D$445,2,FALSE)&D503&\"_\"&VLOOKUP(E503,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0G_TM"},"LLCBB3X0G_TM AT%M584.0 :BOOL; (*照明控制箱B3X0G-定时模式*)","LLCBB3X0G_TM            AT%M584.0      :BOOL; (*照明控制箱B3X0G-定时模式*)"]
["照明控制箱","L","M","B2X0G","定时模式","586.0",null,"验证通过","BOOL","照明控制箱B2X0G-定时模式",{"$f":"B504&VLOOKUP(A504,List!$B$3:$D$445,2,FALSE)&D504&\"_\"&VLOOKUP(E504,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0G_TM"},"LLCBB2X0G_TM AT%M586.0 :BOOL; (*照明控制箱B2X0G-定时模式*)","LLCBB2X0G_TM            AT%M586.0      :BOOL; (*照明控制箱B2X0G-定时模式*)"]
["照明控制箱","L","M","B1X0G","定时模式","588.0",null,"验证通过","BOOL","照明控制箱B1X0G-定时模式",{"$f":"B505&VLOOKUP(A505,List!$B$3:$D$445,2,FALSE)&D505&\"_\"&VLOOKUP(E505,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0G_TM"},"LLCBB1X0G_TM AT%M588.0 :BOOL; (*照明控制箱B1X0G-定时模式*)","LLCBB1X0G_TM            AT%M588.0      :BOOL; (*照明控制箱B1X0G-定时模式*)"]
["照明控制箱","L","M","01X0G","定时模式","590.0",null,{"$f":"IF((IF(OR(I506=\"INT\",I506=\"WORD\",I506=\"BOOL\"),MOD(F506,2),MOD(F506,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A506&D506&\"-\"&E506","v":"照明控制箱01X0G-定时模式"},{"$f":"B506&VLOOKUP(A506,List!$B$3:$D$445,2,FALSE)&D506&\"_\"&VLOOKUP(E506,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0G_TM"},"LLCB01X0G_TM AT%M590.0 :BOOL; (*照明控制箱01X0G-定时模式*)","LLCB01X0G_TM            AT%M590.0      :BOOL; (*照明控制箱01X0G-定时模式*)"]
["照明控制箱","L","M","02X0G","定时模式","592.0",null,"验证通过","BOOL","照明控制箱02X0G-定时模式",{"$f":"B507&VLOOKUP(A507,List!$B$3:$D$445,2,FALSE)&D507&\"_\"&VLOOKUP(E507,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0G_TM"},"LLCB02X0G_TM AT%M592.0 :BOOL; (*照明控制箱02X0G-定时模式*)","LLCB02X0G_TM            AT%M592.0      :BOOL; (*照明控制箱02X0G-定时模式*)"]
["照明控制箱","L","M","03X0G","定时模式","594.0",null,"验证通过","BOOL","照明控制箱03X0G-定时模式",{"$f":"B508&VLOOKUP(A508,List!$B$3:$D$445,2,FALSE)&D508&\"_\"&VLOOKUP(E508,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0G_TM"},"LLCB03X0G_TM AT%M594.0 :BOOL; (*照明控制箱03X0G-定时模式*)","LLCB03X0G_TM            AT%M594.0      :BOOL; (*照明控制箱03X0G-定时模式*)"]
["照明控制箱","L","M","04X0G","定时模式","596.0",null,"验证通过","BOOL","照明控制箱04X0G-定时模式",{"$f":"B509&VLOOKUP(A509,List!$B$3:$D$445,2,FALSE)&D509&\"_\"&VLOOKUP(E509,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0G_TM"},"LLCB04X0G_TM AT%M596.0 :BOOL; (*照明控制箱04X0G-定时模式*)","LLCB04X0G_TM            AT%M596.0      :BOOL; (*照明控制箱04X0G-定时模式*)"]
["照明控制箱","L","M","05X0G","定时模式","598.0",null,"验证通过","BOOL","照明控制箱05X0G-定时模式",{"$f":"B510&VLOOKUP(A510,List!$B$3:$D$445,2,FALSE)&D510&\"_\"&VLOOKUP(E510,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0G_TM"},"LLCB05X0G_TM AT%M598.0 :BOOL; (*照明控制箱05X0G-定时模式*)","LLCB05X0G_TM            AT%M598.0      :BOOL; (*照明控制箱05X0G-定时模式*)"]
["照明控制箱","L","M","06X0G","定时模式","600.0",null,"验证通过","BOOL","照明控制箱06X0G-定时模式",{"$f":"B511&VLOOKUP(A511,List!$B$3:$D$445,2,FALSE)&D511&\"_\"&VLOOKUP(E511,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0G_TM"},"LLCB06X0G_TM AT%M600.0 :BOOL; (*照明控制箱06X0G-定时模式*)","LLCB06X0G_TM            AT%M600.0      :BOOL; (*照明控制箱06X0G-定时模式*)"]
["照明控制箱","L","M","07X0G","定时模式","602.0",null,{"$f":"IF((IF(OR(I512=\"INT\",I512=\"WORD\",I512=\"BOOL\"),MOD(F512,2),MOD(F512,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A512&D512&\"-\"&E512","v":"照明控制箱07X0G-定时模式"},{"$f":"B512&VLOOKUP(A512,List!$B$3:$D$445,2,FALSE)&D512&\"_\"&VLOOKUP(E512,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0G_TM"},{"$f":"K512&\" \"&\"AT%\"&C512&F512&\" \"&\":\"&I512&\";\"&\" \"&\"(*\"&J512&\"*)\"","v":"LLCB07X0G_TM AT%M602.0 :BOOL; (*照明控制箱07X0G-定时模式*)"},{"$f":"REPLACE(REPLACE(L512,SEARCH(\"AT%\",L512),,REPT(\" \",25-SEARCH(\"AT%\",L512))),SEARCH(\":\",REPLACE(L512,SEARCH(\"AT%\",L512),,REPT(\" \",25-SEARCH(\"AT%\",L512)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L512,SEARCH(\"AT%\",L512),,REPT(\" \",25-SEARCH(\"AT%\",L512))))))","v":"LLCB07X0G_TM            AT%M602.0      :BOOL; (*照明控制箱07X0G-定时模式*)"}]
["照明控制箱","L","M","08X0G","定时模式","604.0",null,"验证通过","BOOL","照明控制箱08X0G-定时模式",{"$f":"B513&VLOOKUP(A513,List!$B$3:$D$445,2,FALSE)&D513&\"_\"&VLOOKUP(E513,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0G_TM"},"LLCB08X0G_TM AT%M604.0 :BOOL; (*照明控制箱08X0G-定时模式*)","LLCB08X0G_TM            AT%M604.0      :BOOL; (*照明控制箱08X0G-定时模式*)"]
["照明控制箱","L","M","B3X0H","定时模式","606.0",null,"验证通过","BOOL","照明控制箱B3X0H-定时模式",{"$f":"B514&VLOOKUP(A514,List!$B$3:$D$445,2,FALSE)&D514&\"_\"&VLOOKUP(E514,List!$K$2:$M$447,2,FALSE)","v":"LLCBB3X0H_TM"},"LLCBB3X0H_TM AT%M606.0 :BOOL; (*照明控制箱B3X0H-定时模式*)","LLCBB3X0H_TM            AT%M606.0      :BOOL; (*照明控制箱B3X0H-定时模式*)"]
["照明控制箱","L","M","B2X0H","定时模式","608.0",null,"验证通过","BOOL","照明控制箱B2X0H-定时模式",{"$f":"B515&VLOOKUP(A515,List!$B$3:$D$445,2,FALSE)&D515&\"_\"&VLOOKUP(E515,List!$K$2:$M$447,2,FALSE)","v":"LLCBB2X0H_TM"},"LLCBB2X0H_TM AT%M608.0 :BOOL; (*照明控制箱B2X0H-定时模式*)","LLCBB2X0H_TM            AT%M608.0      :BOOL; (*照明控制箱B2X0H-定时模式*)"]
["照明控制箱","L","M","B1X0H","定时模式","610.0",null,"验证通过","BOOL","照明控制箱B1X0H-定时模式",{"$f":"B516&VLOOKUP(A516,List!$B$3:$D$445,2,FALSE)&D516&\"_\"&VLOOKUP(E516,List!$K$2:$M$447,2,FALSE)","v":"LLCBB1X0H_TM"},"LLCBB1X0H_TM AT%M610.0 :BOOL; (*照明控制箱B1X0H-定时模式*)","LLCBB1X0H_TM            AT%M610.0      :BOOL; (*照明控制箱B1X0H-定时模式*)"]
["照明控制箱","L","M","01X0H","定时模式","612.0",null,"验证通过","BOOL","照明控制箱01X0H-定时模式",{"$f":"B517&VLOOKUP(A517,List!$B$3:$D$445,2,FALSE)&D517&\"_\"&VLOOKUP(E517,List!$K$2:$M$447,2,FALSE)","v":"LLCB01X0H_TM"},"LLCB01X0H_TM AT%M612.0 :BOOL; (*照明控制箱01X0H-定时模式*)","LLCB01X0H_TM            AT%M612.0      :BOOL; (*照明控制箱01X0H-定时模式*)"]
["照明控制箱","L","M","02X0H","定时模式","614.0",null,"验证通过","BOOL","照明控制箱02X0H-定时模式",{"$f":"B518&VLOOKUP(A518,List!$B$3:$D$445,2,FALSE)&D518&\"_\"&VLOOKUP(E518,List!$K$2:$M$447,2,FALSE)","v":"LLCB02X0H_TM"},"LLCB02X0H_TM AT%M614.0 :BOOL; (*照明控制箱02X0H-定时模式*)","LLCB02X0H_TM            AT%M614.0      :BOOL; (*照明控制箱02X0H-定时模式*)"]
["照明控制箱","L","M","03X0H","定时模式","616.0",null,"验证通过","BOOL","照明控制箱03X0H-定时模式",{"$f":"B519&VLOOKUP(A519,List!$B$3:$D$445,2,FALSE)&D519&\"_\"&VLOOKUP(E519,List!$K$2:$M$447,2,FALSE)","v":"LLCB03X0H_TM"},"LLCB03X0H_TM AT%M616.0 :BOOL; (*照明控制箱03X0H-定时模式*)","LLCB03X0H_TM            AT%M616.0      :BOOL; (*照明控制箱03X0H-定时模式*)"]
["照明控制箱","L","M","04X0H","定时模式","618.0",null,"验证通过","BOOL","照明控制箱04X0H-定时模式",{"$f":"B520&VLOOKUP(A520,List!$B$3:$D$445,2,FALSE)&D520&\"_\"&VLOOKUP(E520,List!$K$2:$M$447,2,FALSE)","v":"LLCB04X0H_TM"},"LLCB04X0H_TM AT%M618.0 :BOOL; (*照明控制箱04X0H-定时模式*)","LLCB04X0H_TM            AT%M618.0      :BOOL; (*照明控制箱04X0H-定时模式*)"]
["照明控制箱","L","M","05X0H","定时模式","620.0",null,"验证通过","BOOL","照明控制箱05X0H-定时模式",{"$f":"B521&VLOOKUP(A521,List!$B$3:$D$445,2,FALSE)&D521&\"_\"&VLOOKUP(E521,List!$K$2:$M$447,2,FALSE)","v":"LLCB05X0H_TM"},"LLCB05X0H_TM AT%M620.0 :BOOL; (*照明控制箱05X0H-定时模式*)","LLCB05X0H_TM            AT%M620.0      :BOOL; (*照明控制箱05X0H-定时模式*)"]
["照明控制箱","L","M","06X0H","定时模式","622.0",null,"验证通过","BOOL","照明控制箱06X0H-定时模式",{"$f":"B522&VLOOKUP(A522,List!$B$3:$D$445,2,FALSE)&D522&\"_\"&VLOOKUP(E522,List!$K$2:$M$447,2,FALSE)","v":"LLCB06X0H_TM"},"LLCB06X0H_TM AT%M622.0 :BOOL; (*照明控制箱06X0H-定时模式*)","LLCB06X0H_TM            AT%M622.0      :BOOL; (*照明控制箱06X0H-定时模式*)"]
["照明控制箱","L","M","07X0H","定时模式","624.0",null,{"$f":"IF((IF(OR(I523=\"INT\",I523=\"WORD\",I523=\"BOOL\"),MOD(F523,2),MOD(F523,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A523&D523&\"-\"&E523","v":"照明控制箱07X0H-定时模式"},{"$f":"B523&VLOOKUP(A523,List!$B$3:$D$445,2,FALSE)&D523&\"_\"&VLOOKUP(E523,List!$K$2:$M$447,2,FALSE)","v":"LLCB07X0H_TM"},{"$f":"K523&\" \"&\"AT%\"&C523&F523&\" \"&\":\"&I523&\";\"&\" \"&\"(*\"&J523&\"*)\"","v":"LLCB07X0H_TM AT%M624.0 :BOOL; (*照明控制箱07X0H-定时模式*)"},{"$f":"REPLACE(REPLACE(L523,SEARCH(\"AT%\",L523),,REPT(\" \",25-SEARCH(\"AT%\",L523))),SEARCH(\":\",REPLACE(L523,SEARCH(\"AT%\",L523),,REPT(\" \",25-SEARCH(\"AT%\",L523)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L523,SEARCH(\"AT%\",L523),,REPT(\" \",25-SEARCH(\"AT%\",L523))))))","v":"LLCB07X0H_TM            AT%M624.0      :BOOL; (*照明控制箱07X0H-定时模式*)"}]
["照明控制箱","L","M","08X0H","定时模式","626.0",null,"验证通过","BOOL","照明控制箱08X0H-定时模式",{"$f":"B524&VLOOKUP(A524,List!$B$3:$D$445,2,FALSE)&D524&\"_\"&VLOOKUP(E524,List!$K$2:$M$447,2,FALSE)","v":"LLCB08X0H_TM"},"LLCB08X0H_TM AT%M626.0 :BOOL; (*照明控制箱08X0H-定时模式*)","LLCB08X0H_TM            AT%M626.0      :BOOL; (*照明控制箱08X0H-定时模式*)"]
["照明控制箱","R","M","B3X0A","启停控制","628.0",null,{"$f":"IF((IF(OR(I525=\"INT\",I525=\"WORD\",I525=\"BOOL\"),MOD(F525,2),MOD(F525,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A525&D525&\"-新云平台\"&E525","v":"照明控制箱B3X0A-新云平台启停控制"},{"$f":"B525&VLOOKUP(A525,List!$B$3:$D$445,2,FALSE)&D525&\"_\"&VLOOKUP(E525,List!$K$2:$M$447,2,FALSE)","v":"RLCBB3X0A_C"},"RLCBB3X0A_C AT%M628.0 :BOOL; (*照明控制箱B3X0A-新云平台启停控制*)","RLCBB3X0A_C             AT%M628.0      :BOOL; (*照明控制箱B3X0A-新云平台启停控制*)"]
["照明控制箱","R","M","B2X0A","启停控制","630.0",null,"验证通过","BOOL",{"$f":"A526&D526&\"-新云平台\"&E526","v":"照明控制箱B2X0A-新云平台启停控制"},{"$f":"B526&VLOOKUP(A526,List!$B$3:$D$445,2,FALSE)&D526&\"_\"&VLOOKUP(E526,List!$K$2:$M$447,2,FALSE)","v":"RLCBB2X0A_C"},"RLCBB2X0A_C AT%M630.0 :BOOL; (*照明控制箱B2X0A-新云平台启停控制*)","RLCBB2X0A_C             AT%M630.0      :BOOL; (*照明控制箱B2X0A-新云平台启停控制*)"]
["照明控制箱","R","M","B1X0A","启停控制","632.0",null,"验证通过","BOOL","照明控制箱B1X0A-新云平台启停控制",{"$f":"B527&VLOOKUP(A527,List!$B$3:$D$445,2,FALSE)&D527&\"_\"&VLOOKUP(E527,List!$K$2:$M$447,2,FALSE)","v":"RLCBB1X0A_C"},"RLCBB1X0A_C AT%M632.0 :BOOL; (*照明控制箱B1X0A-新云平台启停控制*)","RLCBB1X0A_C             AT%M632.0      :BOOL; (*照明控制箱B1X0A-新云平台启停控制*)"]
["照明控制箱","R","M","01X0A","启停控制","634.0",null,"验证通过","BOOL","照明控制箱01X0A-新云平台启停控制",{"$f":"B528&VLOOKUP(A528,List!$B$3:$D$445,2,FALSE)&D528&\"_\"&VLOOKUP(E528,List!$K$2:$M$447,2,FALSE)","v":"RLCB01X0A_C"},"RLCB01X0A_C AT%M634.0 :BOOL; (*照明控制箱01X0A-新云平台启停控制*)","RLCB01X0A_C             AT%M634.0      :BOOL; (*照明控制箱01X0A-新云平台启停控制*)"]
["照明控制箱","R","M","02X0A","启停控制","636.0",null,"验证通过","BOOL","照明控制箱02X0A-新云平台启停控制",{"$f":"B529&VLOOKUP(A529,List!$B$3:$D$445,2,FALSE)&D529&\"_\"&VLOOKUP(E529,List!$K$2:$M$447,2,FALSE)","v":"RLCB02X0A_C"},"RLCB02X0A_C AT%M636.0 :BOOL; (*照明控制箱02X0A-新云平台启停控制*)","RLCB02X0A_C             AT%M636.0      :BOOL; (*照明控制箱02X0A-新云平台启停控制*)"]
["照明控制箱","R","M","03X0A","启停控制","638.0",null,"验证通过","BOOL","照明控制箱03X0A-新云平台启停控制",{"$f":"B530&VLOOKUP(A530,List!$B$3:$D$445,2,FALSE)&D530&\"_\"&VLOOKUP(E530,List!$K$2:$M$447,2,FALSE)","v":"RLCB03X0A_C"},"RLCB03X0A_C AT%M638.0 :BOOL; (*照明控制箱03X0A-新云平台启停控制*)","RLCB03X0A_C             AT%M638.0      :BOOL; (*照明控制箱03X0A-新云平台启停控制*)"]
["照明控制箱","R","M","04X0A","启停控制","640.0",null,"验证通过","BOOL","照明控制箱04X0A-新云平台启停控制",{"$f":"B531&VLOOKUP(A531,List!$B$3:$D$445,2,FALSE)&D531&\"_\"&VLOOKUP(E531,List!$K$2:$M$447,2,FALSE)","v":"RLCB04X0A_C"},"RLCB04X0A_C AT%M640.0 :BOOL; (*照明控制箱04X0A-新云平台启停控制*)","RLCB04X0A_C             AT%M640.0      :BOOL; (*照明控制箱04X0A-新云平台启停控制*)"]
["照明控制箱","R","M","05X0A","启停控制",{"$f":"IF(OR(I531=\"REAL\",I531=\"DWORD\",I531=\"DINT\"),(IF(OR(I532=\"REAL\",I532=\"DWORD\",I532=\"DINT\"),F531+4+MOD(F531,4),F531+4)),(IF(OR(I532=\"REAL\",I532=\"DWORD\",I532=\"DINT\"),F531+4+MOD(F531,4),F531+2)))&\".0\"","v":"642.0"},null,"验证通过","BOOL","照明控制箱05X0A-新云平台启停控制",{"$f":"B532&VLOOKUP(A532,List!$B$3:$D$445,2,FALSE)&D532&\"_\"&VLOOKUP(E532,List!$K$2:$M$447,2,FALSE)","v":"RLCB05X0A_C"},"RLCB05X0A_C AT%M642.0 :BOOL; (*照明控制箱05X0A-新云平台启停控制*)","RLCB05X0A_C             AT%M642.0      :BOOL; (*照明控制箱05X0A-新云平台启停控制*)"]
["照明控制箱","R","M","06X0A","启停控制","644.0",null,"验证通过","BOOL","照明控制箱06X0A-新云平台启停控制",{"$f":"B533&VLOOKUP(A533,List!$B$3:$D$445,2,FALSE)&D533&\"_\"&VLOOKUP(E533,List!$K$2:$M$447,2,FALSE)","v":"RLCB06X0A_C"},"RLCB06X0A_C AT%M644.0 :BOOL; (*照明控制箱06X0A-新云平台启停控制*)","RLCB06X0A_C             AT%M644.0      :BOOL; (*照明控制箱06X0A-新云平台启停控制*)"]
["照明控制箱","R","M","07X0A","启停控制","646.0",null,{"$f":"IF((IF(OR(I534=\"INT\",I534=\"WORD\",I534=\"BOOL\"),MOD(F534,2),MOD(F534,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A534&D534&\"-新云平台\"&E534","v":"照明控制箱07X0A-新云平台启停控制"},{"$f":"B534&VLOOKUP(A534,List!$B$3:$D$445,2,FALSE)&D534&\"_\"&VLOOKUP(E534,List!$K$2:$M$447,2,FALSE)","v":"RLCB07X0A_C"},{"$f":"K534&\" \"&\"AT%\"&C534&F534&\" \"&\":\"&I534&\";\"&\" \"&\"(*\"&J534&\"*)\"","v":"RLCB07X0A_C AT%M646.0 :BOOL; (*照明控制箱07X0A-新云平台启停控制*)"},{"$f":"REPLACE(REPLACE(L534,SEARCH(\"AT%\",L534),,REPT(\" \",25-SEARCH(\"AT%\",L534))),SEARCH(\":\",REPLACE(L534,SEARCH(\"AT%\",L534),,REPT(\" \",25-SEARCH(\"AT%\",L534)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L534,SEARCH(\"AT%\",L534),,REPT(\" \",25-SEARCH(\"AT%\",L534))))))","v":"RLCB07X0A_C             AT%M646.0      :BOOL; (*照明控制箱07X0A-新云平台启停控制*)"}]
["照明控制箱","R","M","08X0A","启停控制","648.0",null,"验证通过","BOOL","照明控制箱08X0A-新云平台启停控制",{"$f":"B535&VLOOKUP(A535,List!$B$3:$D$445,2,FALSE)&D535&\"_\"&VLOOKUP(E535,List!$K$2:$M$447,2,FALSE)","v":"RLCB08X0A_C"},"RLCB08X0A_C AT%M648.0 :BOOL; (*照明控制箱08X0A-新云平台启停控制*)","RLCB08X0A_C             AT%M648.0      :BOOL; (*照明控制箱08X0A-新云平台启停控制*)"]
["照明控制箱","R","M","B3X0B","启停控制","650.0",null,"验证通过","BOOL","照明控制箱B3X0B-新云平台启停控制",{"$f":"B536&VLOOKUP(A536,List!$B$3:$D$445,2,FALSE)&D536&\"_\"&VLOOKUP(E536,List!$K$2:$M$447,2,FALSE)","v":"RLCBB3X0B_C"},"RLCBB3X0B_C AT%M650.0 :BOOL; (*照明控制箱B3X0B-新云平台启停控制*)","RLCBB3X0B_C             AT%M650.0      :BOOL; (*照明控制箱B3X0B-新云平台启停控制*)"]
["照明控制箱","R","M","B2X0B","启停控制","652.0",null,"验证通过","BOOL","照明控制箱B2X0B-新云平台启停控制",{"$f":"B537&VLOOKUP(A537,List!$B$3:$D$445,2,FALSE)&D537&\"_\"&VLOOKUP(E537,List!$K$2:$M$447,2,FALSE)","v":"RLCBB2X0B_C"},"RLCBB2X0B_C AT%M652.0 :BOOL; (*照明控制箱B2X0B-新云平台启停控制*)","RLCBB2X0B_C             AT%M652.0      :BOOL; (*照明控制箱B2X0B-新云平台启停控制*)"]
["照明控制箱","R","M","B1X0B","启停控制","654.0",null,"验证通过","BOOL","照明控制箱B1X0B-新云平台启停控制",{"$f":"B538&VLOOKUP(A538,List!$B$3:$D$445,2,FALSE)&D538&\"_\"&VLOOKUP(E538,List!$K$2:$M$447,2,FALSE)","v":"RLCBB1X0B_C"},"RLCBB1X0B_C AT%M654.0 :BOOL; (*照明控制箱B1X0B-新云平台启停控制*)","RLCBB1X0B_C             AT%M654.0      :BOOL; (*照明控制箱B1X0B-新云平台启停控制*)"]
["照明控制箱","R","M","01X0B","启停控制","656.0",null,"验证通过","BOOL","照明控制箱01X0B-新云平台启停控制",{"$f":"B539&VLOOKUP(A539,List!$B$3:$D$445,2,FALSE)&D539&\"_\"&VLOOKUP(E539,List!$K$2:$M$447,2,FALSE)","v":"RLCB01X0B_C"},"RLCB01X0B_C AT%M656.0 :BOOL; (*照明控制箱01X0B-新云平台启停控制*)","RLCB01X0B_C             AT%M656.0      :BOOL; (*照明控制箱01X0B-新云平台启停控制*)"]
["照明控制箱","R","M","02X0B","启停控制","658.0",null,"验证通过","BOOL","照明控制箱02X0B-新云平台启停控制",{"$f":"B540&VLOOKUP(A540,List!$B$3:$D$445,2,FALSE)&D540&\"_\"&VLOOKUP(E540,List!$K$2:$M$447,2,FALSE)","v":"RLCB02X0B_C"},"RLCB02X0B_C AT%M658.0 :BOOL; (*照明控制箱02X0B-新云平台启停控制*)","RLCB02X0B_C             AT%M658.0      :BOOL; (*照明控制箱02X0B-新云平台启停控制*)"]
["照明控制箱","R","M","03X0B","启停控制","660.0",null,"验证通过","BOOL","照明控制箱03X0B-新云平台启停控制",{"$f":"B541&VLOOKUP(A541,List!$B$3:$D$445,2,FALSE)&D541&\"_\"&VLOOKUP(E541,List!$K$2:$M$447,2,FALSE)","v":"RLCB03X0B_C"},"RLCB03X0B_C AT%M660.0 :BOOL; (*照明控制箱03X0B-新云平台启停控制*)","RLCB03X0B_C             AT%M660.0      :BOOL; (*照明控制箱03X0B-新云平台启停控制*)"]
["照明控制箱","R","M","04X0B","启停控制","662.0",null,"验证通过","BOOL","照明控制箱04X0B-新云平台启停控制",{"$f":"B542&VLOOKUP(A542,List!$B$3:$D$445,2,FALSE)&D542&\"_\"&VLOOKUP(E542,List!$K$2:$M$447,2,FALSE)","v":"RLCB04X0B_C"},"RLCB04X0B_C AT%M662.0 :BOOL; (*照明控制箱04X0B-新云平台启停控制*)","RLCB04X0B_C             AT%M662.0      :BOOL; (*照明控制箱04X0B-新云平台启停控制*)"]
["照明控制箱","R","M","05X0B","启停控制","664.0",null,"验证通过","BOOL","照明控制箱05X0B-新云平台启停控制",{"$f":"B543&VLOOKUP(A543,List!$B$3:$D$445,2,FALSE)&D543&\"_\"&VLOOKUP(E543,List!$K$2:$M$447,2,FALSE)","v":"RLCB05X0B_C"},"RLCB05X0B_C AT%M664.0 :BOOL; (*照明控制箱05X0B-新云平台启停控制*)","RLCB05X0B_C             AT%M664.0      :BOOL; (*照明控制箱05X0B-新云平台启停控制*)"]
["照明控制箱","R","M","06X0B","启停控制","666.0",null,"验证通过","BOOL","照明控制箱06X0B-新云平台启停控制",{"$f":"B544&VLOOKUP(A544,List!$B$3:$D$445,2,FALSE)&D544&\"_\"&VLOOKUP(E544,List!$K$2:$M$447,2,FALSE)","v":"RLCB06X0B_C"},"RLCB06X0B_C AT%M666.0 :BOOL; (*照明控制箱06X0B-新云平台启停控制*)","RLCB06X0B_C             AT%M666.0      :BOOL; (*照明控制箱06X0B-新云平台启停控制*)"]
["照明控制箱","R","M","07X0B","启停控制","668.0",null,{"$f":"IF((IF(OR(I545=\"INT\",I545=\"WORD\",I545=\"BOOL\"),MOD(F545,2),MOD(F545,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A545&D545&\"-新云平台\"&E545","v":"照明控制箱07X0B-新云平台启停控制"},{"$f":"B545&VLOOKUP(A545,List!$B$3:$D$445,2,FALSE)&D545&\"_\"&VLOOKUP(E545,List!$K$2:$M$447,2,FALSE)","v":"RLCB07X0B_C"},{"$f":"K545&\" \"&\"AT%\"&C545&F545&\" \"&\":\"&I545&\";\"&\" \"&\"(*\"&J545&\"*)\"","v":"RLCB07X0B_C AT%M668.0 :BOOL; (*照明控制箱07X0B-新云平台启停控制*)"},{"$f":"REPLACE(REPLACE(L545,SEARCH(\"AT%\",L545),,REPT(\" \",25-SEARCH(\"AT%\",L545))),SEARCH(\":\",REPLACE(L545,SEARCH(\"AT%\",L545),,REPT(\" \",25-SEARCH(\"AT%\",L545)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L545,SEARCH(\"AT%\",L545),,REPT(\" \",25-SEARCH(\"AT%\",L545))))))","v":"RLCB07X0B_C             AT%M668.0      :BOOL; (*照明控制箱07X0B-新云平台启停控制*)"}]
["照明控制箱","R","M","08X0B","启停控制","670.0",null,"验证通过","BOOL","照明控制箱08X0B-新云平台启停控制",{"$f":"B546&VLOOKUP(A546,List!$B$3:$D$445,2,FALSE)&D546&\"_\"&VLOOKUP(E546,List!$K$2:$M$447,2,FALSE)","v":"RLCB08X0B_C"},"RLCB08X0B_C AT%M670.0 :BOOL; (*照明控制箱08X0B-新云平台启停控制*)","RLCB08X0B_C             AT%M670.0      :BOOL; (*照明控制箱08X0B-新云平台启停控制*)"]
["照明控制箱","R","M","B3X0C","启停控制","672.0",null,"验证通过","BOOL","照明控制箱B3X0C-新云平台启停控制",{"$f":"B547&VLOOKUP(A547,List!$B$3:$D$445,2,FALSE)&D547&\"_\"&VLOOKUP(E547,List!$K$2:$M$447,2,FALSE)","v":"RLCBB3X0C_C"},"RLCBB3X0C_C AT%M672.0 :BOOL; (*照明控制箱B3X0C-新云平台启停控制*)","RLCBB3X0C_C             AT%M672.0      :BOOL; (*照明控制箱B3X0C-新云平台启停控制*)"]
["照明控制箱","R","M","B2X0C","启停控制","674.0",null,"验证通过","BOOL","照明控制箱B2X0C-新云平台启停控制",{"$f":"B548&VLOOKUP(A548,List!$B$3:$D$445,2,FALSE)&D548&\"_\"&VLOOKUP(E548,List!$K$2:$M$447,2,FALSE)","v":"RLCBB2X0C_C"},"RLCBB2X0C_C AT%M674.0 :BOOL; (*照明控制箱B2X0C-新云平台启停控制*)","RLCBB2X0C_C             AT%M674.0      :BOOL; (*照明控制箱B2X0C-新云平台启停控制*)"]
["照明控制箱","R","M","B1X0C","启停控制","676.0",null,"验证通过","BOOL","照明控制箱B1X0C-新云平台启停控制",{"$f":"B549&VLOOKUP(A549,List!$B$3:$D$445,2,FALSE)&D549&\"_\"&VLOOKUP(E549,List!$K$2:$M$447,2,FALSE)","v":"RLCBB1X0C_C"},"RLCBB1X0C_C AT%M676.0 :BOOL; (*照明控制箱B1X0C-新云平台启停控制*)","RLCBB1X0C_C             AT%M676.0      :BOOL; (*照明控制箱B1X0C-新云平台启停控制*)"]
["照明控制箱","R","M","01X0C","启停控制","678.0",null,"验证通过","BOOL","照明控制箱01X0C-新云平台启停控制",{"$f":"B550&VLOOKUP(A550,List!$B$3:$D$445,2,FALSE)&D550&\"_\"&VLOOKUP(E550,List!$K$2:$M$447,2,FALSE)","v":"RLCB01X0C_C"},"RLCB01X0C_C AT%M678.0 :BOOL; (*照明控制箱01X0C-新云平台启停控制*)","RLCB01X0C_C             AT%M678.0      :BOOL; (*照明控制箱01X0C-新云平台启停控制*)"]
["照明控制箱","R","M","02X0C","启停控制","680.0",null,"验证通过","BOOL","照明控制箱02X0C-新云平台启停控制",{"$f":"B551&VLOOKUP(A551,List!$B$3:$D$445,2,FALSE)&D551&\"_\"&VLOOKUP(E551,List!$K$2:$M$447,2,FALSE)","v":"RLCB02X0C_C"},"RLCB02X0C_C AT%M680.0 :BOOL; (*照明控制箱02X0C-新云平台启停控制*)","RLCB02X0C_C             AT%M680.0      :BOOL; (*照明控制箱02X0C-新云平台启停控制*)"]
["照明控制箱","R","M","03X0C","启停控制","682.0",null,"验证通过","BOOL","照明控制箱03X0C-新云平台启停控制",{"$f":"B552&VLOOKUP(A552,List!$B$3:$D$445,2,FALSE)&D552&\"_\"&VLOOKUP(E552,List!$K$2:$M$447,2,FALSE)","v":"RLCB03X0C_C"},"RLCB03X0C_C AT%M682.0 :BOOL; (*照明控制箱03X0C-新云平台启停控制*)","RLCB03X0C_C             AT%M682.0      :BOOL; (*照明控制箱03X0C-新云平台启停控制*)"]
["照明控制箱","R","M","04X0C","启停控制","684.0",null,"验证通过","BOOL","照明控制箱04X0C-新云平台启停控制",{"$f":"B553&VLOOKUP(A553,List!$B$3:$D$445,2,FALSE)&D553&\"_\"&VLOOKUP(E553,List!$K$2:$M$447,2,FALSE)","v":"RLCB04X0C_C"},"RLCB04X0C_C AT%M684.0 :BOOL; (*照明控制箱04X0C-新云平台启停控制*)","RLCB04X0C_C             AT%M684.0      :BOOL; (*照明控制箱04X0C-新云平台启停控制*)"]
["照明控制箱","R","M","05X0C","启停控制","686.0",null,"验证通过","BOOL","照明控制箱05X0C-新云平台启停控制",{"$f":"B554&VLOOKUP(A554,List!$B$3:$D$445,2,FALSE)&D554&\"_\"&VLOOKUP(E554,List!$K$2:$M$447,2,FALSE)","v":"RLCB05X0C_C"},"RLCB05X0C_C AT%M686.0 :BOOL; (*照明控制箱05X0C-新云平台启停控制*)","RLCB05X0C_C             AT%M686.0      :BOOL; (*照明控制箱05X0C-新云平台启停控制*)"]
["照明控制箱","R","M","06X0C","启停控制","688.0",null,"验证通过","BOOL","照明控制箱06X0C-新云平台启停控制",{"$f":"B555&VLOOKUP(A555,List!$B$3:$D$445,2,FALSE)&D555&\"_\"&VLOOKUP(E555,List!$K$2:$M$447,2,FALSE)","v":"RLCB06X0C_C"},"RLCB06X0C_C AT%M688.0 :BOOL; (*照明控制箱06X0C-新云平台启停控制*)","RLCB06X0C_C             AT%M688.0      :BOOL; (*照明控制箱06X0C-新云平台启停控制*)"]
["照明控制箱","R","M","07X0C","启停控制","690.0",null,{"$f":"IF((IF(OR(I556=\"INT\",I556=\"WORD\",I556=\"BOOL\"),MOD(F556,2),MOD(F556,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A556&D556&\"-新云平台\"&E556","v":"照明控制箱07X0C-新云平台启停控制"},{"$f":"B556&VLOOKUP(A556,List!$B$3:$D$445,2,FALSE)&D556&\"_\"&VLOOKUP(E556,List!$K$2:$M$447,2,FALSE)","v":"RLCB07X0C_C"},{"$f":"K556&\" \"&\"AT%\"&C556&F556&\" \"&\":\"&I556&\";\"&\" \"&\"(*\"&J556&\"*)\"","v":"RLCB07X0C_C AT%M690.0 :BOOL; (*照明控制箱07X0C-新云平台启停控制*)"},{"$f":"REPLACE(REPLACE(L556,SEARCH(\"AT%\",L556),,REPT(\" \",25-SEARCH(\"AT%\",L556))),SEARCH(\":\",REPLACE(L556,SEARCH(\"AT%\",L556),,REPT(\" \",25-SEARCH(\"AT%\",L556)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L556,SEARCH(\"AT%\",L556),,REPT(\" \",25-SEARCH(\"AT%\",L556))))))","v":"RLCB07X0C_C             AT%M690.0      :BOOL; (*照明控制箱07X0C-新云平台启停控制*)"}]
["照明控制箱","R","M","08X0C","启停控制","692.0",null,"验证通过","BOOL","照明控制箱08X0C-新云平台启停控制",{"$f":"B557&VLOOKUP(A557,List!$B$3:$D$445,2,FALSE)&D557&\"_\"&VLOOKUP(E557,List!$K$2:$M$447,2,FALSE)","v":"RLCB08X0C_C"},"RLCB08X0C_C AT%M692.0 :BOOL; (*照明控制箱08X0C-新云平台启停控制*)","RLCB08X0C_C             AT%M692.0      :BOOL; (*照明控制箱08X0C-新云平台启停控制*)"]
["照明控制箱","R","M","B3X0D","启停控制","694.0",null,"验证通过","BOOL","照明控制箱B3X0D-新云平台启停控制",{"$f":"B558&VLOOKUP(A558,List!$B$3:$D$445,2,FALSE)&D558&\"_\"&VLOOKUP(E558,List!$K$2:$M$447,2,FALSE)","v":"RLCBB3X0D_C"},"RLCBB3X0D_C AT%M694.0 :BOOL; (*照明控制箱B3X0D-新云平台启停控制*)","RLCBB3X0D_C             AT%M694.0      :BOOL; (*照明控制箱B3X0D-新云平台启停控制*)"]
["照明控制箱","R","M","B2X0D","启停控制","696.0",null,"验证通过","BOOL","照明控制箱B2X0D-新云平台启停控制",{"$f":"B559&VLOOKUP(A559,List!$B$3:$D$445,2,FALSE)&D559&\"_\"&VLOOKUP(E559,List!$K$2:$M$447,2,FALSE)","v":"RLCBB2X0D_C"},"RLCBB2X0D_C AT%M696.0 :BOOL; (*照明控制箱B2X0D-新云平台启停控制*)","RLCBB2X0D_C             AT%M696.0      :BOOL; (*照明控制箱B2X0D-新云平台启停控制*)"]
["照明控制箱","R","M","B1X0D","启停控制","698.0",null,"验证通过","BOOL","照明控制箱B1X0D-新云平台启停控制",{"$f":"B560&VLOOKUP(A560,List!$B$3:$D$445,2,FALSE)&D560&\"_\"&VLOOKUP(E560,List!$K$2:$M$447,2,FALSE)","v":"RLCBB1X0D_C"},"RLCBB1X0D_C AT%M698.0 :BOOL; (*照明控制箱B1X0D-新云平台启停控制*)","RLCBB1X0D_C             AT%M698.0      :BOOL; (*照明控制箱B1X0D-新云平台启停控制*)"]
["照明控制箱","R","M","01X0D","启停控制","700.0",null,"验证通过","BOOL","照明控制箱01X0D-新云平台启停控制",{"$f":"B561&VLOOKUP(A561,List!$B$3:$D$445,2,FALSE)&D561&\"_\"&VLOOKUP(E561,List!$K$2:$M$447,2,FALSE)","v":"RLCB01X0D_C"},"RLCB01X0D_C AT%M700.0 :BOOL; (*照明控制箱01X0D-新云平台启停控制*)","RLCB01X0D_C             AT%M700.0      :BOOL; (*照明控制箱01X0D-新云平台启停控制*)"]
["照明控制箱","R","M","02X0D","启停控制","702.0",null,"验证通过","BOOL","照明控制箱02X0D-新云平台启停控制",{"$f":"B562&VLOOKUP(A562,List!$B$3:$D$445,2,FALSE)&D562&\"_\"&VLOOKUP(E562,List!$K$2:$M$447,2,FALSE)","v":"RLCB02X0D_C"},"RLCB02X0D_C AT%M702.0 :BOOL; (*照明控制箱02X0D-新云平台启停控制*)","RLCB02X0D_C             AT%M702.0      :BOOL; (*照明控制箱02X0D-新云平台启停控制*)"]
["照明控制箱","R","M","03X0D","启停控制","704.0",null,"验证通过","BOOL","照明控制箱03X0D-新云平台启停控制",{"$f":"B563&VLOOKUP(A563,List!$B$3:$D$445,2,FALSE)&D563&\"_\"&VLOOKUP(E563,List!$K$2:$M$447,2,FALSE)","v":"RLCB03X0D_C"},"RLCB03X0D_C AT%M704.0 :BOOL; (*照明控制箱03X0D-新云平台启停控制*)","RLCB03X0D_C             AT%M704.0      :BOOL; (*照明控制箱03X0D-新云平台启停控制*)"]
["照明控制箱","R","M","04X0D","启停控制","706.0",null,"验证通过","BOOL","照明控制箱04X0D-新云平台启停控制",{"$f":"B564&VLOOKUP(A564,List!$B$3:$D$445,2,FALSE)&D564&\"_\"&VLOOKUP(E564,List!$K$2:$M$447,2,FALSE)","v":"RLCB04X0D_C"},"RLCB04X0D_C AT%M706.0 :BOOL; (*照明控制箱04X0D-新云平台启停控制*)","RLCB04X0D_C             AT%M706.0      :BOOL; (*照明控制箱04X0D-新云平台启停控制*)"]
["照明控制箱","R","M","05X0D","启停控制","708.0",null,"验证通过","BOOL","照明控制箱05X0D-新云平台启停控制",{"$f":"B565&VLOOKUP(A565,List!$B$3:$D$445,2,FALSE)&D565&\"_\"&VLOOKUP(E565,List!$K$2:$M$447,2,FALSE)","v":"RLCB05X0D_C"},"RLCB05X0D_C AT%M708.0 :BOOL; (*照明控制箱05X0D-新云平台启停控制*)","RLCB05X0D_C             AT%M708.0      :BOOL; (*照明控制箱05X0D-新云平台启停控制*)"]
["照明控制箱","R","M","06X0D","启停控制","710.0",null,"验证通过","BOOL","照明控制箱06X0D-新云平台启停控制",{"$f":"B566&VLOOKUP(A566,List!$B$3:$D$445,2,FALSE)&D566&\"_\"&VLOOKUP(E566,List!$K$2:$M$447,2,FALSE)","v":"RLCB06X0D_C"},"RLCB06X0D_C AT%M710.0 :BOOL; (*照明控制箱06X0D-新云平台启停控制*)","RLCB06X0D_C             AT%M710.0      :BOOL; (*照明控制箱06X0D-新云平台启停控制*)"]
["照明控制箱","R","M","07X0D","启停控制","712.0",null,{"$f":"IF((IF(OR(I567=\"INT\",I567=\"WORD\",I567=\"BOOL\"),MOD(F567,2),MOD(F567,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A567&D567&\"-新云平台\"&E567","v":"照明控制箱07X0D-新云平台启停控制"},{"$f":"B567&VLOOKUP(A567,List!$B$3:$D$445,2,FALSE)&D567&\"_\"&VLOOKUP(E567,List!$K$2:$M$447,2,FALSE)","v":"RLCB07X0D_C"},{"$f":"K567&\" \"&\"AT%\"&C567&F567&\" \"&\":\"&I567&\";\"&\" \"&\"(*\"&J567&\"*)\"","v":"RLCB07X0D_C AT%M712.0 :BOOL; (*照明控制箱07X0D-新云平台启停控制*)"},{"$f":"REPLACE(REPLACE(L567,SEARCH(\"AT%\",L567),,REPT(\" \",25-SEARCH(\"AT%\",L567))),SEARCH(\":\",REPLACE(L567,SEARCH(\"AT%\",L567),,REPT(\" \",25-SEARCH(\"AT%\",L567)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L567,SEARCH(\"AT%\",L567),,REPT(\" \",25-SEARCH(\"AT%\",L567))))))","v":"RLCB07X0D_C             AT%M712.0      :BOOL; (*照明控制箱07X0D-新云平台启停控制*)"}]
["照明控制箱","R","M","08X0D","启停控制","714.0",null,"验证通过","BOOL","照明控制箱08X0D-新云平台启停控制",{"$f":"B568&VLOOKUP(A568,List!$B$3:$D$445,2,FALSE)&D568&\"_\"&VLOOKUP(E568,List!$K$2:$M$447,2,FALSE)","v":"RLCB08X0D_C"},"RLCB08X0D_C AT%M714.0 :BOOL; (*照明控制箱08X0D-新云平台启停控制*)","RLCB08X0D_C             AT%M714.0      :BOOL; (*照明控制箱08X0D-新云平台启停控制*)"]
["照明控制箱","R","M","B3X0E","启停控制","716.0",null,"验证通过","BOOL","照明控制箱B3X0E-新云平台启停控制",{"$f":"B569&VLOOKUP(A569,List!$B$3:$D$445,2,FALSE)&D569&\"_\"&VLOOKUP(E569,List!$K$2:$M$447,2,FALSE)","v":"RLCBB3X0E_C"},"RLCBB3X0E_C AT%M716.0 :BOOL; (*照明控制箱B3X0E-新云平台启停控制*)","RLCBB3X0E_C             AT%M716.0      :BOOL; (*照明控制箱B3X0E-新云平台启停控制*)"]
["照明控制箱","R","M","B2X0E","启停控制","718.0",null,"验证通过","BOOL","照明控制箱B2X0E-新云平台启停控制",{"$f":"B570&VLOOKUP(A570,List!$B$3:$D$445,2,FALSE)&D570&\"_\"&VLOOKUP(E570,List!$K$2:$M$447,2,FALSE)","v":"RLCBB2X0E_C"},"RLCBB2X0E_C AT%M718.0 :BOOL; (*照明控制箱B2X0E-新云平台启停控制*)","RLCBB2X0E_C             AT%M718.0      :BOOL; (*照明控制箱B2X0E-新云平台启停控制*)"]
["照明控制箱","R","M","B1X0E","启停控制","720.0",null,"验证通过","BOOL","照明控制箱B1X0E-新云平台启停控制",{"$f":"B571&VLOOKUP(A571,List!$B$3:$D$445,2,FALSE)&D571&\"_\"&VLOOKUP(E571,List!$K$2:$M$447,2,FALSE)","v":"RLCBB1X0E_C"},"RLCBB1X0E_C AT%M720.0 :BOOL; (*照明控制箱B1X0E-新云平台启停控制*)","RLCBB1X0E_C             AT%M720.0      :BOOL; (*照明控制箱B1X0E-新云平台启停控制*)"]
["照明控制箱","R","M","01X0E","启停控制","722.0",null,"验证通过","BOOL","照明控制箱01X0E-新云平台启停控制",{"$f":"B572&VLOOKUP(A572,List!$B$3:$D$445,2,FALSE)&D572&\"_\"&VLOOKUP(E572,List!$K$2:$M$447,2,FALSE)","v":"RLCB01X0E_C"},"RLCB01X0E_C AT%M722.0 :BOOL; (*照明控制箱01X0E-新云平台启停控制*)","RLCB01X0E_C             AT%M722.0      :BOOL; (*照明控制箱01X0E-新云平台启停控制*)"]
["照明控制箱","R","M","02X0E","启停控制","724.0",null,"验证通过","BOOL","照明控制箱02X0E-新云平台启停控制",{"$f":"B573&VLOOKUP(A573,List!$B$3:$D$445,2,FALSE)&D573&\"_\"&VLOOKUP(E573,List!$K$2:$M$447,2,FALSE)","v":"RLCB02X0E_C"},"RLCB02X0E_C AT%M724.0 :BOOL; (*照明控制箱02X0E-新云平台启停控制*)","RLCB02X0E_C             AT%M724.0      :BOOL; (*照明控制箱02X0E-新云平台启停控制*)"]
["照明控制箱","R","M","03X0E","启停控制","726.0",null,"验证通过","BOOL","照明控制箱03X0E-新云平台启停控制",{"$f":"B574&VLOOKUP(A574,List!$B$3:$D$445,2,FALSE)&D574&\"_\"&VLOOKUP(E574,List!$K$2:$M$447,2,FALSE)","v":"RLCB03X0E_C"},"RLCB03X0E_C AT%M726.0 :BOOL; (*照明控制箱03X0E-新云平台启停控制*)","RLCB03X0E_C             AT%M726.0      :BOOL; (*照明控制箱03X0E-新云平台启停控制*)"]
["照明控制箱","R","M","04X0E","启停控制","728.0",null,"验证通过","BOOL","照明控制箱04X0E-新云平台启停控制",{"$f":"B575&VLOOKUP(A575,List!$B$3:$D$445,2,FALSE)&D575&\"_\"&VLOOKUP(E575,List!$K$2:$M$447,2,FALSE)","v":"RLCB04X0E_C"},"RLCB04X0E_C AT%M728.0 :BOOL; (*照明控制箱04X0E-新云平台启停控制*)","RLCB04X0E_C             AT%M728.0      :BOOL; (*照明控制箱04X0E-新云平台启停控制*)"]
["照明控制箱","R","M","05X0E","启停控制","730.0",null,"验证通过","BOOL","照明控制箱05X0E-新云平台启停控制",{"$f":"B576&VLOOKUP(A576,List!$B$3:$D$445,2,FALSE)&D576&\"_\"&VLOOKUP(E576,List!$K$2:$M$447,2,FALSE)","v":"RLCB05X0E_C"},"RLCB05X0E_C AT%M730.0 :BOOL; (*照明控制箱05X0E-新云平台启停控制*)","RLCB05X0E_C             AT%M730.0      :BOOL; (*照明控制箱05X0E-新云平台启停控制*)"]
["照明控制箱","R","M","06X0E","启停控制","732.0",null,"验证通过","BOOL","照明控制箱06X0E-新云平台启停控制",{"$f":"B577&VLOOKUP(A577,List!$B$3:$D$445,2,FALSE)&D577&\"_\"&VLOOKUP(E577,List!$K$2:$M$447,2,FALSE)","v":"RLCB06X0E_C"},"RLCB06X0E_C AT%M732.0 :BOOL; (*照明控制箱06X0E-新云平台启停控制*)","RLCB06X0E_C             AT%M732.0      :BOOL; (*照明控制箱06X0E-新云平台启停控制*)"]
["照明控制箱","R","M","07X0E","启停控制","734.0",null,{"$f":"IF((IF(OR(I578=\"INT\",I578=\"WORD\",I578=\"BOOL\"),MOD(F578,2),MOD(F578,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A578&D578&\"-新云平台\"&E578","v":"照明控制箱07X0E-新云平台启停控制"},{"$f":"B578&VLOOKUP(A578,List!$B$3:$D$445,2,FALSE)&D578&\"_\"&VLOOKUP(E578,List!$K$2:$M$447,2,FALSE)","v":"RLCB07X0E_C"},{"$f":"K578&\" \"&\"AT%\"&C578&F578&\" \"&\":\"&I578&\";\"&\" \"&\"(*\"&J578&\"*)\"","v":"RLCB07X0E_C AT%M734.0 :BOOL; (*照明控制箱07X0E-新云平台启停控制*)"},{"$f":"REPLACE(REPLACE(L578,SEARCH(\"AT%\",L578),,REPT(\" \",25-SEARCH(\"AT%\",L578))),SEARCH(\":\",REPLACE(L578,SEARCH(\"AT%\",L578),,REPT(\" \",25-SEARCH(\"AT%\",L578)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L578,SEARCH(\"AT%\",L578),,REPT(\" \",25-SEARCH(\"AT%\",L578))))))","v":"RLCB07X0E_C             AT%M734.0      :BOOL; (*照明控制箱07X0E-新云平台启停控制*)"}]
["照明控制箱","R","M","08X0E","启停控制","736.0",null,"验证通过","BOOL","照明控制箱08X0E-新云平台启停控制",{"$f":"B579&VLOOKUP(A579,List!$B$3:$D$445,2,FALSE)&D579&\"_\"&VLOOKUP(E579,List!$K$2:$M$447,2,FALSE)","v":"RLCB08X0E_C"},"RLCB08X0E_C AT%M736.0 :BOOL; (*照明控制箱08X0E-新云平台启停控制*)","RLCB08X0E_C             AT%M736.0      :BOOL; (*照明控制箱08X0E-新云平台启停控制*)"]
["照明控制箱","R","M","B3X0F","启停控制","738.0",null,"验证通过","BOOL","照明控制箱B3X0F-新云平台启停控制",{"$f":"B580&VLOOKUP(A580,List!$B$3:$D$445,2,FALSE)&D580&\"_\"&VLOOKUP(E580,List!$K$2:$M$447,2,FALSE)","v":"RLCBB3X0F_C"},"RLCBB3X0F_C AT%M738.0 :BOOL; (*照明控制箱B3X0F-新云平台启停控制*)","RLCBB3X0F_C             AT%M738.0      :BOOL; (*照明控制箱B3X0F-新云平台启停控制*)"]
["照明控制箱","R","M","B2X0F","启停控制","740.0",null,"验证通过","BOOL","照明控制箱B2X0F-新云平台启停控制",{"$f":"B581&VLOOKUP(A581,List!$B$3:$D$445,2,FALSE)&D581&\"_\"&VLOOKUP(E581,List!$K$2:$M$447,2,FALSE)","v":"RLCBB2X0F_C"},"RLCBB2X0F_C AT%M740.0 :BOOL; (*照明控制箱B2X0F-新云平台启停控制*)","RLCBB2X0F_C             AT%M740.0      :BOOL; (*照明控制箱B2X0F-新云平台启停控制*)"]
["照明控制箱","R","M","B1X0F","启停控制","742.0",null,"验证通过","BOOL","照明控制箱B1X0F-新云平台启停控制",{"$f":"B582&VLOOKUP(A582,List!$B$3:$D$445,2,FALSE)&D582&\"_\"&VLOOKUP(E582,List!$K$2:$M$447,2,FALSE)","v":"RLCBB1X0F_C"},"RLCBB1X0F_C AT%M742.0 :BOOL; (*照明控制箱B1X0F-新云平台启停控制*)","RLCBB1X0F_C             AT%M742.0      :BOOL; (*照明控制箱B1X0F-新云平台启停控制*)"]
["照明控制箱","R","M","01X0F","启停控制","744.0",null,"验证通过","BOOL","照明控制箱01X0F-新云平台启停控制",{"$f":"B583&VLOOKUP(A583,List!$B$3:$D$445,2,FALSE)&D583&\"_\"&VLOOKUP(E583,List!$K$2:$M$447,2,FALSE)","v":"RLCB01X0F_C"},"RLCB01X0F_C AT%M744.0 :BOOL; (*照明控制箱01X0F-新云平台启停控制*)","RLCB01X0F_C             AT%M744.0      :BOOL; (*照明控制箱01X0F-新云平台启停控制*)"]
["照明控制箱","R","M","02X0F","启停控制","746.0",null,"验证通过","BOOL","照明控制箱02X0F-新云平台启停控制",{"$f":"B584&VLOOKUP(A584,List!$B$3:$D$445,2,FALSE)&D584&\"_\"&VLOOKUP(E584,List!$K$2:$M$447,2,FALSE)","v":"RLCB02X0F_C"},"RLCB02X0F_C AT%M746.0 :BOOL; (*照明控制箱02X0F-新云平台启停控制*)","RLCB02X0F_C             AT%M746.0      :BOOL; (*照明控制箱02X0F-新云平台启停控制*)"]
["照明控制箱","R","M","03X0F","启停控制","748.0",null,"验证通过","BOOL","照明控制箱03X0F-新云平台启停控制",{"$f":"B585&VLOOKUP(A585,List!$B$3:$D$445,2,FALSE)&D585&\"_\"&VLOOKUP(E585,List!$K$2:$M$447,2,FALSE)","v":"RLCB03X0F_C"},"RLCB03X0F_C AT%M748.0 :BOOL; (*照明控制箱03X0F-新云平台启停控制*)","RLCB03X0F_C             AT%M748.0      :BOOL; (*照明控制箱03X0F-新云平台启停控制*)"]
["照明控制箱","R","M","04X0F","启停控制","750.0",null,"验证通过","BOOL","照明控制箱04X0F-新云平台启停控制",{"$f":"B586&VLOOKUP(A586,List!$B$3:$D$445,2,FALSE)&D586&\"_\"&VLOOKUP(E586,List!$K$2:$M$447,2,FALSE)","v":"RLCB04X0F_C"},"RLCB04X0F_C AT%M750.0 :BOOL; (*照明控制箱04X0F-新云平台启停控制*)","RLCB04X0F_C             AT%M750.0      :BOOL; (*照明控制箱04X0F-新云平台启停控制*)"]
["照明控制箱","R","M","05X0F","启停控制","752.0",null,"验证通过","BOOL","照明控制箱05X0F-新云平台启停控制",{"$f":"B587&VLOOKUP(A587,List!$B$3:$D$445,2,FALSE)&D587&\"_\"&VLOOKUP(E587,List!$K$2:$M$447,2,FALSE)","v":"RLCB05X0F_C"},"RLCB05X0F_C AT%M752.0 :BOOL; (*照明控制箱05X0F-新云平台启停控制*)","RLCB05X0F_C             AT%M752.0      :BOOL; (*照明控制箱05X0F-新云平台启停控制*)"]
["照明控制箱","R","M","06X0F","启停控制","754.0",null,"验证通过","BOOL","照明控制箱06X0F-新云平台启停控制",{"$f":"B588&VLOOKUP(A588,List!$B$3:$D$445,2,FALSE)&D588&\"_\"&VLOOKUP(E588,List!$K$2:$M$447,2,FALSE)","v":"RLCB06X0F_C"},"RLCB06X0F_C AT%M754.0 :BOOL; (*照明控制箱06X0F-新云平台启停控制*)","RLCB06X0F_C             AT%M754.0      :BOOL; (*照明控制箱06X0F-新云平台启停控制*)"]
["照明控制箱","R","M","07X0F","启停控制","756.0",null,{"$f":"IF((IF(OR(I589=\"INT\",I589=\"WORD\",I589=\"BOOL\"),MOD(F589,2),MOD(F589,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A589&D589&\"-新云平台\"&E589","v":"照明控制箱07X0F-新云平台启停控制"},{"$f":"B589&VLOOKUP(A589,List!$B$3:$D$445,2,FALSE)&D589&\"_\"&VLOOKUP(E589,List!$K$2:$M$447,2,FALSE)","v":"RLCB07X0F_C"},{"$f":"K589&\" \"&\"AT%\"&C589&F589&\" \"&\":\"&I589&\";\"&\" \"&\"(*\"&J589&\"*)\"","v":"RLCB07X0F_C AT%M756.0 :BOOL; (*照明控制箱07X0F-新云平台启停控制*)"},{"$f":"REPLACE(REPLACE(L589,SEARCH(\"AT%\",L589),,REPT(\" \",25-SEARCH(\"AT%\",L589))),SEARCH(\":\",REPLACE(L589,SEARCH(\"AT%\",L589),,REPT(\" \",25-SEARCH(\"AT%\",L589)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L589,SEARCH(\"AT%\",L589),,REPT(\" \",25-SEARCH(\"AT%\",L589))))))","v":"RLCB07X0F_C             AT%M756.0      :BOOL; (*照明控制箱07X0F-新云平台启停控制*)"}]
["照明控制箱","R","M","08X0F","启停控制","758.0",null,"验证通过","BOOL","照明控制箱08X0F-新云平台启停控制",{"$f":"B590&VLOOKUP(A590,List!$B$3:$D$445,2,FALSE)&D590&\"_\"&VLOOKUP(E590,List!$K$2:$M$447,2,FALSE)","v":"RLCB08X0F_C"},"RLCB08X0F_C AT%M758.0 :BOOL; (*照明控制箱08X0F-新云平台启停控制*)","RLCB08X0F_C             AT%M758.0      :BOOL; (*照明控制箱08X0F-新云平台启停控制*)"]
["照明控制箱","R","M","B3X0G","启停控制","760.0",null,"验证通过","BOOL","照明控制箱B3X0G-新云平台启停控制",{"$f":"B591&VLOOKUP(A591,List!$B$3:$D$445,2,FALSE)&D591&\"_\"&VLOOKUP(E591,List!$K$2:$M$447,2,FALSE)","v":"RLCBB3X0G_C"},{"$f":"K591&\" \"&\"AT%\"&C591&F591&\" \"&\":\"&I591&\";\"&\" \"&\"(*\"&J591&\"*)\"","v":"RLCBB3X0G_C AT%M760.0 :BOOL; (*照明控制箱B3X0G-新云平台启停控制*)"},{"$f":"REPLACE(REPLACE(L591,SEARCH(\"AT%\",L591),,REPT(\" \",25-SEARCH(\"AT%\",L591))),SEARCH(\":\",REPLACE(L591,SEARCH(\"AT%\",L591),,REPT(\" \",25-SEARCH(\"AT%\",L591)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L591,SEARCH(\"AT%\",L591),,REPT(\" \",25-SEARCH(\"AT%\",L591))))))","v":"RLCBB3X0G_C             AT%M760.0      :BOOL; (*照明控制箱B3X0G-新云平台启停控制*)"}]
["照明控制箱","R","M","B2X0G","启停控制","762.0",null,"验证通过","BOOL","照明控制箱B2X0G-新云平台启停控制",{"$f":"B592&VLOOKUP(A592,List!$B$3:$D$445,2,FALSE)&D592&\"_\"&VLOOKUP(E592,List!$K$2:$M$447,2,FALSE)","v":"RLCBB2X0G_C"},"RLCBB2X0G_C AT%M762.0 :BOOL; (*照明控制箱B2X0G-新云平台启停控制*)","RLCBB2X0G_C             AT%M762.0      :BOOL; (*照明控制箱B2X0G-新云平台启停控制*)"]
["照明控制箱","R","M","B1X0G","启停控制","764.0",null,"验证通过","BOOL","照明控制箱B1X0G-新云平台启停控制",{"$f":"B593&VLOOKUP(A593,List!$B$3:$D$445,2,FALSE)&D593&\"_\"&VLOOKUP(E593,List!$K$2:$M$447,2,FALSE)","v":"RLCBB1X0G_C"},"RLCBB1X0G_C AT%M764.0 :BOOL; (*照明控制箱B1X0G-新云平台启停控制*)","RLCBB1X0G_C             AT%M764.0      :BOOL; (*照明控制箱B1X0G-新云平台启停控制*)"]
["照明控制箱","R","M","01X0G","启停控制","766.0",null,"验证通过","BOOL","照明控制箱01X0G-新云平台启停控制",{"$f":"B594&VLOOKUP(A594,List!$B$3:$D$445,2,FALSE)&D594&\"_\"&VLOOKUP(E594,List!$K$2:$M$447,2,FALSE)","v":"RLCB01X0G_C"},"RLCB01X0G_C AT%M766.0 :BOOL; (*照明控制箱01X0G-新云平台启停控制*)","RLCB01X0G_C             AT%M766.0      :BOOL; (*照明控制箱01X0G-新云平台启停控制*)"]
["照明控制箱","R","M","02X0G","启停控制","768.0",null,"验证通过","BOOL","照明控制箱02X0G-新云平台启停控制",{"$f":"B595&VLOOKUP(A595,List!$B$3:$D$445,2,FALSE)&D595&\"_\"&VLOOKUP(E595,List!$K$2:$M$447,2,FALSE)","v":"RLCB02X0G_C"},"RLCB02X0G_C AT%M768.0 :BOOL; (*照明控制箱02X0G-新云平台启停控制*)","RLCB02X0G_C             AT%M768.0      :BOOL; (*照明控制箱02X0G-新云平台启停控制*)"]
["照明控制箱","R","M","03X0G","启停控制",{"$f":"IF(OR(I595=\"REAL\",I595=\"DWORD\",I595=\"DINT\"),(IF(OR(I596=\"REAL\",I596=\"DWORD\",I596=\"DINT\"),F595+4+MOD(F595,4),F595+4)),(IF(OR(I596=\"REAL\",I596=\"DWORD\",I596=\"DINT\"),F595+4+MOD(F595,4),F595+2)))&\".0\"","v":"770.0"},null,"验证通过","BOOL","照明控制箱03X0G-新云平台启停控制",{"$f":"B596&VLOOKUP(A596,List!$B$3:$D$445,2,FALSE)&D596&\"_\"&VLOOKUP(E596,List!$K$2:$M$447,2,FALSE)","v":"RLCB03X0G_C"},"RLCB03X0G_C AT%M770.0 :BOOL; (*照明控制箱03X0G-新云平台启停控制*)","RLCB03X0G_C             AT%M770.0      :BOOL; (*照明控制箱03X0G-新云平台启停控制*)"]
["照明控制箱","R","M","04X0G","启停控制","772.0",null,"验证通过","BOOL","照明控制箱04X0G-新云平台启停控制",{"$f":"B597&VLOOKUP(A597,List!$B$3:$D$445,2,FALSE)&D597&\"_\"&VLOOKUP(E597,List!$K$2:$M$447,2,FALSE)","v":"RLCB04X0G_C"},"RLCB04X0G_C AT%M772.0 :BOOL; (*照明控制箱04X0G-新云平台启停控制*)","RLCB04X0G_C             AT%M772.0      :BOOL; (*照明控制箱04X0G-新云平台启停控制*)"]
["照明控制箱","R","M","05X0G","启停控制","774.0",null,"验证通过","BOOL","照明控制箱05X0G-新云平台启停控制",{"$f":"B598&VLOOKUP(A598,List!$B$3:$D$445,2,FALSE)&D598&\"_\"&VLOOKUP(E598,List!$K$2:$M$447,2,FALSE)","v":"RLCB05X0G_C"},"RLCB05X0G_C AT%M774.0 :BOOL; (*照明控制箱05X0G-新云平台启停控制*)","RLCB05X0G_C             AT%M774.0      :BOOL; (*照明控制箱05X0G-新云平台启停控制*)"]
["照明控制箱","R","M","06X0G","启停控制","776.0",null,"验证通过","BOOL","照明控制箱06X0G-新云平台启停控制",{"$f":"B599&VLOOKUP(A599,List!$B$3:$D$445,2,FALSE)&D599&\"_\"&VLOOKUP(E599,List!$K$2:$M$447,2,FALSE)","v":"RLCB06X0G_C"},"RLCB06X0G_C AT%M776.0 :BOOL; (*照明控制箱06X0G-新云平台启停控制*)","RLCB06X0G_C             AT%M776.0      :BOOL; (*照明控制箱06X0G-新云平台启停控制*)"]
["照明控制箱","R","M","07X0G","启停控制","778.0",null,{"$f":"IF((IF(OR(I600=\"INT\",I600=\"WORD\",I600=\"BOOL\"),MOD(F600,2),MOD(F600,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A600&D600&\"-新云平台\"&E600","v":"照明控制箱07X0G-新云平台启停控制"},{"$f":"B600&VLOOKUP(A600,List!$B$3:$D$445,2,FALSE)&D600&\"_\"&VLOOKUP(E600,List!$K$2:$M$447,2,FALSE)","v":"RLCB07X0G_C"},{"$f":"K600&\" \"&\"AT%\"&C600&F600&\" \"&\":\"&I600&\";\"&\" \"&\"(*\"&J600&\"*)\"","v":"RLCB07X0G_C AT%M778.0 :BOOL; (*照明控制箱07X0G-新云平台启停控制*)"},{"$f":"REPLACE(REPLACE(L600,SEARCH(\"AT%\",L600),,REPT(\" \",25-SEARCH(\"AT%\",L600))),SEARCH(\":\",REPLACE(L600,SEARCH(\"AT%\",L600),,REPT(\" \",25-SEARCH(\"AT%\",L600)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L600,SEARCH(\"AT%\",L600),,REPT(\" \",25-SEARCH(\"AT%\",L600))))))","v":"RLCB07X0G_C             AT%M778.0      :BOOL; (*照明控制箱07X0G-新云平台启停控制*)"}]
["照明控制箱","R","M","08X0G","启停控制","780.0",null,"验证通过","BOOL","照明控制箱08X0G-新云平台启停控制",{"$f":"B601&VLOOKUP(A601,List!$B$3:$D$445,2,FALSE)&D601&\"_\"&VLOOKUP(E601,List!$K$2:$M$447,2,FALSE)","v":"RLCB08X0G_C"},"RLCB08X0G_C AT%M780.0 :BOOL; (*照明控制箱08X0G-新云平台启停控制*)","RLCB08X0G_C             AT%M780.0      :BOOL; (*照明控制箱08X0G-新云平台启停控制*)"]
["照明控制箱","R","M","B3X0H","启停控制","782.0",null,"验证通过","BOOL","照明控制箱B3X0H-新云平台启停控制",{"$f":"B602&VLOOKUP(A602,List!$B$3:$D$445,2,FALSE)&D602&\"_\"&VLOOKUP(E602,List!$K$2:$M$447,2,FALSE)","v":"RLCBB3X0H_C"},"RLCBB3X0H_C AT%M782.0 :BOOL; (*照明控制箱B3X0H-新云平台启停控制*)","RLCBB3X0H_C             AT%M782.0      :BOOL; (*照明控制箱B3X0H-新云平台启停控制*)"]
["照明控制箱","R","M","B2X0H","启停控制","784.0",null,"验证通过","BOOL","照明控制箱B2X0H-新云平台启停控制",{"$f":"B603&VLOOKUP(A603,List!$B$3:$D$445,2,FALSE)&D603&\"_\"&VLOOKUP(E603,List!$K$2:$M$447,2,FALSE)","v":"RLCBB2X0H_C"},"RLCBB2X0H_C AT%M784.0 :BOOL; (*照明控制箱B2X0H-新云平台启停控制*)","RLCBB2X0H_C             AT%M784.0      :BOOL; (*照明控制箱B2X0H-新云平台启停控制*)"]
["照明控制箱","R","M","B1X0H","启停控制","786.0",null,"验证通过","BOOL",{"$f":"A604&D604&\"-新云平台\"&E604","v":"照明控制箱B1X0H-新云平台启停控制"},{"$f":"B604&VLOOKUP(A604,List!$B$3:$D$445,2,FALSE)&D604&\"_\"&VLOOKUP(E604,List!$K$2:$M$447,2,FALSE)","v":"RLCBB1X0H_C"},"RLCBB1X0H_C AT%M786.0 :BOOL; (*照明控制箱B1X0H-新云平台启停控制*)","RLCBB1X0H_C             AT%M786.0      :BOOL; (*照明控制箱B1X0H-新云平台启停控制*)"]
["照明控制箱","R","M","01X0H","启停控制","788.0",null,"验证通过","BOOL","照明控制箱01X0H-新云平台启停控制",{"$f":"B605&VLOOKUP(A605,List!$B$3:$D$445,2,FALSE)&D605&\"_\"&VLOOKUP(E605,List!$K$2:$M$447,2,FALSE)","v":"RLCB01X0H_C"},"RLCB01X0H_C AT%M788.0 :BOOL; (*照明控制箱01X0H-新云平台启停控制*)","RLCB01X0H_C             AT%M788.0      :BOOL; (*照明控制箱01X0H-新云平台启停控制*)"]
["照明控制箱","R","M","02X0H","启停控制","790.0",null,"验证通过","BOOL","照明控制箱02X0H-新云平台启停控制",{"$f":"B606&VLOOKUP(A606,List!$B$3:$D$445,2,FALSE)&D606&\"_\"&VLOOKUP(E606,List!$K$2:$M$447,2,FALSE)","v":"RLCB02X0H_C"},"RLCB02X0H_C AT%M790.0 :BOOL; (*照明控制箱02X0H-新云平台启停控制*)","RLCB02X0H_C             AT%M790.0      :BOOL; (*照明控制箱02X0H-新云平台启停控制*)"]
["照明控制箱","R","M","03X0H","启停控制","792.0",null,"验证通过","BOOL","照明控制箱03X0H-新云平台启停控制",{"$f":"B607&VLOOKUP(A607,List!$B$3:$D$445,2,FALSE)&D607&\"_\"&VLOOKUP(E607,List!$K$2:$M$447,2,FALSE)","v":"RLCB03X0H_C"},"RLCB03X0H_C AT%M792.0 :BOOL; (*照明控制箱03X0H-新云平台启停控制*)","RLCB03X0H_C             AT%M792.0      :BOOL; (*照明控制箱03X0H-新云平台启停控制*)"]
["照明控制箱","R","M","04X0H","启停控制","794.0",null,"验证通过","BOOL","照明控制箱04X0H-新云平台启停控制",{"$f":"B608&VLOOKUP(A608,List!$B$3:$D$445,2,FALSE)&D608&\"_\"&VLOOKUP(E608,List!$K$2:$M$447,2,FALSE)","v":"RLCB04X0H_C"},"RLCB04X0H_C AT%M794.0 :BOOL; (*照明控制箱04X0H-新云平台启停控制*)","RLCB04X0H_C             AT%M794.0      :BOOL; (*照明控制箱04X0H-新云平台启停控制*)"]
["照明控制箱","R","M","05X0H","启停控制","796.0",null,"验证通过","BOOL","照明控制箱05X0H-新云平台启停控制",{"$f":"B609&VLOOKUP(A609,List!$B$3:$D$445,2,FALSE)&D609&\"_\"&VLOOKUP(E609,List!$K$2:$M$447,2,FALSE)","v":"RLCB05X0H_C"},"RLCB05X0H_C AT%M796.0 :BOOL; (*照明控制箱05X0H-新云平台启停控制*)","RLCB05X0H_C             AT%M796.0      :BOOL; (*照明控制箱05X0H-新云平台启停控制*)"]
["照明控制箱","R","M","06X0H","启停控制","798.0",null,"验证通过","BOOL","照明控制箱06X0H-新云平台启停控制",{"$f":"B610&VLOOKUP(A610,List!$B$3:$D$445,2,FALSE)&D610&\"_\"&VLOOKUP(E610,List!$K$2:$M$447,2,FALSE)","v":"RLCB06X0H_C"},"RLCB06X0H_C AT%M798.0 :BOOL; (*照明控制箱06X0H-新云平台启停控制*)","RLCB06X0H_C             AT%M798.0      :BOOL; (*照明控制箱06X0H-新云平台启停控制*)"]
["照明控制箱","R","M","07X0H","启停控制","800.0",null,{"$f":"IF((IF(OR(I611=\"INT\",I611=\"WORD\",I611=\"BOOL\"),MOD(F611,2),MOD(F611,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A611&D611&\"-新云平台\"&E611","v":"照明控制箱07X0H-新云平台启停控制"},{"$f":"B611&VLOOKUP(A611,List!$B$3:$D$445,2,FALSE)&D611&\"_\"&VLOOKUP(E611,List!$K$2:$M$447,2,FALSE)","v":"RLCB07X0H_C"},{"$f":"K611&\" \"&\"AT%\"&C611&F611&\" \"&\":\"&I611&\";\"&\" \"&\"(*\"&J611&\"*)\"","v":"RLCB07X0H_C AT%M800.0 :BOOL; (*照明控制箱07X0H-新云平台启停控制*)"},{"$f":"REPLACE(REPLACE(L611,SEARCH(\"AT%\",L611),,REPT(\" \",25-SEARCH(\"AT%\",L611))),SEARCH(\":\",REPLACE(L611,SEARCH(\"AT%\",L611),,REPT(\" \",25-SEARCH(\"AT%\",L611)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L611,SEARCH(\"AT%\",L611),,REPT(\" \",25-SEARCH(\"AT%\",L611))))))","v":"RLCB07X0H_C             AT%M800.0      :BOOL; (*照明控制箱07X0H-新云平台启停控制*)"}]
["照明控制箱","R","M","08X0H","启停控制","802.0",null,"验证通过","BOOL","照明控制箱08X0H-新云平台启停控制",{"$f":"B612&VLOOKUP(A612,List!$B$3:$D$445,2,FALSE)&D612&\"_\"&VLOOKUP(E612,List!$K$2:$M$447,2,FALSE)","v":"RLCB08X0H_C"},"RLCB08X0H_C AT%M802.0 :BOOL; (*照明控制箱08X0H-新云平台启停控制*)","RLCB08X0H_C             AT%M802.0      :BOOL; (*照明控制箱08X0H-新云平台启停控制*)"]
["空调机组","L","M","B3X00","设定温度值","808.0",null,{"$f":"IF((IF(OR(I613=\"INT\",I613=\"WORD\",I613=\"BOOL\"),MOD(F613,2),MOD(F613,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"REAL",{"$f":"A613&D613&\"-\"&E613","v":"空调机组B3X00-设定温度值"},{"$f":"B613&VLOOKUP(A613,List!$B$3:$D$445,2,FALSE)&D613&\"_\"&VLOOKUP(E613,List!$K$2:$M$447,2,FALSE)","v":"LAHUB3X00_TSET"},{"$f":"K613&\" \"&\"AT%\"&C613&F613&\" \"&\":\"&I613&\";\"&\" \"&\"(*\"&J613&\"*)\"","v":"LAHUB3X00_TSET AT%M808.0 :REAL; (*空调机组B3X00-设定温度值*)"},{"$f":"REPLACE(REPLACE(L613,SEARCH(\"AT%\",L613),,REPT(\" \",25-SEARCH(\"AT%\",L613))),SEARCH(\":\",REPLACE(L613,SEARCH(\"AT%\",L613),,REPT(\" \",25-SEARCH(\"AT%\",L613)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L613,SEARCH(\"AT%\",L613),,REPT(\" \",25-SEARCH(\"AT%\",L613))))))","v":"LAHUB3X00_TSET          AT%M808.0      :REAL; (*空调机组B3X00-设定温度值*)"}]
["空调机组","L","M","B2X00","设定温度值","812.0",null,"验证通过","REAL","空调机组B2X00-设定温度值",{"$f":"B614&VLOOKUP(A614,List!$B$3:$D$445,2,FALSE)&D614&\"_\"&VLOOKUP(E614,List!$K$2:$M$447,2,FALSE)","v":"LAHUB2X00_TSET"},"LAHUB2X00_TSET AT%M812.0 :REAL; (*空调机组B2X00-设定温度值*)","LAHUB2X00_TSET          AT%M812.0      :REAL; (*空调机组B2X00-设定温度值*)"]
["空调机组","L","M","B1X00","设定温度值","816.0",null,"验证通过","REAL","空调机组B1X00-设定温度值",{"$f":"B615&VLOOKUP(A615,List!$B$3:$D$445,2,FALSE)&D615&\"_\"&VLOOKUP(E615,List!$K$2:$M$447,2,FALSE)","v":"LAHUB1X00_TSET"},"LAHUB1X00_TSET AT%M816.0 :REAL; (*空调机组B1X00-设定温度值*)","LAHUB1X00_TSET          AT%M816.0      :REAL; (*空调机组B1X00-设定温度值*)"]
["空调机组","L","M","01X00","设定温度值","820.0",null,"验证通过","REAL","空调机组01X00-设定温度值",{"$f":"B616&VLOOKUP(A616,List!$B$3:$D$445,2,FALSE)&D616&\"_\"&VLOOKUP(E616,List!$K$2:$M$447,2,FALSE)","v":"LAHU01X00_TSET"},"LAHU01X00_TSET AT%M820.0 :REAL; (*空调机组01X00-设定温度值*)","LAHU01X00_TSET          AT%M820.0      :REAL; (*空调机组01X00-设定温度值*)"]
["空调机组","L","M","02X00","设定温度值","824.0",null,"验证通过","REAL","空调机组02X00-设定温度值",{"$f":"B617&VLOOKUP(A617,List!$B$3:$D$445,2,FALSE)&D617&\"_\"&VLOOKUP(E617,List!$K$2:$M$447,2,FALSE)","v":"LAHU02X00_TSET"},"LAHU02X00_TSET AT%M824.0 :REAL; (*空调机组02X00-设定温度值*)","LAHU02X00_TSET          AT%M824.0      :REAL; (*空调机组02X00-设定温度值*)"]
["空调机组","L","M","03X00","设定温度值","828.0",null,"验证通过","REAL","空调机组03X00-设定温度值",{"$f":"B618&VLOOKUP(A618,List!$B$3:$D$445,2,FALSE)&D618&\"_\"&VLOOKUP(E618,List!$K$2:$M$447,2,FALSE)","v":"LAHU03X00_TSET"},"LAHU03X00_TSET AT%M828.0 :REAL; (*空调机组03X00-设定温度值*)","LAHU03X00_TSET          AT%M828.0      :REAL; (*空调机组03X00-设定温度值*)"]
["空调机组","L","M","04X00","设定温度值","832.0",null,"验证通过","REAL","空调机组04X00-设定温度值",{"$f":"B619&VLOOKUP(A619,List!$B$3:$D$445,2,FALSE)&D619&\"_\"&VLOOKUP(E619,List!$K$2:$M$447,2,FALSE)","v":"LAHU04X00_TSET"},"LAHU04X00_TSET AT%M832.0 :REAL; (*空调机组04X00-设定温度值*)","LAHU04X00_TSET          AT%M832.0      :REAL; (*空调机组04X00-设定温度值*)"]
["空调机组","L","M","05X00","设定温度值","836.0",null,"验证通过","REAL","空调机组05X00-设定温度值",{"$f":"B620&VLOOKUP(A620,List!$B$3:$D$445,2,FALSE)&D620&\"_\"&VLOOKUP(E620,List!$K$2:$M$447,2,FALSE)","v":"LAHU05X00_TSET"},"LAHU05X00_TSET AT%M836.0 :REAL; (*空调机组05X00-设定温度值*)","LAHU05X00_TSET          AT%M836.0      :REAL; (*空调机组05X00-设定温度值*)"]
["空调机组","L","M","06X00","设定温度值","840.0",null,"验证通过","REAL","空调机组06X00-设定温度值",{"$f":"B621&VLOOKUP(A621,List!$B$3:$D$445,2,FALSE)&D621&\"_\"&VLOOKUP(E621,List!$K$2:$M$447,2,FALSE)","v":"LAHU06X00_TSET"},"LAHU06X00_TSET AT%M840.0 :REAL; (*空调机组06X00-设定温度值*)","LAHU06X00_TSET          AT%M840.0      :REAL; (*空调机组06X00-设定温度值*)"]
["空调机组","L","M","07X00","设定温度值","844.0",null,{"$f":"IF((IF(OR(I622=\"INT\",I622=\"WORD\",I622=\"BOOL\"),MOD(F622,2),MOD(F622,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"REAL",{"$f":"A622&D622&\"-\"&E622","v":"空调机组07X00-设定温度值"},{"$f":"B622&VLOOKUP(A622,List!$B$3:$D$445,2,FALSE)&D622&\"_\"&VLOOKUP(E622,List!$K$2:$M$447,2,FALSE)","v":"LAHU07X00_TSET"},{"$f":"K622&\" \"&\"AT%\"&C622&F622&\" \"&\":\"&I622&\";\"&\" \"&\"(*\"&J622&\"*)\"","v":"LAHU07X00_TSET AT%M844.0 :REAL; (*空调机组07X00-设定温度值*)"},{"$f":"REPLACE(REPLACE(L622,SEARCH(\"AT%\",L622),,REPT(\" \",25-SEARCH(\"AT%\",L622))),SEARCH(\":\",REPLACE(L622,SEARCH(\"AT%\",L622),,REPT(\" \",25-SEARCH(\"AT%\",L622)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L622,SEARCH(\"AT%\",L622),,REPT(\" \",25-SEARCH(\"AT%\",L622))))))","v":"LAHU07X00_TSET          AT%M844.0      :REAL; (*空调机组07X00-设定温度值*)"}]
["空调机组","L","M","08X00","设定温度值","848.0",null,"验证通过","REAL","空调机组08X00-设定温度值",{"$f":"B623&VLOOKUP(A623,List!$B$3:$D$445,2,FALSE)&D623&\"_\"&VLOOKUP(E623,List!$K$2:$M$447,2,FALSE)","v":"LAHU08X00_TSET"},"LAHU08X00_TSET AT%M848.0 :REAL; (*空调机组08X00-设定温度值*)","LAHU08X00_TSET          AT%M848.0      :REAL; (*空调机组08X00-设定温度值*)"]
["空调机组","L","M","B3X00","季节模式","852.0",null,"验证通过","INT","空调机组B3X00-季节模式",{"$f":"B624&VLOOKUP(A624,List!$B$3:$D$445,2,FALSE)&D624&\"_\"&VLOOKUP(E624,List!$K$2:$M$447,2,FALSE)","v":"LAHUB3X00_SM"},{"$f":"K624&\" \"&\"AT%\"&C624&F624&\" \"&\":\"&I624&\";\"&\" \"&\"(*\"&J624&\"*)\"","v":"LAHUB3X00_SM AT%M852.0 :INT; (*空调机组B3X00-季节模式*)"},{"$f":"REPLACE(REPLACE(L624,SEARCH(\"AT%\",L624),,REPT(\" \",25-SEARCH(\"AT%\",L624))),SEARCH(\":\",REPLACE(L624,SEARCH(\"AT%\",L624),,REPT(\" \",25-SEARCH(\"AT%\",L624)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L624,SEARCH(\"AT%\",L624),,REPT(\" \",25-SEARCH(\"AT%\",L624))))))","v":"LAHUB3X00_SM            AT%M852.0      :INT; (*空调机组B3X00-季节模式*)"}]
["空调机组","L","M","B2X00","季节模式","854.0",null,"验证通过","INT","空调机组B2X00-季节模式",{"$f":"B625&VLOOKUP(A625,List!$B$3:$D$445,2,FALSE)&D625&\"_\"&VLOOKUP(E625,List!$K$2:$M$447,2,FALSE)","v":"LAHUB2X00_SM"},"LAHUB2X00_SM AT%M854.0 :INT; (*空调机组B2X00-季节模式*)","LAHUB2X00_SM            AT%M854.0      :INT; (*空调机组B2X00-季节模式*)"]
["空调机组","L","M","B1X00","季节模式","856.0",null,"验证通过","INT","空调机组B1X00-季节模式",{"$f":"B626&VLOOKUP(A626,List!$B$3:$D$445,2,FALSE)&D626&\"_\"&VLOOKUP(E626,List!$K$2:$M$447,2,FALSE)","v":"LAHUB1X00_SM"},"LAHUB1X00_SM AT%M856.0 :INT; (*空调机组B1X00-季节模式*)","LAHUB1X00_SM            AT%M856.0      :INT; (*空调机组B1X00-季节模式*)"]
["空调机组","L","M","01X00","季节模式","858.0",null,"验证通过","INT","空调机组01X00-季节模式",{"$f":"B627&VLOOKUP(A627,List!$B$3:$D$445,2,FALSE)&D627&\"_\"&VLOOKUP(E627,List!$K$2:$M$447,2,FALSE)","v":"LAHU01X00_SM"},"LAHU01X00_SM AT%M858.0 :INT; (*空调机组01X00-季节模式*)","LAHU01X00_SM            AT%M858.0      :INT; (*空调机组01X00-季节模式*)"]
["空调机组","L","M","02X00","季节模式","860.0",null,"验证通过","INT","空调机组02X00-季节模式",{"$f":"B628&VLOOKUP(A628,List!$B$3:$D$445,2,FALSE)&D628&\"_\"&VLOOKUP(E628,List!$K$2:$M$447,2,FALSE)","v":"LAHU02X00_SM"},"LAHU02X00_SM AT%M860.0 :INT; (*空调机组02X00-季节模式*)","LAHU02X00_SM            AT%M860.0      :INT; (*空调机组02X00-季节模式*)"]
["空调机组","L","M","03X00","季节模式","862.0",null,"验证通过","INT","空调机组03X00-季节模式",{"$f":"B629&VLOOKUP(A629,List!$B$3:$D$445,2,FALSE)&D629&\"_\"&VLOOKUP(E629,List!$K$2:$M$447,2,FALSE)","v":"LAHU03X00_SM"},"LAHU03X00_SM AT%M862.0 :INT; (*空调机组03X00-季节模式*)","LAHU03X00_SM            AT%M862.0      :INT; (*空调机组03X00-季节模式*)"]
["空调机组","L","M","04X00","季节模式","864.0",null,"验证通过","INT","空调机组04X00-季节模式",{"$f":"B630&VLOOKUP(A630,List!$B$3:$D$445,2,FALSE)&D630&\"_\"&VLOOKUP(E630,List!$K$2:$M$447,2,FALSE)","v":"LAHU04X00_SM"},"LAHU04X00_SM AT%M864.0 :INT; (*空调机组04X00-季节模式*)","LAHU04X00_SM            AT%M864.0      :INT; (*空调机组04X00-季节模式*)"]
["空调机组","L","M","05X00","季节模式","866.0",null,"验证通过","INT","空调机组05X00-季节模式",{"$f":"B631&VLOOKUP(A631,List!$B$3:$D$445,2,FALSE)&D631&\"_\"&VLOOKUP(E631,List!$K$2:$M$447,2,FALSE)","v":"LAHU05X00_SM"},"LAHU05X00_SM AT%M866.0 :INT; (*空调机组05X00-季节模式*)","LAHU05X00_SM            AT%M866.0      :INT; (*空调机组05X00-季节模式*)"]
["空调机组","L","M","06X00","季节模式","868.0",null,"验证通过","INT","空调机组06X00-季节模式",{"$f":"B632&VLOOKUP(A632,List!$B$3:$D$445,2,FALSE)&D632&\"_\"&VLOOKUP(E632,List!$K$2:$M$447,2,FALSE)","v":"LAHU06X00_SM"},"LAHU06X00_SM AT%M868.0 :INT; (*空调机组06X00-季节模式*)","LAHU06X00_SM            AT%M868.0      :INT; (*空调机组06X00-季节模式*)"]
["空调机组","L","M","07X00","季节模式","870.0",null,{"$f":"IF((IF(OR(I633=\"INT\",I633=\"WORD\",I633=\"BOOL\"),MOD(F633,2),MOD(F633,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"INT",{"$f":"A633&D633&\"-\"&E633","v":"空调机组07X00-季节模式"},{"$f":"B633&VLOOKUP(A633,List!$B$3:$D$445,2,FALSE)&D633&\"_\"&VLOOKUP(E633,List!$K$2:$M$447,2,FALSE)","v":"LAHU07X00_SM"},{"$f":"K633&\" \"&\"AT%\"&C633&F633&\" \"&\":\"&I633&\";\"&\" \"&\"(*\"&J633&\"*)\"","v":"LAHU07X00_SM AT%M870.0 :INT; (*空调机组07X00-季节模式*)"},{"$f":"REPLACE(REPLACE(L633,SEARCH(\"AT%\",L633),,REPT(\" \",25-SEARCH(\"AT%\",L633))),SEARCH(\":\",REPLACE(L633,SEARCH(\"AT%\",L633),,REPT(\" \",25-SEARCH(\"AT%\",L633)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L633,SEARCH(\"AT%\",L633),,REPT(\" \",25-SEARCH(\"AT%\",L633))))))","v":"LAHU07X00_SM            AT%M870.0      :INT; (*空调机组07X00-季节模式*)"}]
["空调机组","L","M","08X00","季节模式","872.0",null,"验证通过","INT","空调机组08X00-季节模式",{"$f":"B634&VLOOKUP(A634,List!$B$3:$D$445,2,FALSE)&D634&\"_\"&VLOOKUP(E634,List!$K$2:$M$447,2,FALSE)","v":"LAHU08X00_SM"},"LAHU08X00_SM AT%M872.0 :INT; (*空调机组08X00-季节模式*)","LAHU08X00_SM            AT%M872.0      :INT; (*空调机组08X00-季节模式*)"]
["空调机组","L","M","B3X00","启停控制","874.0",null,"验证通过","BOOL","空调机组B3X00-启停控制",{"$f":"B635&VLOOKUP(A635,List!$B$3:$D$445,2,FALSE)&D635&\"_\"&VLOOKUP(E635,List!$K$2:$M$447,2,FALSE)","v":"LAHUB3X00_C"},{"$f":"K635&\" \"&\"AT%\"&C635&F635&\" \"&\":\"&I635&\";\"&\" \"&\"(*\"&J635&\"*)\"","v":"LAHUB3X00_C AT%M874.0 :BOOL; (*空调机组B3X00-启停控制*)"},{"$f":"REPLACE(REPLACE(L635,SEARCH(\"AT%\",L635),,REPT(\" \",25-SEARCH(\"AT%\",L635))),SEARCH(\":\",REPLACE(L635,SEARCH(\"AT%\",L635),,REPT(\" \",25-SEARCH(\"AT%\",L635)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L635,SEARCH(\"AT%\",L635),,REPT(\" \",25-SEARCH(\"AT%\",L635))))))","v":"LAHUB3X00_C             AT%M874.0      :BOOL; (*空调机组B3X00-启停控制*)"}]
["空调机组","L","M","B2X00","启停控制","876.0",null,"验证通过","BOOL","空调机组B2X00-启停控制",{"$f":"B636&VLOOKUP(A636,List!$B$3:$D$445,2,FALSE)&D636&\"_\"&VLOOKUP(E636,List!$K$2:$M$447,2,FALSE)","v":"LAHUB2X00_C"},"LAHUB2X00_C AT%M876.0 :BOOL; (*空调机组B2X00-启停控制*)","LAHUB2X00_C             AT%M876.0      :BOOL; (*空调机组B2X00-启停控制*)"]
["空调机组","L","M","B1X00","启停控制","878.0",null,"验证通过","BOOL","空调机组B1X00-启停控制",{"$f":"B637&VLOOKUP(A637,List!$B$3:$D$445,2,FALSE)&D637&\"_\"&VLOOKUP(E637,List!$K$2:$M$447,2,FALSE)","v":"LAHUB1X00_C"},"LAHUB1X00_C AT%M878.0 :BOOL; (*空调机组B1X00-启停控制*)","LAHUB1X00_C             AT%M878.0      :BOOL; (*空调机组B1X00-启停控制*)"]
["空调机组","L","M","01X00","启停控制","880.0",null,"验证通过","BOOL","空调机组01X00-启停控制",{"$f":"B638&VLOOKUP(A638,List!$B$3:$D$445,2,FALSE)&D638&\"_\"&VLOOKUP(E638,List!$K$2:$M$447,2,FALSE)","v":"LAHU01X00_C"},"LAHU01X00_C AT%M880.0 :BOOL; (*空调机组01X00-启停控制*)","LAHU01X00_C             AT%M880.0      :BOOL; (*空调机组01X00-启停控制*)"]
["空调机组","L","M","02X00","启停控制","882.0",null,"验证通过","BOOL","空调机组02X00-启停控制",{"$f":"B639&VLOOKUP(A639,List!$B$3:$D$445,2,FALSE)&D639&\"_\"&VLOOKUP(E639,List!$K$2:$M$447,2,FALSE)","v":"LAHU02X00_C"},"LAHU02X00_C AT%M882.0 :BOOL; (*空调机组02X00-启停控制*)","LAHU02X00_C             AT%M882.0      :BOOL; (*空调机组02X00-启停控制*)"]
["空调机组","L","M","03X00","启停控制","884.0",null,"验证通过","BOOL","空调机组03X00-启停控制",{"$f":"B640&VLOOKUP(A640,List!$B$3:$D$445,2,FALSE)&D640&\"_\"&VLOOKUP(E640,List!$K$2:$M$447,2,FALSE)","v":"LAHU03X00_C"},"LAHU03X00_C AT%M884.0 :BOOL; (*空调机组03X00-启停控制*)","LAHU03X00_C             AT%M884.0      :BOOL; (*空调机组03X00-启停控制*)"]
["空调机组","L","M","04X00","启停控制","886.0",null,"验证通过","BOOL","空调机组04X00-启停控制",{"$f":"B641&VLOOKUP(A641,List!$B$3:$D$445,2,FALSE)&D641&\"_\"&VLOOKUP(E641,List!$K$2:$M$447,2,FALSE)","v":"LAHU04X00_C"},"LAHU04X00_C AT%M886.0 :BOOL; (*空调机组04X00-启停控制*)","LAHU04X00_C             AT%M886.0      :BOOL; (*空调机组04X00-启停控制*)"]
["空调机组","L","M","05X00","启停控制","888.0",null,"验证通过","BOOL","空调机组05X00-启停控制",{"$f":"B642&VLOOKUP(A642,List!$B$3:$D$445,2,FALSE)&D642&\"_\"&VLOOKUP(E642,List!$K$2:$M$447,2,FALSE)","v":"LAHU05X00_C"},"LAHU05X00_C AT%M888.0 :BOOL; (*空调机组05X00-启停控制*)","LAHU05X00_C             AT%M888.0      :BOOL; (*空调机组05X00-启停控制*)"]
["空调机组","L","M","06X00","启停控制","890.0",null,"验证通过","BOOL","空调机组06X00-启停控制",{"$f":"B643&VLOOKUP(A643,List!$B$3:$D$445,2,FALSE)&D643&\"_\"&VLOOKUP(E643,List!$K$2:$M$447,2,FALSE)","v":"LAHU06X00_C"},"LAHU06X00_C AT%M890.0 :BOOL; (*空调机组06X00-启停控制*)","LAHU06X00_C             AT%M890.0      :BOOL; (*空调机组06X00-启停控制*)"]
["空调机组","L","M","07X00","启停控制","892.0",null,{"$f":"IF((IF(OR(I644=\"INT\",I644=\"WORD\",I644=\"BOOL\"),MOD(F644,2),MOD(F644,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A644&D644&\"-\"&E644","v":"空调机组07X00-启停控制"},{"$f":"B644&VLOOKUP(A644,List!$B$3:$D$445,2,FALSE)&D644&\"_\"&VLOOKUP(E644,List!$K$2:$M$447,2,FALSE)","v":"LAHU07X00_C"},{"$f":"K644&\" \"&\"AT%\"&C644&F644&\" \"&\":\"&I644&\";\"&\" \"&\"(*\"&J644&\"*)\"","v":"LAHU07X00_C AT%M892.0 :BOOL; (*空调机组07X00-启停控制*)"},{"$f":"REPLACE(REPLACE(L644,SEARCH(\"AT%\",L644),,REPT(\" \",25-SEARCH(\"AT%\",L644))),SEARCH(\":\",REPLACE(L644,SEARCH(\"AT%\",L644),,REPT(\" \",25-SEARCH(\"AT%\",L644)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L644,SEARCH(\"AT%\",L644),,REPT(\" \",25-SEARCH(\"AT%\",L644))))))","v":"LAHU07X00_C             AT%M892.0      :BOOL; (*空调机组07X00-启停控制*)"}]
["空调机组","L","M","08X00","启停控制","894.0",null,"验证通过","BOOL","空调机组08X00-启停控制",{"$f":"B645&VLOOKUP(A645,List!$B$3:$D$445,2,FALSE)&D645&\"_\"&VLOOKUP(E645,List!$K$2:$M$447,2,FALSE)","v":"LAHU08X00_C"},"LAHU08X00_C AT%M894.0 :BOOL; (*空调机组08X00-启停控制*)","LAHU08X00_C             AT%M894.0      :BOOL; (*空调机组08X00-启停控制*)"]
["空调机组","L","M","B3X00","定时控制","896.0",null,{"$f":"IF((IF(OR(I646=\"INT\",I646=\"WORD\",I646=\"BOOL\"),MOD(F646,2),MOD(F646,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","空调机组B3X00-定时控制",{"$f":"B646&VLOOKUP(A646,List!$B$3:$D$445,2,FALSE)&D646&\"_\"&VLOOKUP(E646,List!$K$2:$M$447,2,FALSE)","v":"LAHUB3X00_TC"},"LAHUB3X00_TC AT%M896.0 :BOOL; (*空调机组B3X00-定时控制*)","LAHUB3X00_TC            AT%M896.0      :BOOL; (*空调机组B3X00-定时控制*)"]
["空调机组","L","M","B2X00","定时控制","898.0",null,"验证通过","BOOL","空调机组B2X00-定时控制",{"$f":"B647&VLOOKUP(A647,List!$B$3:$D$445,2,FALSE)&D647&\"_\"&VLOOKUP(E647,List!$K$2:$M$447,2,FALSE)","v":"LAHUB2X00_TC"},"LAHUB2X00_TC AT%M898.0 :BOOL; (*空调机组B2X00-定时控制*)","LAHUB2X00_TC            AT%M898.0      :BOOL; (*空调机组B2X00-定时控制*)"]
["空调机组","L","M","B1X00","定时控制","900.0",null,"验证通过","BOOL","空调机组B1X00-定时控制",{"$f":"B648&VLOOKUP(A648,List!$B$3:$D$445,2,FALSE)&D648&\"_\"&VLOOKUP(E648,List!$K$2:$M$447,2,FALSE)","v":"LAHUB1X00_TC"},"LAHUB1X00_TC AT%M900.0 :BOOL; (*空调机组B1X00-定时控制*)","LAHUB1X00_TC            AT%M900.0      :BOOL; (*空调机组B1X00-定时控制*)"]
["空调机组","L","M","01X00","定时控制","902.0",null,"验证通过","BOOL","空调机组01X00-定时控制",{"$f":"B649&VLOOKUP(A649,List!$B$3:$D$445,2,FALSE)&D649&\"_\"&VLOOKUP(E649,List!$K$2:$M$447,2,FALSE)","v":"LAHU01X00_TC"},"LAHU01X00_TC AT%M902.0 :BOOL; (*空调机组01X00-定时控制*)","LAHU01X00_TC            AT%M902.0      :BOOL; (*空调机组01X00-定时控制*)"]
["空调机组","L","M","02X00","定时控制","904.0",null,"验证通过","BOOL","空调机组02X00-定时控制",{"$f":"B650&VLOOKUP(A650,List!$B$3:$D$445,2,FALSE)&D650&\"_\"&VLOOKUP(E650,List!$K$2:$M$447,2,FALSE)","v":"LAHU02X00_TC"},"LAHU02X00_TC AT%M904.0 :BOOL; (*空调机组02X00-定时控制*)","LAHU02X00_TC            AT%M904.0      :BOOL; (*空调机组02X00-定时控制*)"]
["空调机组","L","M","03X00","定时控制","906.0",null,"验证通过","BOOL","空调机组03X00-定时控制",{"$f":"B651&VLOOKUP(A651,List!$B$3:$D$445,2,FALSE)&D651&\"_\"&VLOOKUP(E651,List!$K$2:$M$447,2,FALSE)","v":"LAHU03X00_TC"},"LAHU03X00_TC AT%M906.0 :BOOL; (*空调机组03X00-定时控制*)","LAHU03X00_TC            AT%M906.0      :BOOL; (*空调机组03X00-定时控制*)"]
["空调机组","L","M","04X00","定时控制","908.0",null,"验证通过","BOOL","空调机组04X00-定时控制",{"$f":"B652&VLOOKUP(A652,List!$B$3:$D$445,2,FALSE)&D652&\"_\"&VLOOKUP(E652,List!$K$2:$M$447,2,FALSE)","v":"LAHU04X00_TC"},"LAHU04X00_TC AT%M908.0 :BOOL; (*空调机组04X00-定时控制*)","LAHU04X00_TC            AT%M908.0      :BOOL; (*空调机组04X00-定时控制*)"]
["空调机组","L","M","05X00","定时控制","910.0",null,"验证通过","BOOL","空调机组05X00-定时控制",{"$f":"B653&VLOOKUP(A653,List!$B$3:$D$445,2,FALSE)&D653&\"_\"&VLOOKUP(E653,List!$K$2:$M$447,2,FALSE)","v":"LAHU05X00_TC"},"LAHU05X00_TC AT%M910.0 :BOOL; (*空调机组05X00-定时控制*)","LAHU05X00_TC            AT%M910.0      :BOOL; (*空调机组05X00-定时控制*)"]
["空调机组","L","M","06X00","定时控制","912.0",null,"验证通过","BOOL","空调机组06X00-定时控制",{"$f":"B654&VLOOKUP(A654,List!$B$3:$D$445,2,FALSE)&D654&\"_\"&VLOOKUP(E654,List!$K$2:$M$447,2,FALSE)","v":"LAHU06X00_TC"},"LAHU06X00_TC AT%M912.0 :BOOL; (*空调机组06X00-定时控制*)","LAHU06X00_TC            AT%M912.0      :BOOL; (*空调机组06X00-定时控制*)"]
["空调机组","L","M","07X00","定时控制","914.0",null,{"$f":"IF((IF(OR(I655=\"INT\",I655=\"WORD\",I655=\"BOOL\"),MOD(F655,2),MOD(F655,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A655&D655&\"-\"&E655","v":"空调机组07X00-定时控制"},{"$f":"B655&VLOOKUP(A655,List!$B$3:$D$445,2,FALSE)&D655&\"_\"&VLOOKUP(E655,List!$K$2:$M$447,2,FALSE)","v":"LAHU07X00_TC"},{"$f":"K655&\" \"&\"AT%\"&C655&F655&\" \"&\":\"&I655&\";\"&\" \"&\"(*\"&J655&\"*)\"","v":"LAHU07X00_TC AT%M914.0 :BOOL; (*空调机组07X00-定时控制*)"},{"$f":"REPLACE(REPLACE(L655,SEARCH(\"AT%\",L655),,REPT(\" \",25-SEARCH(\"AT%\",L655))),SEARCH(\":\",REPLACE(L655,SEARCH(\"AT%\",L655),,REPT(\" \",25-SEARCH(\"AT%\",L655)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L655,SEARCH(\"AT%\",L655),,REPT(\" \",25-SEARCH(\"AT%\",L655))))))","v":"LAHU07X00_TC            AT%M914.0      :BOOL; (*空调机组07X00-定时控制*)"}]
["空调机组","L","M","08X00","定时控制","916.0",null,"验证通过","BOOL","空调机组08X00-定时控制",{"$f":"B656&VLOOKUP(A656,List!$B$3:$D$445,2,FALSE)&D656&\"_\"&VLOOKUP(E656,List!$K$2:$M$447,2,FALSE)","v":"LAHU08X00_TC"},"LAHU08X00_TC AT%M916.0 :BOOL; (*空调机组08X00-定时控制*)","LAHU08X00_TC            AT%M916.0      :BOOL; (*空调机组08X00-定时控制*)"]
["空调机组","L","M","B3X00","定时模式","918.0",null,"验证通过","BOOL","空调机组B3X00-定时模式",{"$f":"B657&VLOOKUP(A657,List!$B$3:$D$445,2,FALSE)&D657&\"_\"&VLOOKUP(E657,List!$K$2:$M$447,2,FALSE)","v":"LAHUB3X00_TM"},"LAHUB3X00_TM AT%M918.0 :BOOL; (*空调机组B3X00-定时模式*)","LAHUB3X00_TM            AT%M918.0      :BOOL; (*空调机组B3X00-定时模式*)"]
["空调机组","L","M","B2X00","定时模式","920.0",null,"验证通过","BOOL","空调机组B2X00-定时模式",{"$f":"B658&VLOOKUP(A658,List!$B$3:$D$445,2,FALSE)&D658&\"_\"&VLOOKUP(E658,List!$K$2:$M$447,2,FALSE)","v":"LAHUB2X00_TM"},"LAHUB2X00_TM AT%M920.0 :BOOL; (*空调机组B2X00-定时模式*)","LAHUB2X00_TM            AT%M920.0      :BOOL; (*空调机组B2X00-定时模式*)"]
["空调机组","L","M","B1X00","定时模式","922.0",null,"验证通过","BOOL","空调机组B1X00-定时模式",{"$f":"B659&VLOOKUP(A659,List!$B$3:$D$445,2,FALSE)&D659&\"_\"&VLOOKUP(E659,List!$K$2:$M$447,2,FALSE)","v":"LAHUB1X00_TM"},"LAHUB1X00_TM AT%M922.0 :BOOL; (*空调机组B1X00-定时模式*)","LAHUB1X00_TM            AT%M922.0      :BOOL; (*空调机组B1X00-定时模式*)"]
["空调机组","L","M","01X00","定时模式",{"$f":"IF(OR(I659=\"REAL\",I659=\"DWORD\",I659=\"DINT\"),(IF(OR(I660=\"REAL\",I660=\"DWORD\",I660=\"DINT\"),F659+4+MOD(F659,4),F659+4)),(IF(OR(I660=\"REAL\",I660=\"DWORD\",I660=\"DINT\"),F659+4+MOD(F659,4),F659+2)))&\".0\"","v":"924.0"},null,"验证通过","BOOL","空调机组01X00-定时模式",{"$f":"B660&VLOOKUP(A660,List!$B$3:$D$445,2,FALSE)&D660&\"_\"&VLOOKUP(E660,List!$K$2:$M$447,2,FALSE)","v":"LAHU01X00_TM"},"LAHU01X00_TM AT%M924.0 :BOOL; (*空调机组01X00-定时模式*)","LAHU01X00_TM            AT%M924.0      :BOOL; (*空调机组01X00-定时模式*)"]
["空调机组","L","M","02X00","定时模式","926.0",null,"验证通过","BOOL","空调机组02X00-定时模式",{"$f":"B661&VLOOKUP(A661,List!$B$3:$D$445,2,FALSE)&D661&\"_\"&VLOOKUP(E661,List!$K$2:$M$447,2,FALSE)","v":"LAHU02X00_TM"},"LAHU02X00_TM AT%M926.0 :BOOL; (*空调机组02X00-定时模式*)","LAHU02X00_TM            AT%M926.0      :BOOL; (*空调机组02X00-定时模式*)"]
["空调机组","L","M","03X00","定时模式","928.0",null,"验证通过","BOOL","空调机组03X00-定时模式",{"$f":"B662&VLOOKUP(A662,List!$B$3:$D$445,2,FALSE)&D662&\"_\"&VLOOKUP(E662,List!$K$2:$M$447,2,FALSE)","v":"LAHU03X00_TM"},"LAHU03X00_TM AT%M928.0 :BOOL; (*空调机组03X00-定时模式*)","LAHU03X00_TM            AT%M928.0      :BOOL; (*空调机组03X00-定时模式*)"]
["空调机组","L","M","04X00","定时模式","930.0",null,"验证通过","BOOL","空调机组04X00-定时模式",{"$f":"B663&VLOOKUP(A663,List!$B$3:$D$445,2,FALSE)&D663&\"_\"&VLOOKUP(E663,List!$K$2:$M$447,2,FALSE)","v":"LAHU04X00_TM"},"LAHU04X00_TM AT%M930.0 :BOOL; (*空调机组04X00-定时模式*)","LAHU04X00_TM            AT%M930.0      :BOOL; (*空调机组04X00-定时模式*)"]
["空调机组","L","M","05X00","定时模式","932.0",null,"验证通过","BOOL","空调机组05X00-定时模式",{"$f":"B664&VLOOKUP(A664,List!$B$3:$D$445,2,FALSE)&D664&\"_\"&VLOOKUP(E664,List!$K$2:$M$447,2,FALSE)","v":"LAHU05X00_TM"},"LAHU05X00_TM AT%M932.0 :BOOL; (*空调机组05X00-定时模式*)","LAHU05X00_TM            AT%M932.0      :BOOL; (*空调机组05X00-定时模式*)"]
["空调机组","L","M","06X00","定时模式","934.0",null,"验证通过","BOOL","空调机组06X00-定时模式",{"$f":"B665&VLOOKUP(A665,List!$B$3:$D$445,2,FALSE)&D665&\"_\"&VLOOKUP(E665,List!$K$2:$M$447,2,FALSE)","v":"LAHU06X00_TM"},"LAHU06X00_TM AT%M934.0 :BOOL; (*空调机组06X00-定时模式*)","LAHU06X00_TM            AT%M934.0      :BOOL; (*空调机组06X00-定时模式*)"]
["空调机组","L","M","07X00","定时模式","936.0",null,{"$f":"IF((IF(OR(I666=\"INT\",I666=\"WORD\",I666=\"BOOL\"),MOD(F666,2),MOD(F666,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A666&D666&\"-\"&E666","v":"空调机组07X00-定时模式"},{"$f":"B666&VLOOKUP(A666,List!$B$3:$D$445,2,FALSE)&D666&\"_\"&VLOOKUP(E666,List!$K$2:$M$447,2,FALSE)","v":"LAHU07X00_TM"},{"$f":"K666&\" \"&\"AT%\"&C666&F666&\" \"&\":\"&I666&\";\"&\" \"&\"(*\"&J666&\"*)\"","v":"LAHU07X00_TM AT%M936.0 :BOOL; (*空调机组07X00-定时模式*)"},{"$f":"REPLACE(REPLACE(L666,SEARCH(\"AT%\",L666),,REPT(\" \",25-SEARCH(\"AT%\",L666))),SEARCH(\":\",REPLACE(L666,SEARCH(\"AT%\",L666),,REPT(\" \",25-SEARCH(\"AT%\",L666)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L666,SEARCH(\"AT%\",L666),,REPT(\" \",25-SEARCH(\"AT%\",L666))))))","v":"LAHU07X00_TM            AT%M936.0      :BOOL; (*空调机组07X00-定时模式*)"}]
["空调机组","L","M","08X00","定时模式","938.0",null,"验证通过","BOOL","空调机组08X00-定时模式",{"$f":"B667&VLOOKUP(A667,List!$B$3:$D$445,2,FALSE)&D667&\"_\"&VLOOKUP(E667,List!$K$2:$M$447,2,FALSE)","v":"LAHU08X00_TM"},"LAHU08X00_TM AT%M938.0 :BOOL; (*空调机组08X00-定时模式*)","LAHU08X00_TM            AT%M938.0      :BOOL; (*空调机组08X00-定时模式*)"]
["空调机组","R","M","B3X00","设定温度值","944.0",null,{"$f":"IF((IF(OR(I668=\"INT\",I668=\"WORD\",I668=\"BOOL\"),MOD(F668,2),MOD(F668,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"REAL",{"$f":"A668&D668&\"-新云平台\"&E668","v":"空调机组B3X00-新云平台设定温度值"},{"$f":"B668&VLOOKUP(A668,List!$B$3:$D$445,2,FALSE)&D668&\"_\"&VLOOKUP(E668,List!$K$2:$M$447,2,FALSE)","v":"RAHUB3X00_TSET"},"RAHUB3X00_TSET AT%M944.0 :REAL; (*空调机组B3X00-新云平台设定温度值*)","RAHUB3X00_TSET          AT%M944.0      :REAL; (*空调机组B3X00-新云平台设定温度值*)"]
["空调机组","R","M","B2X00","设定温度值","948.0",null,"验证通过","REAL",{"$f":"A669&D669&\"-新云平台\"&E669","v":"空调机组B2X00-新云平台设定温度值"},{"$f":"B669&VLOOKUP(A669,List!$B$3:$D$445,2,FALSE)&D669&\"_\"&VLOOKUP(E669,List!$K$2:$M$447,2,FALSE)","v":"RAHUB2X00_TSET"},"RAHUB2X00_TSET AT%M948.0 :REAL; (*空调机组B2X00-新云平台设定温度值*)","RAHUB2X00_TSET          AT%M948.0      :REAL; (*空调机组B2X00-新云平台设定温度值*)"]
["空调机组","R","M","B1X00","设定温度值","952.0",null,"验证通过","REAL","空调机组B1X00-新云平台设定温度值",{"$f":"B670&VLOOKUP(A670,List!$B$3:$D$445,2,FALSE)&D670&\"_\"&VLOOKUP(E670,List!$K$2:$M$447,2,FALSE)","v":"RAHUB1X00_TSET"},"RAHUB1X00_TSET AT%M952.0 :REAL; (*空调机组B1X00-新云平台设定温度值*)","RAHUB1X00_TSET          AT%M952.0      :REAL; (*空调机组B1X00-新云平台设定温度值*)"]
["空调机组","R","M","01X00","设定温度值","956.0",null,"验证通过","REAL","空调机组01X00-新云平台设定温度值",{"$f":"B671&VLOOKUP(A671,List!$B$3:$D$445,2,FALSE)&D671&\"_\"&VLOOKUP(E671,List!$K$2:$M$447,2,FALSE)","v":"RAHU01X00_TSET"},"RAHU01X00_TSET AT%M956.0 :REAL; (*空调机组01X00-新云平台设定温度值*)","RAHU01X00_TSET          AT%M956.0      :REAL; (*空调机组01X00-新云平台设定温度值*)"]
["空调机组","R","M","02X00","设定温度值","960.0",null,"验证通过","REAL","空调机组02X00-新云平台设定温度值",{"$f":"B672&VLOOKUP(A672,List!$B$3:$D$445,2,FALSE)&D672&\"_\"&VLOOKUP(E672,List!$K$2:$M$447,2,FALSE)","v":"RAHU02X00_TSET"},"RAHU02X00_TSET AT%M960.0 :REAL; (*空调机组02X00-新云平台设定温度值*)","RAHU02X00_TSET          AT%M960.0      :REAL; (*空调机组02X00-新云平台设定温度值*)"]
["空调机组","R","M","03X00","设定温度值","964.0",null,"验证通过","REAL","空调机组03X00-新云平台设定温度值",{"$f":"B673&VLOOKUP(A673,List!$B$3:$D$445,2,FALSE)&D673&\"_\"&VLOOKUP(E673,List!$K$2:$M$447,2,FALSE)","v":"RAHU03X00_TSET"},"RAHU03X00_TSET AT%M964.0 :REAL; (*空调机组03X00-新云平台设定温度值*)","RAHU03X00_TSET          AT%M964.0      :REAL; (*空调机组03X00-新云平台设定温度值*)"]
["空调机组","R","M","04X00","设定温度值","968.0",null,"验证通过","REAL","空调机组04X00-新云平台设定温度值",{"$f":"B674&VLOOKUP(A674,List!$B$3:$D$445,2,FALSE)&D674&\"_\"&VLOOKUP(E674,List!$K$2:$M$447,2,FALSE)","v":"RAHU04X00_TSET"},"RAHU04X00_TSET AT%M968.0 :REAL; (*空调机组04X00-新云平台设定温度值*)","RAHU04X00_TSET          AT%M968.0      :REAL; (*空调机组04X00-新云平台设定温度值*)"]
["空调机组","R","M","05X00","设定温度值","972.0",null,"验证通过","REAL","空调机组05X00-新云平台设定温度值",{"$f":"B675&VLOOKUP(A675,List!$B$3:$D$445,2,FALSE)&D675&\"_\"&VLOOKUP(E675,List!$K$2:$M$447,2,FALSE)","v":"RAHU05X00_TSET"},"RAHU05X00_TSET AT%M972.0 :REAL; (*空调机组05X00-新云平台设定温度值*)","RAHU05X00_TSET          AT%M972.0      :REAL; (*空调机组05X00-新云平台设定温度值*)"]
["空调机组","R","M","06X00","设定温度值","976.0",null,"验证通过","REAL","空调机组06X00-新云平台设定温度值",{"$f":"B676&VLOOKUP(A676,List!$B$3:$D$445,2,FALSE)&D676&\"_\"&VLOOKUP(E676,List!$K$2:$M$447,2,FALSE)","v":"RAHU06X00_TSET"},"RAHU06X00_TSET AT%M976.0 :REAL; (*空调机组06X00-新云平台设定温度值*)","RAHU06X00_TSET          AT%M976.0      :REAL; (*空调机组06X00-新云平台设定温度值*)"]
["空调机组","R","M","07X00","设定温度值","980.0",null,{"$f":"IF((IF(OR(I677=\"INT\",I677=\"WORD\",I677=\"BOOL\"),MOD(F677,2),MOD(F677,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"REAL",{"$f":"A677&D677&\"-新云平台\"&E677","v":"空调机组07X00-新云平台设定温度值"},{"$f":"B677&VLOOKUP(A677,List!$B$3:$D$445,2,FALSE)&D677&\"_\"&VLOOKUP(E677,List!$K$2:$M$447,2,FALSE)","v":"RAHU07X00_TSET"},{"$f":"K677&\" \"&\"AT%\"&C677&F677&\" \"&\":\"&I677&\";\"&\" \"&\"(*\"&J677&\"*)\"","v":"RAHU07X00_TSET AT%M980.0 :REAL; (*空调机组07X00-新云平台设定温度值*)"},{"$f":"REPLACE(REPLACE(L677,SEARCH(\"AT%\",L677),,REPT(\" \",25-SEARCH(\"AT%\",L677))),SEARCH(\":\",REPLACE(L677,SEARCH(\"AT%\",L677),,REPT(\" \",25-SEARCH(\"AT%\",L677)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L677,SEARCH(\"AT%\",L677),,REPT(\" \",25-SEARCH(\"AT%\",L677))))))","v":"RAHU07X00_TSET          AT%M980.0      :REAL; (*空调机组07X00-新云平台设定温度值*)"}]
["空调机组","R","M","08X00","设定温度值","984.0",null,"验证通过","REAL","空调机组08X00-新云平台设定温度值",{"$f":"B678&VLOOKUP(A678,List!$B$3:$D$445,2,FALSE)&D678&\"_\"&VLOOKUP(E678,List!$K$2:$M$447,2,FALSE)","v":"RAHU08X00_TSET"},"RAHU08X00_TSET AT%M984.0 :REAL; (*空调机组08X00-新云平台设定温度值*)","RAHU08X00_TSET          AT%M984.0      :REAL; (*空调机组08X00-新云平台设定温度值*)"]
["空调机组","R","M","B3X00","季节模式","988.0",null,"验证通过","INT","空调机组B3X00-新云平台季节模式",{"$f":"B679&VLOOKUP(A679,List!$B$3:$D$445,2,FALSE)&D679&\"_\"&VLOOKUP(E679,List!$K$2:$M$447,2,FALSE)","v":"RAHUB3X00_SM"},"RAHUB3X00_SM AT%M988.0 :INT; (*空调机组B3X00-新云平台季节模式*)","RAHUB3X00_SM            AT%M988.0      :INT; (*空调机组B3X00-新云平台季节模式*)"]
["空调机组","R","M","B2X00","季节模式","990.0",null,"验证通过","INT","空调机组B2X00-新云平台季节模式",{"$f":"B680&VLOOKUP(A680,List!$B$3:$D$445,2,FALSE)&D680&\"_\"&VLOOKUP(E680,List!$K$2:$M$447,2,FALSE)","v":"RAHUB2X00_SM"},"RAHUB2X00_SM AT%M990.0 :INT; (*空调机组B2X00-新云平台季节模式*)","RAHUB2X00_SM            AT%M990.0      :INT; (*空调机组B2X00-新云平台季节模式*)"]
["空调机组","R","M","B1X00","季节模式","992.0",null,"验证通过","INT","空调机组B1X00-新云平台季节模式",{"$f":"B681&VLOOKUP(A681,List!$B$3:$D$445,2,FALSE)&D681&\"_\"&VLOOKUP(E681,List!$K$2:$M$447,2,FALSE)","v":"RAHUB1X00_SM"},"RAHUB1X00_SM AT%M992.0 :INT; (*空调机组B1X00-新云平台季节模式*)","RAHUB1X00_SM            AT%M992.0      :INT; (*空调机组B1X00-新云平台季节模式*)"]
["空调机组","R","M","01X00","季节模式","994.0",null,"验证通过","INT","空调机组01X00-新云平台季节模式",{"$f":"B682&VLOOKUP(A682,List!$B$3:$D$445,2,FALSE)&D682&\"_\"&VLOOKUP(E682,List!$K$2:$M$447,2,FALSE)","v":"RAHU01X00_SM"},"RAHU01X00_SM AT%M994.0 :INT; (*空调机组01X00-新云平台季节模式*)","RAHU01X00_SM            AT%M994.0      :INT; (*空调机组01X00-新云平台季节模式*)"]
["空调机组","R","M","02X00","季节模式","996.0",null,"验证通过","INT","空调机组02X00-新云平台季节模式",{"$f":"B683&VLOOKUP(A683,List!$B$3:$D$445,2,FALSE)&D683&\"_\"&VLOOKUP(E683,List!$K$2:$M$447,2,FALSE)","v":"RAHU02X00_SM"},"RAHU02X00_SM AT%M996.0 :INT; (*空调机组02X00-新云平台季节模式*)","RAHU02X00_SM            AT%M996.0      :INT; (*空调机组02X00-新云平台季节模式*)"]
["空调机组","R","M","03X00","季节模式","998.0",null,"验证通过","INT","空调机组03X00-新云平台季节模式",{"$f":"B684&VLOOKUP(A684,List!$B$3:$D$445,2,FALSE)&D684&\"_\"&VLOOKUP(E684,List!$K$2:$M$447,2,FALSE)","v":"RAHU03X00_SM"},"RAHU03X00_SM AT%M998.0 :INT; (*空调机组03X00-新云平台季节模式*)","RAHU03X00_SM            AT%M998.0      :INT; (*空调机组03X00-新云平台季节模式*)"]
["空调机组","R","M","04X00","季节模式","1000.0",null,"验证通过","INT","空调机组04X00-新云平台季节模式",{"$f":"B685&VLOOKUP(A685,List!$B$3:$D$445,2,FALSE)&D685&\"_\"&VLOOKUP(E685,List!$K$2:$M$447,2,FALSE)","v":"RAHU04X00_SM"},"RAHU04X00_SM AT%M1000.0 :INT; (*空调机组04X00-新云平台季节模式*)","RAHU04X00_SM            AT%M1000.0     :INT; (*空调机组04X00-新云平台季节模式*)"]
["空调机组","R","M","05X00","季节模式","1002.0",null,"验证通过","INT","空调机组05X00-新云平台季节模式",{"$f":"B686&VLOOKUP(A686,List!$B$3:$D$445,2,FALSE)&D686&\"_\"&VLOOKUP(E686,List!$K$2:$M$447,2,FALSE)","v":"RAHU05X00_SM"},"RAHU05X00_SM AT%M1002.0 :INT; (*空调机组05X00-新云平台季节模式*)","RAHU05X00_SM            AT%M1002.0     :INT; (*空调机组05X00-新云平台季节模式*)"]
["空调机组","R","M","06X00","季节模式","1004.0",null,"验证通过","INT","空调机组06X00-新云平台季节模式",{"$f":"B687&VLOOKUP(A687,List!$B$3:$D$445,2,FALSE)&D687&\"_\"&VLOOKUP(E687,List!$K$2:$M$447,2,FALSE)","v":"RAHU06X00_SM"},"RAHU06X00_SM AT%M1004.0 :INT; (*空调机组06X00-新云平台季节模式*)","RAHU06X00_SM            AT%M1004.0     :INT; (*空调机组06X00-新云平台季节模式*)"]
["空调机组","R","M","07X00","季节模式","1006.0",null,{"$f":"IF((IF(OR(I688=\"INT\",I688=\"WORD\",I688=\"BOOL\"),MOD(F688,2),MOD(F688,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"INT",{"$f":"A688&D688&\"-新云平台\"&E688","v":"空调机组07X00-新云平台季节模式"},{"$f":"B688&VLOOKUP(A688,List!$B$3:$D$445,2,FALSE)&D688&\"_\"&VLOOKUP(E688,List!$K$2:$M$447,2,FALSE)","v":"RAHU07X00_SM"},{"$f":"K688&\" \"&\"AT%\"&C688&F688&\" \"&\":\"&I688&\";\"&\" \"&\"(*\"&J688&\"*)\"","v":"RAHU07X00_SM AT%M1006.0 :INT; (*空调机组07X00-新云平台季节模式*)"},{"$f":"REPLACE(REPLACE(L688,SEARCH(\"AT%\",L688),,REPT(\" \",25-SEARCH(\"AT%\",L688))),SEARCH(\":\",REPLACE(L688,SEARCH(\"AT%\",L688),,REPT(\" \",25-SEARCH(\"AT%\",L688)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L688,SEARCH(\"AT%\",L688),,REPT(\" \",25-SEARCH(\"AT%\",L688))))))","v":"RAHU07X00_SM            AT%M1006.0     :INT; (*空调机组07X00-新云平台季节模式*)"}]
["空调机组","R","M","08X00","季节模式","1008.0",null,"验证通过","INT","空调机组08X00-新云平台季节模式",{"$f":"B689&VLOOKUP(A689,List!$B$3:$D$445,2,FALSE)&D689&\"_\"&VLOOKUP(E689,List!$K$2:$M$447,2,FALSE)","v":"RAHU08X00_SM"},"RAHU08X00_SM AT%M1008.0 :INT; (*空调机组08X00-新云平台季节模式*)","RAHU08X00_SM            AT%M1008.0     :INT; (*空调机组08X00-新云平台季节模式*)"]
["空调机组","R","M","B3X00","启停控制","1010.0",null,"验证通过","BOOL","空调机组B3X00-新云平台启停控制",{"$f":"B690&VLOOKUP(A690,List!$B$3:$D$445,2,FALSE)&D690&\"_\"&VLOOKUP(E690,List!$K$2:$M$447,2,FALSE)","v":"RAHUB3X00_C"},{"$f":"K690&\" \"&\"AT%\"&C690&F690&\" \"&\":\"&I690&\";\"&\" \"&\"(*\"&J690&\"*)\"","v":"RAHUB3X00_C AT%M1010.0 :BOOL; (*空调机组B3X00-新云平台启停控制*)"},{"$f":"REPLACE(REPLACE(L690,SEARCH(\"AT%\",L690),,REPT(\" \",25-SEARCH(\"AT%\",L690))),SEARCH(\":\",REPLACE(L690,SEARCH(\"AT%\",L690),,REPT(\" \",25-SEARCH(\"AT%\",L690)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L690,SEARCH(\"AT%\",L690),,REPT(\" \",25-SEARCH(\"AT%\",L690))))))","v":"RAHUB3X00_C             AT%M1010.0     :BOOL; (*空调机组B3X00-新云平台启停控制*)"}]
["空调机组","R","M","B2X00","启停控制","1012.0",null,"验证通过","BOOL","空调机组B2X00-新云平台启停控制",{"$f":"B691&VLOOKUP(A691,List!$B$3:$D$445,2,FALSE)&D691&\"_\"&VLOOKUP(E691,List!$K$2:$M$447,2,FALSE)","v":"RAHUB2X00_C"},"RAHUB2X00_C AT%M1012.0 :BOOL; (*空调机组B2X00-新云平台启停控制*)","RAHUB2X00_C             AT%M1012.0     :BOOL; (*空调机组B2X00-新云平台启停控制*)"]
["空调机组","R","M","B1X00","启停控制","1014.0",null,"验证通过","BOOL","空调机组B1X00-新云平台启停控制",{"$f":"B692&VLOOKUP(A692,List!$B$3:$D$445,2,FALSE)&D692&\"_\"&VLOOKUP(E692,List!$K$2:$M$447,2,FALSE)","v":"RAHUB1X00_C"},"RAHUB1X00_C AT%M1014.0 :BOOL; (*空调机组B1X00-新云平台启停控制*)","RAHUB1X00_C             AT%M1014.0     :BOOL; (*空调机组B1X00-新云平台启停控制*)"]
["空调机组","R","M","01X00","启停控制","1016.0",null,"验证通过","BOOL","空调机组01X00-新云平台启停控制",{"$f":"B693&VLOOKUP(A693,List!$B$3:$D$445,2,FALSE)&D693&\"_\"&VLOOKUP(E693,List!$K$2:$M$447,2,FALSE)","v":"RAHU01X00_C"},"RAHU01X00_C AT%M1016.0 :BOOL; (*空调机组01X00-新云平台启停控制*)","RAHU01X00_C             AT%M1016.0     :BOOL; (*空调机组01X00-新云平台启停控制*)"]
["空调机组","R","M","02X00","启停控制","1018.0",null,"验证通过","BOOL","空调机组02X00-新云平台启停控制",{"$f":"B694&VLOOKUP(A694,List!$B$3:$D$445,2,FALSE)&D694&\"_\"&VLOOKUP(E694,List!$K$2:$M$447,2,FALSE)","v":"RAHU02X00_C"},"RAHU02X00_C AT%M1018.0 :BOOL; (*空调机组02X00-新云平台启停控制*)","RAHU02X00_C             AT%M1018.0     :BOOL; (*空调机组02X00-新云平台启停控制*)"]
["空调机组","R","M","03X00","启停控制","1020.0",null,"验证通过","BOOL","空调机组03X00-新云平台启停控制",{"$f":"B695&VLOOKUP(A695,List!$B$3:$D$445,2,FALSE)&D695&\"_\"&VLOOKUP(E695,List!$K$2:$M$447,2,FALSE)","v":"RAHU03X00_C"},"RAHU03X00_C AT%M1020.0 :BOOL; (*空调机组03X00-新云平台启停控制*)","RAHU03X00_C             AT%M1020.0     :BOOL; (*空调机组03X00-新云平台启停控制*)"]
["空调机组","R","M","04X00","启停控制","1022.0",null,"验证通过","BOOL","空调机组04X00-新云平台启停控制",{"$f":"B696&VLOOKUP(A696,List!$B$3:$D$445,2,FALSE)&D696&\"_\"&VLOOKUP(E696,List!$K$2:$M$447,2,FALSE)","v":"RAHU04X00_C"},"RAHU04X00_C AT%M1022.0 :BOOL; (*空调机组04X00-新云平台启停控制*)","RAHU04X00_C             AT%M1022.0     :BOOL; (*空调机组04X00-新云平台启停控制*)"]
["空调机组","R","M","05X00","启停控制","1024.0",null,"验证通过","BOOL","空调机组05X00-新云平台启停控制",{"$f":"B697&VLOOKUP(A697,List!$B$3:$D$445,2,FALSE)&D697&\"_\"&VLOOKUP(E697,List!$K$2:$M$447,2,FALSE)","v":"RAHU05X00_C"},"RAHU05X00_C AT%M1024.0 :BOOL; (*空调机组05X00-新云平台启停控制*)","RAHU05X00_C             AT%M1024.0     :BOOL; (*空调机组05X00-新云平台启停控制*)"]
["空调机组","R","M","06X00","启停控制","1026.0",null,"验证通过","BOOL","空调机组06X00-新云平台启停控制",{"$f":"B698&VLOOKUP(A698,List!$B$3:$D$445,2,FALSE)&D698&\"_\"&VLOOKUP(E698,List!$K$2:$M$447,2,FALSE)","v":"RAHU06X00_C"},"RAHU06X00_C AT%M1026.0 :BOOL; (*空调机组06X00-新云平台启停控制*)","RAHU06X00_C             AT%M1026.0     :BOOL; (*空调机组06X00-新云平台启停控制*)"]
["空调机组","R","M","07X00","启停控制","1028.0",null,{"$f":"IF((IF(OR(I699=\"INT\",I699=\"WORD\",I699=\"BOOL\"),MOD(F699,2),MOD(F699,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A699&D699&\"-新云平台\"&E699","v":"空调机组07X00-新云平台启停控制"},{"$f":"B699&VLOOKUP(A699,List!$B$3:$D$445,2,FALSE)&D699&\"_\"&VLOOKUP(E699,List!$K$2:$M$447,2,FALSE)","v":"RAHU07X00_C"},{"$f":"K699&\" \"&\"AT%\"&C699&F699&\" \"&\":\"&I699&\";\"&\" \"&\"(*\"&J699&\"*)\"","v":"RAHU07X00_C AT%M1028.0 :BOOL; (*空调机组07X00-新云平台启停控制*)"},{"$f":"REPLACE(REPLACE(L699,SEARCH(\"AT%\",L699),,REPT(\" \",25-SEARCH(\"AT%\",L699))),SEARCH(\":\",REPLACE(L699,SEARCH(\"AT%\",L699),,REPT(\" \",25-SEARCH(\"AT%\",L699)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L699,SEARCH(\"AT%\",L699),,REPT(\" \",25-SEARCH(\"AT%\",L699))))))","v":"RAHU07X00_C             AT%M1028.0     :BOOL; (*空调机组07X00-新云平台启停控制*)"}]
["空调机组","R","M","08X00","启停控制","1030.0",null,"验证通过","BOOL","空调机组08X00-新云平台启停控制",{"$f":"B700&VLOOKUP(A700,List!$B$3:$D$445,2,FALSE)&D700&\"_\"&VLOOKUP(E700,List!$K$2:$M$447,2,FALSE)","v":"RAHU08X00_C"},"RAHU08X00_C AT%M1030.0 :BOOL; (*空调机组08X00-新云平台启停控制*)","RAHU08X00_C             AT%M1030.0     :BOOL; (*空调机组08X00-新云平台启停控制*)"]
["风机盘管","L","M","B3X00","设定温度值","1036.0",null,{"$f":"IF((IF(OR(I701=\"INT\",I701=\"WORD\",I701=\"BOOL\"),MOD(F701,2),MOD(F701,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"REAL",{"$f":"A701&D701&\"-\"&E701","v":"风机盘管B3X00-设定温度值"},{"$f":"B701&VLOOKUP(A701,List!$B$3:$D$445,2,FALSE)&D701&\"_\"&VLOOKUP(E701,List!$K$2:$M$447,2,FALSE)","v":"LFCUB3X00_TSET"},{"$f":"K701&\" \"&\"AT%\"&C701&F701&\" \"&\":\"&I701&\";\"&\" \"&\"(*\"&J701&\"*)\"","v":"LFCUB3X00_TSET AT%M1036.0 :REAL; (*风机盘管B3X00-设定温度值*)"},{"$f":"REPLACE(REPLACE(L701,SEARCH(\"AT%\",L701),,REPT(\" \",25-SEARCH(\"AT%\",L701))),SEARCH(\":\",REPLACE(L701,SEARCH(\"AT%\",L701),,REPT(\" \",25-SEARCH(\"AT%\",L701)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L701,SEARCH(\"AT%\",L701),,REPT(\" \",25-SEARCH(\"AT%\",L701))))))","v":"LFCUB3X00_TSET          AT%M1036.0     :REAL; (*风机盘管B3X00-设定温度值*)"}]
["风机盘管","L","M","B2X00","设定温度值","1040.0",null,"验证通过","REAL",{"$f":"A702&D702&\"-\"&E702","v":"风机盘管B2X00-设定温度值"},{"$f":"B702&VLOOKUP(A702,List!$B$3:$D$445,2,FALSE)&D702&\"_\"&VLOOKUP(E702,List!$K$2:$M$447,2,FALSE)","v":"LFCUB2X00_TSET"},"LFCUB2X00_TSET AT%M1040.0 :REAL; (*风机盘管B2X00-设定温度值*)","LFCUB2X00_TSET          AT%M1040.0     :REAL; (*风机盘管B2X00-设定温度值*)"]
["风机盘管","L","M","B1X00","设定温度值","1044.0",null,"验证通过","REAL","风机盘管B1X00-设定温度值",{"$f":"B703&VLOOKUP(A703,List!$B$3:$D$445,2,FALSE)&D703&\"_\"&VLOOKUP(E703,List!$K$2:$M$447,2,FALSE)","v":"LFCUB1X00_TSET"},"LFCUB1X00_TSET AT%M1044.0 :REAL; (*风机盘管B1X00-设定温度值*)","LFCUB1X00_TSET          AT%M1044.0     :REAL; (*风机盘管B1X00-设定温度值*)"]
["风机盘管","L","M","01X00","设定温度值","1048.0",null,"验证通过","REAL","风机盘管01X00-设定温度值",{"$f":"B704&VLOOKUP(A704,List!$B$3:$D$445,2,FALSE)&D704&\"_\"&VLOOKUP(E704,List!$K$2:$M$447,2,FALSE)","v":"LFCU01X00_TSET"},"LFCU01X00_TSET AT%M1048.0 :REAL; (*风机盘管01X00-设定温度值*)","LFCU01X00_TSET          AT%M1048.0     :REAL; (*风机盘管01X00-设定温度值*)"]
["风机盘管","L","M","02X00","设定温度值","1052.0",null,"验证通过","REAL","风机盘管02X00-设定温度值",{"$f":"B705&VLOOKUP(A705,List!$B$3:$D$445,2,FALSE)&D705&\"_\"&VLOOKUP(E705,List!$K$2:$M$447,2,FALSE)","v":"LFCU02X00_TSET"},"LFCU02X00_TSET AT%M1052.0 :REAL; (*风机盘管02X00-设定温度值*)","LFCU02X00_TSET          AT%M1052.0     :REAL; (*风机盘管02X00-设定温度值*)"]
["风机盘管","L","M","03X00","设定温度值","1056.0",null,"验证通过","REAL","风机盘管03X00-设定温度值",{"$f":"B706&VLOOKUP(A706,List!$B$3:$D$445,2,FALSE)&D706&\"_\"&VLOOKUP(E706,List!$K$2:$M$447,2,FALSE)","v":"LFCU03X00_TSET"},"LFCU03X00_TSET AT%M1056.0 :REAL; (*风机盘管03X00-设定温度值*)","LFCU03X00_TSET          AT%M1056.0     :REAL; (*风机盘管03X00-设定温度值*)"]
["风机盘管","L","M","04X00","设定温度值","1060.0",null,"验证通过","REAL","风机盘管04X00-设定温度值",{"$f":"B707&VLOOKUP(A707,List!$B$3:$D$445,2,FALSE)&D707&\"_\"&VLOOKUP(E707,List!$K$2:$M$447,2,FALSE)","v":"LFCU04X00_TSET"},"LFCU04X00_TSET AT%M1060.0 :REAL; (*风机盘管04X00-设定温度值*)","LFCU04X00_TSET          AT%M1060.0     :REAL; (*风机盘管04X00-设定温度值*)"]
["风机盘管","L","M","05X00","设定温度值","1064.0",null,"验证通过","REAL","风机盘管05X00-设定温度值",{"$f":"B708&VLOOKUP(A708,List!$B$3:$D$445,2,FALSE)&D708&\"_\"&VLOOKUP(E708,List!$K$2:$M$447,2,FALSE)","v":"LFCU05X00_TSET"},"LFCU05X00_TSET AT%M1064.0 :REAL; (*风机盘管05X00-设定温度值*)","LFCU05X00_TSET          AT%M1064.0     :REAL; (*风机盘管05X00-设定温度值*)"]
["风机盘管","L","M","06X00","设定温度值","1068.0",null,"验证通过","REAL","风机盘管06X00-设定温度值",{"$f":"B709&VLOOKUP(A709,List!$B$3:$D$445,2,FALSE)&D709&\"_\"&VLOOKUP(E709,List!$K$2:$M$447,2,FALSE)","v":"LFCU06X00_TSET"},"LFCU06X00_TSET AT%M1068.0 :REAL; (*风机盘管06X00-设定温度值*)","LFCU06X00_TSET          AT%M1068.0     :REAL; (*风机盘管06X00-设定温度值*)"]
["风机盘管","L","M","07X00","设定温度值","1072.0",null,{"$f":"IF((IF(OR(I710=\"INT\",I710=\"WORD\",I710=\"BOOL\"),MOD(F710,2),MOD(F710,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"REAL",{"$f":"A710&D710&\"-\"&E710","v":"风机盘管07X00-设定温度值"},{"$f":"B710&VLOOKUP(A710,List!$B$3:$D$445,2,FALSE)&D710&\"_\"&VLOOKUP(E710,List!$K$2:$M$447,2,FALSE)","v":"LFCU07X00_TSET"},{"$f":"K710&\" \"&\"AT%\"&C710&F710&\" \"&\":\"&I710&\";\"&\" \"&\"(*\"&J710&\"*)\"","v":"LFCU07X00_TSET AT%M1072.0 :REAL; (*风机盘管07X00-设定温度值*)"},{"$f":"REPLACE(REPLACE(L710,SEARCH(\"AT%\",L710),,REPT(\" \",25-SEARCH(\"AT%\",L710))),SEARCH(\":\",REPLACE(L710,SEARCH(\"AT%\",L710),,REPT(\" \",25-SEARCH(\"AT%\",L710)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L710,SEARCH(\"AT%\",L710),,REPT(\" \",25-SEARCH(\"AT%\",L710))))))","v":"LFCU07X00_TSET          AT%M1072.0     :REAL; (*风机盘管07X00-设定温度值*)"}]
["风机盘管","L","M","08X00","设定温度值","1076.0",null,"验证通过","REAL","风机盘管08X00-设定温度值",{"$f":"B711&VLOOKUP(A711,List!$B$3:$D$445,2,FALSE)&D711&\"_\"&VLOOKUP(E711,List!$K$2:$M$447,2,FALSE)","v":"LFCU08X00_TSET"},"LFCU08X00_TSET AT%M1076.0 :REAL; (*风机盘管08X00-设定温度值*)","LFCU08X00_TSET          AT%M1076.0     :REAL; (*风机盘管08X00-设定温度值*)"]
["风机盘管","L","M","B3X00","季节模式","1080.0",null,"验证通过","INT","风机盘管B3X00-季节模式",{"$f":"B712&VLOOKUP(A712,List!$B$3:$D$445,2,FALSE)&D712&\"_\"&VLOOKUP(E712,List!$K$2:$M$447,2,FALSE)","v":"LFCUB3X00_SM"},"LFCUB3X00_SM AT%M1080.0 :INT; (*风机盘管B3X00-季节模式*)","LFCUB3X00_SM            AT%M1080.0     :INT; (*风机盘管B3X00-季节模式*)"]
["风机盘管","L","M","B2X00","季节模式","1082.0",null,"验证通过","INT","风机盘管B2X00-季节模式",{"$f":"B713&VLOOKUP(A713,List!$B$3:$D$445,2,FALSE)&D713&\"_\"&VLOOKUP(E713,List!$K$2:$M$447,2,FALSE)","v":"LFCUB2X00_SM"},"LFCUB2X00_SM AT%M1082.0 :INT; (*风机盘管B2X00-季节模式*)","LFCUB2X00_SM            AT%M1082.0     :INT; (*风机盘管B2X00-季节模式*)"]
["风机盘管","L","M","B1X00","季节模式","1084.0",null,"验证通过","INT","风机盘管B1X00-季节模式",{"$f":"B714&VLOOKUP(A714,List!$B$3:$D$445,2,FALSE)&D714&\"_\"&VLOOKUP(E714,List!$K$2:$M$447,2,FALSE)","v":"LFCUB1X00_SM"},"LFCUB1X00_SM AT%M1084.0 :INT; (*风机盘管B1X00-季节模式*)","LFCUB1X00_SM            AT%M1084.0     :INT; (*风机盘管B1X00-季节模式*)"]
["风机盘管","L","M","01X00","季节模式","1086.0",null,"验证通过","INT","风机盘管01X00-季节模式",{"$f":"B715&VLOOKUP(A715,List!$B$3:$D$445,2,FALSE)&D715&\"_\"&VLOOKUP(E715,List!$K$2:$M$447,2,FALSE)","v":"LFCU01X00_SM"},"LFCU01X00_SM AT%M1086.0 :INT; (*风机盘管01X00-季节模式*)","LFCU01X00_SM            AT%M1086.0     :INT; (*风机盘管01X00-季节模式*)"]
["风机盘管","L","M","02X00","季节模式","1088.0",null,"验证通过","INT","风机盘管02X00-季节模式",{"$f":"B716&VLOOKUP(A716,List!$B$3:$D$445,2,FALSE)&D716&\"_\"&VLOOKUP(E716,List!$K$2:$M$447,2,FALSE)","v":"LFCU02X00_SM"},"LFCU02X00_SM AT%M1088.0 :INT; (*风机盘管02X00-季节模式*)","LFCU02X00_SM            AT%M1088.0     :INT; (*风机盘管02X00-季节模式*)"]
["风机盘管","L","M","03X00","季节模式","1090.0",null,"验证通过","INT","风机盘管03X00-季节模式",{"$f":"B717&VLOOKUP(A717,List!$B$3:$D$445,2,FALSE)&D717&\"_\"&VLOOKUP(E717,List!$K$2:$M$447,2,FALSE)","v":"LFCU03X00_SM"},"LFCU03X00_SM AT%M1090.0 :INT; (*风机盘管03X00-季节模式*)","LFCU03X00_SM            AT%M1090.0     :INT; (*风机盘管03X00-季节模式*)"]
["风机盘管","L","M","04X00","季节模式","1092.0",null,"验证通过","INT","风机盘管04X00-季节模式",{"$f":"B718&VLOOKUP(A718,List!$B$3:$D$445,2,FALSE)&D718&\"_\"&VLOOKUP(E718,List!$K$2:$M$447,2,FALSE)","v":"LFCU04X00_SM"},"LFCU04X00_SM AT%M1092.0 :INT; (*风机盘管04X00-季节模式*)","LFCU04X00_SM            AT%M1092.0     :INT; (*风机盘管04X00-季节模式*)"]
["风机盘管","L","M","05X00","季节模式","1094.0",null,"验证通过","INT","风机盘管05X00-季节模式",{"$f":"B719&VLOOKUP(A719,List!$B$3:$D$445,2,FALSE)&D719&\"_\"&VLOOKUP(E719,List!$K$2:$M$447,2,FALSE)","v":"LFCU05X00_SM"},"LFCU05X00_SM AT%M1094.0 :INT; (*风机盘管05X00-季节模式*)","LFCU05X00_SM            AT%M1094.0     :INT; (*风机盘管05X00-季节模式*)"]
["风机盘管","L","M","06X00","季节模式","1096.0",null,"验证通过","INT","风机盘管06X00-季节模式",{"$f":"B720&VLOOKUP(A720,List!$B$3:$D$445,2,FALSE)&D720&\"_\"&VLOOKUP(E720,List!$K$2:$M$447,2,FALSE)","v":"LFCU06X00_SM"},"LFCU06X00_SM AT%M1096.0 :INT; (*风机盘管06X00-季节模式*)","LFCU06X00_SM            AT%M1096.0     :INT; (*风机盘管06X00-季节模式*)"]
["风机盘管","L","M","07X00","季节模式","1098.0",null,{"$f":"IF((IF(OR(I721=\"INT\",I721=\"WORD\",I721=\"BOOL\"),MOD(F721,2),MOD(F721,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"INT",{"$f":"A721&D721&\"-\"&E721","v":"风机盘管07X00-季节模式"},{"$f":"B721&VLOOKUP(A721,List!$B$3:$D$445,2,FALSE)&D721&\"_\"&VLOOKUP(E721,List!$K$2:$M$447,2,FALSE)","v":"LFCU07X00_SM"},{"$f":"K721&\" \"&\"AT%\"&C721&F721&\" \"&\":\"&I721&\";\"&\" \"&\"(*\"&J721&\"*)\"","v":"LFCU07X00_SM AT%M1098.0 :INT; (*风机盘管07X00-季节模式*)"},{"$f":"REPLACE(REPLACE(L721,SEARCH(\"AT%\",L721),,REPT(\" \",25-SEARCH(\"AT%\",L721))),SEARCH(\":\",REPLACE(L721,SEARCH(\"AT%\",L721),,REPT(\" \",25-SEARCH(\"AT%\",L721)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L721,SEARCH(\"AT%\",L721),,REPT(\" \",25-SEARCH(\"AT%\",L721))))))","v":"LFCU07X00_SM            AT%M1098.0     :INT; (*风机盘管07X00-季节模式*)"}]
["风机盘管","L","M","08X00","季节模式","1100.0",null,"验证通过","INT","风机盘管08X00-季节模式",{"$f":"B722&VLOOKUP(A722,List!$B$3:$D$445,2,FALSE)&D722&\"_\"&VLOOKUP(E722,List!$K$2:$M$447,2,FALSE)","v":"LFCU08X00_SM"},"LFCU08X00_SM AT%M1100.0 :INT; (*风机盘管08X00-季节模式*)","LFCU08X00_SM            AT%M1100.0     :INT; (*风机盘管08X00-季节模式*)"]
["风机盘管","L","M","B3X00","启停控制","1102.0",null,"验证通过","BOOL","风机盘管B3X00-启停控制",{"$f":"B723&VLOOKUP(A723,List!$B$3:$D$445,2,FALSE)&D723&\"_\"&VLOOKUP(E723,List!$K$2:$M$447,2,FALSE)","v":"LFCUB3X00_C"},{"$f":"K723&\" \"&\"AT%\"&C723&F723&\" \"&\":\"&I723&\";\"&\" \"&\"(*\"&J723&\"*)\"","v":"LFCUB3X00_C AT%M1102.0 :BOOL; (*风机盘管B3X00-启停控制*)"},{"$f":"REPLACE(REPLACE(L723,SEARCH(\"AT%\",L723),,REPT(\" \",25-SEARCH(\"AT%\",L723))),SEARCH(\":\",REPLACE(L723,SEARCH(\"AT%\",L723),,REPT(\" \",25-SEARCH(\"AT%\",L723)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L723,SEARCH(\"AT%\",L723),,REPT(\" \",25-SEARCH(\"AT%\",L723))))))","v":"LFCUB3X00_C             AT%M1102.0     :BOOL; (*风机盘管B3X00-启停控制*)"}]
["风机盘管","L","M","B2X00","启停控制",{"$f":"IF(OR(I723=\"REAL\",I723=\"DWORD\",I723=\"DINT\"),(IF(OR(I724=\"REAL\",I724=\"DWORD\",I724=\"DINT\"),F723+4+MOD(F723,4),F723+4)),(IF(OR(I724=\"REAL\",I724=\"DWORD\",I724=\"DINT\"),F723+4+MOD(F723,4),F723+2)))&\".0\"","v":"1104.0"},null,"验证通过","BOOL","风机盘管B2X00-启停控制",{"$f":"B724&VLOOKUP(A724,List!$B$3:$D$445,2,FALSE)&D724&\"_\"&VLOOKUP(E724,List!$K$2:$M$447,2,FALSE)","v":"LFCUB2X00_C"},"LFCUB2X00_C AT%M1104.0 :BOOL; (*风机盘管B2X00-启停控制*)","LFCUB2X00_C             AT%M1104.0     :BOOL; (*风机盘管B2X00-启停控制*)"]
["风机盘管","L","M","B1X00","启停控制","1106.0",null,"验证通过","BOOL","风机盘管B1X00-启停控制",{"$f":"B725&VLOOKUP(A725,List!$B$3:$D$445,2,FALSE)&D725&\"_\"&VLOOKUP(E725,List!$K$2:$M$447,2,FALSE)","v":"LFCUB1X00_C"},"LFCUB1X00_C AT%M1106.0 :BOOL; (*风机盘管B1X00-启停控制*)","LFCUB1X00_C             AT%M1106.0     :BOOL; (*风机盘管B1X00-启停控制*)"]
["风机盘管","L","M","01X00","启停控制","1108.0",null,"验证通过","BOOL","风机盘管01X00-启停控制",{"$f":"B726&VLOOKUP(A726,List!$B$3:$D$445,2,FALSE)&D726&\"_\"&VLOOKUP(E726,List!$K$2:$M$447,2,FALSE)","v":"LFCU01X00_C"},"LFCU01X00_C AT%M1108.0 :BOOL; (*风机盘管01X00-启停控制*)","LFCU01X00_C             AT%M1108.0     :BOOL; (*风机盘管01X00-启停控制*)"]
["风机盘管","L","M","02X00","启停控制","1110.0",null,{"$f":"IF((IF(OR(I727=\"INT\",I727=\"WORD\",I727=\"BOOL\"),MOD(F727,2),MOD(F727,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","风机盘管02X00-启停控制",{"$f":"B727&VLOOKUP(A727,List!$B$3:$D$445,2,FALSE)&D727&\"_\"&VLOOKUP(E727,List!$K$2:$M$447,2,FALSE)","v":"LFCU02X00_C"},"LFCU02X00_C AT%M1110.0 :BOOL; (*风机盘管02X00-启停控制*)","LFCU02X00_C             AT%M1110.0     :BOOL; (*风机盘管02X00-启停控制*)"]
["风机盘管","L","M","03X00","启停控制","1112.0",null,"验证通过","BOOL","风机盘管03X00-启停控制",{"$f":"B728&VLOOKUP(A728,List!$B$3:$D$445,2,FALSE)&D728&\"_\"&VLOOKUP(E728,List!$K$2:$M$447,2,FALSE)","v":"LFCU03X00_C"},"LFCU03X00_C AT%M1112.0 :BOOL; (*风机盘管03X00-启停控制*)","LFCU03X00_C             AT%M1112.0     :BOOL; (*风机盘管03X00-启停控制*)"]
["风机盘管","L","M","04X00","启停控制","1114.0",null,"验证通过","BOOL","风机盘管04X00-启停控制",{"$f":"B729&VLOOKUP(A729,List!$B$3:$D$445,2,FALSE)&D729&\"_\"&VLOOKUP(E729,List!$K$2:$M$447,2,FALSE)","v":"LFCU04X00_C"},"LFCU04X00_C AT%M1114.0 :BOOL; (*风机盘管04X00-启停控制*)","LFCU04X00_C             AT%M1114.0     :BOOL; (*风机盘管04X00-启停控制*)"]
["风机盘管","L","M","05X00","启停控制","1116.0",null,"验证通过","BOOL","风机盘管05X00-启停控制",{"$f":"B730&VLOOKUP(A730,List!$B$3:$D$445,2,FALSE)&D730&\"_\"&VLOOKUP(E730,List!$K$2:$M$447,2,FALSE)","v":"LFCU05X00_C"},"LFCU05X00_C AT%M1116.0 :BOOL; (*风机盘管05X00-启停控制*)","LFCU05X00_C             AT%M1116.0     :BOOL; (*风机盘管05X00-启停控制*)"]
["风机盘管","L","M","06X00","启停控制","1118.0",null,"验证通过","BOOL","风机盘管06X00-启停控制",{"$f":"B731&VLOOKUP(A731,List!$B$3:$D$445,2,FALSE)&D731&\"_\"&VLOOKUP(E731,List!$K$2:$M$447,2,FALSE)","v":"LFCU06X00_C"},"LFCU06X00_C AT%M1118.0 :BOOL; (*风机盘管06X00-启停控制*)","LFCU06X00_C             AT%M1118.0     :BOOL; (*风机盘管06X00-启停控制*)"]
["风机盘管","L","M","07X00","启停控制","1120.0",null,{"$f":"IF((IF(OR(I732=\"INT\",I732=\"WORD\",I732=\"BOOL\"),MOD(F732,2),MOD(F732,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A732&D732&\"-\"&E732","v":"风机盘管07X00-启停控制"},{"$f":"B732&VLOOKUP(A732,List!$B$3:$D$445,2,FALSE)&D732&\"_\"&VLOOKUP(E732,List!$K$2:$M$447,2,FALSE)","v":"LFCU07X00_C"},{"$f":"K732&\" \"&\"AT%\"&C732&F732&\" \"&\":\"&I732&\";\"&\" \"&\"(*\"&J732&\"*)\"","v":"LFCU07X00_C AT%M1120.0 :BOOL; (*风机盘管07X00-启停控制*)"},{"$f":"REPLACE(REPLACE(L732,SEARCH(\"AT%\",L732),,REPT(\" \",25-SEARCH(\"AT%\",L732))),SEARCH(\":\",REPLACE(L732,SEARCH(\"AT%\",L732),,REPT(\" \",25-SEARCH(\"AT%\",L732)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L732,SEARCH(\"AT%\",L732),,REPT(\" \",25-SEARCH(\"AT%\",L732))))))","v":"LFCU07X00_C             AT%M1120.0     :BOOL; (*风机盘管07X00-启停控制*)"}]
["风机盘管","L","M","08X00","启停控制","1122.0",null,"验证通过","BOOL","风机盘管08X00-启停控制",{"$f":"B733&VLOOKUP(A733,List!$B$3:$D$445,2,FALSE)&D733&\"_\"&VLOOKUP(E733,List!$K$2:$M$447,2,FALSE)","v":"LFCU08X00_C"},"LFCU08X00_C AT%M1122.0 :BOOL; (*风机盘管08X00-启停控制*)","LFCU08X00_C             AT%M1122.0     :BOOL; (*风机盘管08X00-启停控制*)"]
["风机盘管","L","M","B3X00","定时控制","1124.0",null,"验证通过","BOOL",{"$f":"A734&D734&\"-\"&E734","v":"风机盘管B3X00-定时控制"},{"$f":"B734&VLOOKUP(A734,List!$B$3:$D$445,2,FALSE)&D734&\"_\"&VLOOKUP(E734,List!$K$2:$M$447,2,FALSE)","v":"LFCUB3X00_TC"},"LFCUB3X00_TC AT%M1124.0 :BOOL; (*风机盘管B3X00-定时控制*)","LFCUB3X00_TC            AT%M1124.0     :BOOL; (*风机盘管B3X00-定时控制*)"]
["风机盘管","L","M","B2X00","定时控制","1126.0",null,"验证通过","BOOL","风机盘管B2X00-定时控制",{"$f":"B735&VLOOKUP(A735,List!$B$3:$D$445,2,FALSE)&D735&\"_\"&VLOOKUP(E735,List!$K$2:$M$447,2,FALSE)","v":"LFCUB2X00_TC"},"LFCUB2X00_TC AT%M1126.0 :BOOL; (*风机盘管B2X00-定时控制*)","LFCUB2X00_TC            AT%M1126.0     :BOOL; (*风机盘管B2X00-定时控制*)"]
["风机盘管","L","M","B1X00","定时控制","1128.0",null,"验证通过","BOOL","风机盘管B1X00-定时控制",{"$f":"B736&VLOOKUP(A736,List!$B$3:$D$445,2,FALSE)&D736&\"_\"&VLOOKUP(E736,List!$K$2:$M$447,2,FALSE)","v":"LFCUB1X00_TC"},"LFCUB1X00_TC AT%M1128.0 :BOOL; (*风机盘管B1X00-定时控制*)","LFCUB1X00_TC            AT%M1128.0     :BOOL; (*风机盘管B1X00-定时控制*)"]
["风机盘管","L","M","01X00","定时控制","1130.0",null,"验证通过","BOOL","风机盘管01X00-定时控制",{"$f":"B737&VLOOKUP(A737,List!$B$3:$D$445,2,FALSE)&D737&\"_\"&VLOOKUP(E737,List!$K$2:$M$447,2,FALSE)","v":"LFCU01X00_TC"},"LFCU01X00_TC AT%M1130.0 :BOOL; (*风机盘管01X00-定时控制*)","LFCU01X00_TC            AT%M1130.0     :BOOL; (*风机盘管01X00-定时控制*)"]
["风机盘管","L","M","02X00","定时控制","1132.0",null,{"$f":"IF((IF(OR(I738=\"INT\",I738=\"WORD\",I738=\"BOOL\"),MOD(F738,2),MOD(F738,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","风机盘管02X00-定时控制",{"$f":"B738&VLOOKUP(A738,List!$B$3:$D$445,2,FALSE)&D738&\"_\"&VLOOKUP(E738,List!$K$2:$M$447,2,FALSE)","v":"LFCU02X00_TC"},"LFCU02X00_TC AT%M1132.0 :BOOL; (*风机盘管02X00-定时控制*)","LFCU02X00_TC            AT%M1132.0     :BOOL; (*风机盘管02X00-定时控制*)"]
["风机盘管","L","M","03X00","定时控制","1134.0",null,"验证通过","BOOL","风机盘管03X00-定时控制",{"$f":"B739&VLOOKUP(A739,List!$B$3:$D$445,2,FALSE)&D739&\"_\"&VLOOKUP(E739,List!$K$2:$M$447,2,FALSE)","v":"LFCU03X00_TC"},"LFCU03X00_TC AT%M1134.0 :BOOL; (*风机盘管03X00-定时控制*)","LFCU03X00_TC            AT%M1134.0     :BOOL; (*风机盘管03X00-定时控制*)"]
["风机盘管","L","M","04X00","定时控制","1136.0",null,"验证通过","BOOL","风机盘管04X00-定时控制",{"$f":"B740&VLOOKUP(A740,List!$B$3:$D$445,2,FALSE)&D740&\"_\"&VLOOKUP(E740,List!$K$2:$M$447,2,FALSE)","v":"LFCU04X00_TC"},"LFCU04X00_TC AT%M1136.0 :BOOL; (*风机盘管04X00-定时控制*)","LFCU04X00_TC            AT%M1136.0     :BOOL; (*风机盘管04X00-定时控制*)"]
["风机盘管","L","M","05X00","定时控制","1138.0",null,"验证通过","BOOL","风机盘管05X00-定时控制",{"$f":"B741&VLOOKUP(A741,List!$B$3:$D$445,2,FALSE)&D741&\"_\"&VLOOKUP(E741,List!$K$2:$M$447,2,FALSE)","v":"LFCU05X00_TC"},"LFCU05X00_TC AT%M1138.0 :BOOL; (*风机盘管05X00-定时控制*)","LFCU05X00_TC            AT%M1138.0     :BOOL; (*风机盘管05X00-定时控制*)"]
["风机盘管","L","M","06X00","定时控制","1140.0",null,"验证通过","BOOL","风机盘管06X00-定时控制",{"$f":"B742&VLOOKUP(A742,List!$B$3:$D$445,2,FALSE)&D742&\"_\"&VLOOKUP(E742,List!$K$2:$M$447,2,FALSE)","v":"LFCU06X00_TC"},"LFCU06X00_TC AT%M1140.0 :BOOL; (*风机盘管06X00-定时控制*)","LFCU06X00_TC            AT%M1140.0     :BOOL; (*风机盘管06X00-定时控制*)"]
["风机盘管","L","M","07X00","定时控制","1142.0",null,{"$f":"IF((IF(OR(I743=\"INT\",I743=\"WORD\",I743=\"BOOL\"),MOD(F743,2),MOD(F743,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A743&D743&\"-\"&E743","v":"风机盘管07X00-定时控制"},{"$f":"B743&VLOOKUP(A743,List!$B$3:$D$445,2,FALSE)&D743&\"_\"&VLOOKUP(E743,List!$K$2:$M$447,2,FALSE)","v":"LFCU07X00_TC"},{"$f":"K743&\" \"&\"AT%\"&C743&F743&\" \"&\":\"&I743&\";\"&\" \"&\"(*\"&J743&\"*)\"","v":"LFCU07X00_TC AT%M1142.0 :BOOL; (*风机盘管07X00-定时控制*)"},{"$f":"REPLACE(REPLACE(L743,SEARCH(\"AT%\",L743),,REPT(\" \",25-SEARCH(\"AT%\",L743))),SEARCH(\":\",REPLACE(L743,SEARCH(\"AT%\",L743),,REPT(\" \",25-SEARCH(\"AT%\",L743)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L743,SEARCH(\"AT%\",L743),,REPT(\" \",25-SEARCH(\"AT%\",L743))))))","v":"LFCU07X00_TC            AT%M1142.0     :BOOL; (*风机盘管07X00-定时控制*)"}]
["风机盘管","L","M","08X00","定时控制","1144.0",null,"验证通过","BOOL","风机盘管08X00-定时控制",{"$f":"B744&VLOOKUP(A744,List!$B$3:$D$445,2,FALSE)&D744&\"_\"&VLOOKUP(E744,List!$K$2:$M$447,2,FALSE)","v":"LFCU08X00_TC"},"LFCU08X00_TC AT%M1144.0 :BOOL; (*风机盘管08X00-定时控制*)","LFCU08X00_TC            AT%M1144.0     :BOOL; (*风机盘管08X00-定时控制*)"]
["风机盘管","L","M","B3X00","定时模式","1146.0",null,"验证通过","BOOL","风机盘管B3X00-定时模式",{"$f":"B745&VLOOKUP(A745,List!$B$3:$D$445,2,FALSE)&D745&\"_\"&VLOOKUP(E745,List!$K$2:$M$447,2,FALSE)","v":"LFCUB3X00_TM"},"LFCUB3X00_TM AT%M1146.0 :BOOL; (*风机盘管B3X00-定时模式*)","LFCUB3X00_TM            AT%M1146.0     :BOOL; (*风机盘管B3X00-定时模式*)"]
["风机盘管","L","M","B2X00","定时模式","1148.0",null,"验证通过","BOOL","风机盘管B2X00-定时模式",{"$f":"B746&VLOOKUP(A746,List!$B$3:$D$445,2,FALSE)&D746&\"_\"&VLOOKUP(E746,List!$K$2:$M$447,2,FALSE)","v":"LFCUB2X00_TM"},"LFCUB2X00_TM AT%M1148.0 :BOOL; (*风机盘管B2X00-定时模式*)","LFCUB2X00_TM            AT%M1148.0     :BOOL; (*风机盘管B2X00-定时模式*)"]
["风机盘管","L","M","B1X00","定时模式","1150.0",null,"验证通过","BOOL","风机盘管B1X00-定时模式",{"$f":"B747&VLOOKUP(A747,List!$B$3:$D$445,2,FALSE)&D747&\"_\"&VLOOKUP(E747,List!$K$2:$M$447,2,FALSE)","v":"LFCUB1X00_TM"},"LFCUB1X00_TM AT%M1150.0 :BOOL; (*风机盘管B1X00-定时模式*)","LFCUB1X00_TM            AT%M1150.0     :BOOL; (*风机盘管B1X00-定时模式*)"]
["风机盘管","L","M","01X00","定时模式","1152.0",null,"验证通过","BOOL","风机盘管01X00-定时模式",{"$f":"B748&VLOOKUP(A748,List!$B$3:$D$445,2,FALSE)&D748&\"_\"&VLOOKUP(E748,List!$K$2:$M$447,2,FALSE)","v":"LFCU01X00_TM"},"LFCU01X00_TM AT%M1152.0 :BOOL; (*风机盘管01X00-定时模式*)","LFCU01X00_TM            AT%M1152.0     :BOOL; (*风机盘管01X00-定时模式*)"]
["风机盘管","L","M","02X00","定时模式","1154.0",null,{"$f":"IF((IF(OR(I749=\"INT\",I749=\"WORD\",I749=\"BOOL\"),MOD(F749,2),MOD(F749,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","风机盘管02X00-定时模式",{"$f":"B749&VLOOKUP(A749,List!$B$3:$D$445,2,FALSE)&D749&\"_\"&VLOOKUP(E749,List!$K$2:$M$447,2,FALSE)","v":"LFCU02X00_TM"},"LFCU02X00_TM AT%M1154.0 :BOOL; (*风机盘管02X00-定时模式*)","LFCU02X00_TM            AT%M1154.0     :BOOL; (*风机盘管02X00-定时模式*)"]
["风机盘管","L","M","03X00","定时模式","1156.0",null,"验证通过","BOOL","风机盘管03X00-定时模式",{"$f":"B750&VLOOKUP(A750,List!$B$3:$D$445,2,FALSE)&D750&\"_\"&VLOOKUP(E750,List!$K$2:$M$447,2,FALSE)","v":"LFCU03X00_TM"},"LFCU03X00_TM AT%M1156.0 :BOOL; (*风机盘管03X00-定时模式*)","LFCU03X00_TM            AT%M1156.0     :BOOL; (*风机盘管03X00-定时模式*)"]
["风机盘管","L","M","04X00","定时模式","1158.0",null,"验证通过","BOOL","风机盘管04X00-定时模式",{"$f":"B751&VLOOKUP(A751,List!$B$3:$D$445,2,FALSE)&D751&\"_\"&VLOOKUP(E751,List!$K$2:$M$447,2,FALSE)","v":"LFCU04X00_TM"},"LFCU04X00_TM AT%M1158.0 :BOOL; (*风机盘管04X00-定时模式*)","LFCU04X00_TM            AT%M1158.0     :BOOL; (*风机盘管04X00-定时模式*)"]
["风机盘管","L","M","05X00","定时模式","1160.0",null,"验证通过","BOOL","风机盘管05X00-定时模式",{"$f":"B752&VLOOKUP(A752,List!$B$3:$D$445,2,FALSE)&D752&\"_\"&VLOOKUP(E752,List!$K$2:$M$447,2,FALSE)","v":"LFCU05X00_TM"},"LFCU05X00_TM AT%M1160.0 :BOOL; (*风机盘管05X00-定时模式*)","LFCU05X00_TM            AT%M1160.0     :BOOL; (*风机盘管05X00-定时模式*)"]
["风机盘管","L","M","06X00","定时模式","1162.0",null,"验证通过","BOOL","风机盘管06X00-定时模式",{"$f":"B753&VLOOKUP(A753,List!$B$3:$D$445,2,FALSE)&D753&\"_\"&VLOOKUP(E753,List!$K$2:$M$447,2,FALSE)","v":"LFCU06X00_TM"},"LFCU06X00_TM AT%M1162.0 :BOOL; (*风机盘管06X00-定时模式*)","LFCU06X00_TM            AT%M1162.0     :BOOL; (*风机盘管06X00-定时模式*)"]
["风机盘管","L","M","07X00","定时模式","1164.0",null,{"$f":"IF((IF(OR(I754=\"INT\",I754=\"WORD\",I754=\"BOOL\"),MOD(F754,2),MOD(F754,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A754&D754&\"-\"&E754","v":"风机盘管07X00-定时模式"},{"$f":"B754&VLOOKUP(A754,List!$B$3:$D$445,2,FALSE)&D754&\"_\"&VLOOKUP(E754,List!$K$2:$M$447,2,FALSE)","v":"LFCU07X00_TM"},{"$f":"K754&\" \"&\"AT%\"&C754&F754&\" \"&\":\"&I754&\";\"&\" \"&\"(*\"&J754&\"*)\"","v":"LFCU07X00_TM AT%M1164.0 :BOOL; (*风机盘管07X00-定时模式*)"},{"$f":"REPLACE(REPLACE(L754,SEARCH(\"AT%\",L754),,REPT(\" \",25-SEARCH(\"AT%\",L754))),SEARCH(\":\",REPLACE(L754,SEARCH(\"AT%\",L754),,REPT(\" \",25-SEARCH(\"AT%\",L754)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L754,SEARCH(\"AT%\",L754),,REPT(\" \",25-SEARCH(\"AT%\",L754))))))","v":"LFCU07X00_TM            AT%M1164.0     :BOOL; (*风机盘管07X00-定时模式*)"}]
["风机盘管","L","M","08X00","定时模式","1166.0",null,"验证通过","BOOL","风机盘管08X00-定时模式",{"$f":"B755&VLOOKUP(A755,List!$B$3:$D$445,2,FALSE)&D755&\"_\"&VLOOKUP(E755,List!$K$2:$M$447,2,FALSE)","v":"LFCU08X00_TM"},"LFCU08X00_TM AT%M1166.0 :BOOL; (*风机盘管08X00-定时模式*)","LFCU08X00_TM            AT%M1166.0     :BOOL; (*风机盘管08X00-定时模式*)"]
["风机盘管","R","M","B3X00","设定温度值","1172.0",null,{"$f":"IF((IF(OR(I756=\"INT\",I756=\"WORD\",I756=\"BOOL\"),MOD(F756,2),MOD(F756,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"REAL",{"$f":"A756&D756&\"-新云平台\"&E756","v":"风机盘管B3X00-新云平台设定温度值"},{"$f":"B756&VLOOKUP(A756,List!$B$3:$D$445,2,FALSE)&D756&\"_\"&VLOOKUP(E756,List!$K$2:$M$447,2,FALSE)","v":"RFCUB3X00_TSET"},{"$f":"K756&\" \"&\"AT%\"&C756&F756&\" \"&\":\"&I756&\";\"&\" \"&\"(*\"&J756&\"*)\"","v":"RFCUB3X00_TSET AT%M1172.0 :REAL; (*风机盘管B3X00-新云平台设定温度值*)"},{"$f":"REPLACE(REPLACE(L756,SEARCH(\"AT%\",L756),,REPT(\" \",25-SEARCH(\"AT%\",L756))),SEARCH(\":\",REPLACE(L756,SEARCH(\"AT%\",L756),,REPT(\" \",25-SEARCH(\"AT%\",L756)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L756,SEARCH(\"AT%\",L756),,REPT(\" \",25-SEARCH(\"AT%\",L756))))))","v":"RFCUB3X00_TSET          AT%M1172.0     :REAL; (*风机盘管B3X00-新云平台设定温度值*)"}]
["风机盘管","R","M","B2X00","设定温度值","1176.0",null,"验证通过","REAL",{"$f":"A757&D757&\"-新云平台\"&E757","v":"风机盘管B2X00-新云平台设定温度值"},{"$f":"B757&VLOOKUP(A757,List!$B$3:$D$445,2,FALSE)&D757&\"_\"&VLOOKUP(E757,List!$K$2:$M$447,2,FALSE)","v":"RFCUB2X00_TSET"},"RFCUB2X00_TSET AT%M1176.0 :REAL; (*风机盘管B2X00-新云平台设定温度值*)","RFCUB2X00_TSET          AT%M1176.0     :REAL; (*风机盘管B2X00-新云平台设定温度值*)"]
["风机盘管","R","M","B1X00","设定温度值","1180.0",null,"验证通过","REAL","风机盘管B1X00-新云平台设定温度值",{"$f":"B758&VLOOKUP(A758,List!$B$3:$D$445,2,FALSE)&D758&\"_\"&VLOOKUP(E758,List!$K$2:$M$447,2,FALSE)","v":"RFCUB1X00_TSET"},"RFCUB1X00_TSET AT%M1180.0 :REAL; (*风机盘管B1X00-新云平台设定温度值*)","RFCUB1X00_TSET          AT%M1180.0     :REAL; (*风机盘管B1X00-新云平台设定温度值*)"]
["风机盘管","R","M","01X00","设定温度值","1184.0",null,"验证通过","REAL","风机盘管01X00-新云平台设定温度值",{"$f":"B759&VLOOKUP(A759,List!$B$3:$D$445,2,FALSE)&D759&\"_\"&VLOOKUP(E759,List!$K$2:$M$447,2,FALSE)","v":"RFCU01X00_TSET"},"RFCU01X00_TSET AT%M1184.0 :REAL; (*风机盘管01X00-新云平台设定温度值*)","RFCU01X00_TSET          AT%M1184.0     :REAL; (*风机盘管01X00-新云平台设定温度值*)"]
["风机盘管","R","M","02X00","设定温度值","1188.0",null,"验证通过","REAL","风机盘管02X00-新云平台设定温度值",{"$f":"B760&VLOOKUP(A760,List!$B$3:$D$445,2,FALSE)&D760&\"_\"&VLOOKUP(E760,List!$K$2:$M$447,2,FALSE)","v":"RFCU02X00_TSET"},"RFCU02X00_TSET AT%M1188.0 :REAL; (*风机盘管02X00-新云平台设定温度值*)","RFCU02X00_TSET          AT%M1188.0     :REAL; (*风机盘管02X00-新云平台设定温度值*)"]
["风机盘管","R","M","03X00","设定温度值","1192.0",null,"验证通过","REAL","风机盘管03X00-新云平台设定温度值",{"$f":"B761&VLOOKUP(A761,List!$B$3:$D$445,2,FALSE)&D761&\"_\"&VLOOKUP(E761,List!$K$2:$M$447,2,FALSE)","v":"RFCU03X00_TSET"},"RFCU03X00_TSET AT%M1192.0 :REAL; (*风机盘管03X00-新云平台设定温度值*)","RFCU03X00_TSET          AT%M1192.0     :REAL; (*风机盘管03X00-新云平台设定温度值*)"]
["风机盘管","R","M","04X00","设定温度值","1196.0",null,"验证通过","REAL","风机盘管04X00-新云平台设定温度值",{"$f":"B762&VLOOKUP(A762,List!$B$3:$D$445,2,FALSE)&D762&\"_\"&VLOOKUP(E762,List!$K$2:$M$447,2,FALSE)","v":"RFCU04X00_TSET"},"RFCU04X00_TSET AT%M1196.0 :REAL; (*风机盘管04X00-新云平台设定温度值*)","RFCU04X00_TSET          AT%M1196.0     :REAL; (*风机盘管04X00-新云平台设定温度值*)"]
["风机盘管","R","M","05X00","设定温度值","1200.0",null,"验证通过","REAL","风机盘管05X00-新云平台设定温度值",{"$f":"B763&VLOOKUP(A763,List!$B$3:$D$445,2,FALSE)&D763&\"_\"&VLOOKUP(E763,List!$K$2:$M$447,2,FALSE)","v":"RFCU05X00_TSET"},"RFCU05X00_TSET AT%M1200.0 :REAL; (*风机盘管05X00-新云平台设定温度值*)","RFCU05X00_TSET          AT%M1200.0     :REAL; (*风机盘管05X00-新云平台设定温度值*)"]
["风机盘管","R","M","06X00","设定温度值","1204.0",null,"验证通过","REAL","风机盘管06X00-新云平台设定温度值",{"$f":"B764&VLOOKUP(A764,List!$B$3:$D$445,2,FALSE)&D764&\"_\"&VLOOKUP(E764,List!$K$2:$M$447,2,FALSE)","v":"RFCU06X00_TSET"},"RFCU06X00_TSET AT%M1204.0 :REAL; (*风机盘管06X00-新云平台设定温度值*)","RFCU06X00_TSET          AT%M1204.0     :REAL; (*风机盘管06X00-新云平台设定温度值*)"]
["风机盘管","R","M","07X00","设定温度值","1208.0",null,{"$f":"IF((IF(OR(I765=\"INT\",I765=\"WORD\",I765=\"BOOL\"),MOD(F765,2),MOD(F765,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"REAL",{"$f":"A765&D765&\"-新云平台\"&E765","v":"风机盘管07X00-新云平台设定温度值"},{"$f":"B765&VLOOKUP(A765,List!$B$3:$D$445,2,FALSE)&D765&\"_\"&VLOOKUP(E765,List!$K$2:$M$447,2,FALSE)","v":"RFCU07X00_TSET"},{"$f":"K765&\" \"&\"AT%\"&C765&F765&\" \"&\":\"&I765&\";\"&\" \"&\"(*\"&J765&\"*)\"","v":"RFCU07X00_TSET AT%M1208.0 :REAL; (*风机盘管07X00-新云平台设定温度值*)"},{"$f":"REPLACE(REPLACE(L765,SEARCH(\"AT%\",L765),,REPT(\" \",25-SEARCH(\"AT%\",L765))),SEARCH(\":\",REPLACE(L765,SEARCH(\"AT%\",L765),,REPT(\" \",25-SEARCH(\"AT%\",L765)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L765,SEARCH(\"AT%\",L765),,REPT(\" \",25-SEARCH(\"AT%\",L765))))))","v":"RFCU07X00_TSET          AT%M1208.0     :REAL; (*风机盘管07X00-新云平台设定温度值*)"}]
["风机盘管","R","M","08X00","设定温度值","1212.0",null,"验证通过","REAL","风机盘管08X00-新云平台设定温度值",{"$f":"B766&VLOOKUP(A766,List!$B$3:$D$445,2,FALSE)&D766&\"_\"&VLOOKUP(E766,List!$K$2:$M$447,2,FALSE)","v":"RFCU08X00_TSET"},"RFCU08X00_TSET AT%M1212.0 :REAL; (*风机盘管08X00-新云平台设定温度值*)","RFCU08X00_TSET          AT%M1212.0     :REAL; (*风机盘管08X00-新云平台设定温度值*)"]
["风机盘管","R","M","B3X00","季节模式","1216.0",null,"验证通过","INT","风机盘管B3X00-新云平台季节模式",{"$f":"B767&VLOOKUP(A767,List!$B$3:$D$445,2,FALSE)&D767&\"_\"&VLOOKUP(E767,List!$K$2:$M$447,2,FALSE)","v":"RFCUB3X00_SM"},"RFCUB3X00_SM AT%M1216.0 :INT; (*风机盘管B3X00-新云平台季节模式*)","RFCUB3X00_SM            AT%M1216.0     :INT; (*风机盘管B3X00-新云平台季节模式*)"]
["风机盘管","R","M","B2X00","季节模式","1218.0",null,"验证通过","INT","风机盘管B2X00-新云平台季节模式",{"$f":"B768&VLOOKUP(A768,List!$B$3:$D$445,2,FALSE)&D768&\"_\"&VLOOKUP(E768,List!$K$2:$M$447,2,FALSE)","v":"RFCUB2X00_SM"},"RFCUB2X00_SM AT%M1218.0 :INT; (*风机盘管B2X00-新云平台季节模式*)","RFCUB2X00_SM            AT%M1218.0     :INT; (*风机盘管B2X00-新云平台季节模式*)"]
["风机盘管","R","M","B1X00","季节模式","1220.0",null,"验证通过","INT","风机盘管B1X00-新云平台季节模式",{"$f":"B769&VLOOKUP(A769,List!$B$3:$D$445,2,FALSE)&D769&\"_\"&VLOOKUP(E769,List!$K$2:$M$447,2,FALSE)","v":"RFCUB1X00_SM"},"RFCUB1X00_SM AT%M1220.0 :INT; (*风机盘管B1X00-新云平台季节模式*)","RFCUB1X00_SM            AT%M1220.0     :INT; (*风机盘管B1X00-新云平台季节模式*)"]
["风机盘管","R","M","01X00","季节模式","1222.0",null,"验证通过","INT","风机盘管01X00-新云平台季节模式",{"$f":"B770&VLOOKUP(A770,List!$B$3:$D$445,2,FALSE)&D770&\"_\"&VLOOKUP(E770,List!$K$2:$M$447,2,FALSE)","v":"RFCU01X00_SM"},"RFCU01X00_SM AT%M1222.0 :INT; (*风机盘管01X00-新云平台季节模式*)","RFCU01X00_SM            AT%M1222.0     :INT; (*风机盘管01X00-新云平台季节模式*)"]
["风机盘管","R","M","02X00","季节模式","1224.0",null,"验证通过","INT","风机盘管02X00-新云平台季节模式",{"$f":"B771&VLOOKUP(A771,List!$B$3:$D$445,2,FALSE)&D771&\"_\"&VLOOKUP(E771,List!$K$2:$M$447,2,FALSE)","v":"RFCU02X00_SM"},"RFCU02X00_SM AT%M1224.0 :INT; (*风机盘管02X00-新云平台季节模式*)","RFCU02X00_SM            AT%M1224.0     :INT; (*风机盘管02X00-新云平台季节模式*)"]
["风机盘管","R","M","03X00","季节模式","1226.0",null,"验证通过","INT","风机盘管03X00-新云平台季节模式",{"$f":"B772&VLOOKUP(A772,List!$B$3:$D$445,2,FALSE)&D772&\"_\"&VLOOKUP(E772,List!$K$2:$M$447,2,FALSE)","v":"RFCU03X00_SM"},"RFCU03X00_SM AT%M1226.0 :INT; (*风机盘管03X00-新云平台季节模式*)","RFCU03X00_SM            AT%M1226.0     :INT; (*风机盘管03X00-新云平台季节模式*)"]
["风机盘管","R","M","04X00","季节模式","1228.0",null,"验证通过","INT","风机盘管04X00-新云平台季节模式",{"$f":"B773&VLOOKUP(A773,List!$B$3:$D$445,2,FALSE)&D773&\"_\"&VLOOKUP(E773,List!$K$2:$M$447,2,FALSE)","v":"RFCU04X00_SM"},"RFCU04X00_SM AT%M1228.0 :INT; (*风机盘管04X00-新云平台季节模式*)","RFCU04X00_SM            AT%M1228.0     :INT; (*风机盘管04X00-新云平台季节模式*)"]
["风机盘管","R","M","05X00","季节模式","1230.0",null,"验证通过","INT","风机盘管05X00-新云平台季节模式",{"$f":"B774&VLOOKUP(A774,List!$B$3:$D$445,2,FALSE)&D774&\"_\"&VLOOKUP(E774,List!$K$2:$M$447,2,FALSE)","v":"RFCU05X00_SM"},"RFCU05X00_SM AT%M1230.0 :INT; (*风机盘管05X00-新云平台季节模式*)","RFCU05X00_SM            AT%M1230.0     :INT; (*风机盘管05X00-新云平台季节模式*)"]
["风机盘管","R","M","06X00","季节模式","1232.0",null,"验证通过","INT","风机盘管06X00-新云平台季节模式",{"$f":"B775&VLOOKUP(A775,List!$B$3:$D$445,2,FALSE)&D775&\"_\"&VLOOKUP(E775,List!$K$2:$M$447,2,FALSE)","v":"RFCU06X00_SM"},"RFCU06X00_SM AT%M1232.0 :INT; (*风机盘管06X00-新云平台季节模式*)","RFCU06X00_SM            AT%M1232.0     :INT; (*风机盘管06X00-新云平台季节模式*)"]
["风机盘管","R","M","07X00","季节模式","1234.0",null,{"$f":"IF((IF(OR(I776=\"INT\",I776=\"WORD\",I776=\"BOOL\"),MOD(F776,2),MOD(F776,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"INT",{"$f":"A776&D776&\"-新云平台\"&E776","v":"风机盘管07X00-新云平台季节模式"},{"$f":"B776&VLOOKUP(A776,List!$B$3:$D$445,2,FALSE)&D776&\"_\"&VLOOKUP(E776,List!$K$2:$M$447,2,FALSE)","v":"RFCU07X00_SM"},{"$f":"K776&\" \"&\"AT%\"&C776&F776&\" \"&\":\"&I776&\";\"&\" \"&\"(*\"&J776&\"*)\"","v":"RFCU07X00_SM AT%M1234.0 :INT; (*风机盘管07X00-新云平台季节模式*)"},{"$f":"REPLACE(REPLACE(L776,SEARCH(\"AT%\",L776),,REPT(\" \",25-SEARCH(\"AT%\",L776))),SEARCH(\":\",REPLACE(L776,SEARCH(\"AT%\",L776),,REPT(\" \",25-SEARCH(\"AT%\",L776)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L776,SEARCH(\"AT%\",L776),,REPT(\" \",25-SEARCH(\"AT%\",L776))))))","v":"RFCU07X00_SM            AT%M1234.0     :INT; (*风机盘管07X00-新云平台季节模式*)"}]
["风机盘管","R","M","08X00","季节模式","1236.0",null,"验证通过","INT","风机盘管08X00-新云平台季节模式",{"$f":"B777&VLOOKUP(A777,List!$B$3:$D$445,2,FALSE)&D777&\"_\"&VLOOKUP(E777,List!$K$2:$M$447,2,FALSE)","v":"RFCU08X00_SM"},"RFCU08X00_SM AT%M1236.0 :INT; (*风机盘管08X00-新云平台季节模式*)","RFCU08X00_SM            AT%M1236.0     :INT; (*风机盘管08X00-新云平台季节模式*)"]
["风机盘管","R","M","B3X00","启停控制","1238.0",null,"验证通过","BOOL","风机盘管B3X00-新云平台启停控制",{"$f":"B778&VLOOKUP(A778,List!$B$3:$D$445,2,FALSE)&D778&\"_\"&VLOOKUP(E778,List!$K$2:$M$447,2,FALSE)","v":"RFCUB3X00_C"},{"$f":"K778&\" \"&\"AT%\"&C778&F778&\" \"&\":\"&I778&\";\"&\" \"&\"(*\"&J778&\"*)\"","v":"RFCUB3X00_C AT%M1238.0 :BOOL; (*风机盘管B3X00-新云平台启停控制*)"},{"$f":"REPLACE(REPLACE(L778,SEARCH(\"AT%\",L778),,REPT(\" \",25-SEARCH(\"AT%\",L778))),SEARCH(\":\",REPLACE(L778,SEARCH(\"AT%\",L778),,REPT(\" \",25-SEARCH(\"AT%\",L778)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L778,SEARCH(\"AT%\",L778),,REPT(\" \",25-SEARCH(\"AT%\",L778))))))","v":"RFCUB3X00_C             AT%M1238.0     :BOOL; (*风机盘管B3X00-新云平台启停控制*)"}]
["风机盘管","R","M","B2X00","启停控制","1240.0",null,"验证通过","BOOL","风机盘管B2X00-新云平台启停控制",{"$f":"B779&VLOOKUP(A779,List!$B$3:$D$445,2,FALSE)&D779&\"_\"&VLOOKUP(E779,List!$K$2:$M$447,2,FALSE)","v":"RFCUB2X00_C"},"RFCUB2X00_C AT%M1240.0 :BOOL; (*风机盘管B2X00-新云平台启停控制*)","RFCUB2X00_C             AT%M1240.0     :BOOL; (*风机盘管B2X00-新云平台启停控制*)"]
["风机盘管","R","M","B1X00","启停控制","1242.0",null,"验证通过","BOOL","风机盘管B1X00-新云平台启停控制",{"$f":"B780&VLOOKUP(A780,List!$B$3:$D$445,2,FALSE)&D780&\"_\"&VLOOKUP(E780,List!$K$2:$M$447,2,FALSE)","v":"RFCUB1X00_C"},"RFCUB1X00_C AT%M1242.0 :BOOL; (*风机盘管B1X00-新云平台启停控制*)","RFCUB1X00_C             AT%M1242.0     :BOOL; (*风机盘管B1X00-新云平台启停控制*)"]
["风机盘管","R","M","01X00","启停控制","1244.0",null,"验证通过","BOOL","风机盘管01X00-新云平台启停控制",{"$f":"B781&VLOOKUP(A781,List!$B$3:$D$445,2,FALSE)&D781&\"_\"&VLOOKUP(E781,List!$K$2:$M$447,2,FALSE)","v":"RFCU01X00_C"},"RFCU01X00_C AT%M1244.0 :BOOL; (*风机盘管01X00-新云平台启停控制*)","RFCU01X00_C             AT%M1244.0     :BOOL; (*风机盘管01X00-新云平台启停控制*)"]
["风机盘管","R","M","02X00","启停控制","1246.0",null,{"$f":"IF((IF(OR(I782=\"INT\",I782=\"WORD\",I782=\"BOOL\"),MOD(F782,2),MOD(F782,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","风机盘管02X00-新云平台启停控制",{"$f":"B782&VLOOKUP(A782,List!$B$3:$D$445,2,FALSE)&D782&\"_\"&VLOOKUP(E782,List!$K$2:$M$447,2,FALSE)","v":"RFCU02X00_C"},"RFCU02X00_C AT%M1246.0 :BOOL; (*风机盘管02X00-新云平台启停控制*)","RFCU02X00_C             AT%M1246.0     :BOOL; (*风机盘管02X00-新云平台启停控制*)"]
["风机盘管","R","M","03X00","启停控制","1248.0",null,"验证通过","BOOL","风机盘管03X00-新云平台启停控制",{"$f":"B783&VLOOKUP(A783,List!$B$3:$D$445,2,FALSE)&D783&\"_\"&VLOOKUP(E783,List!$K$2:$M$447,2,FALSE)","v":"RFCU03X00_C"},"RFCU03X00_C AT%M1248.0 :BOOL; (*风机盘管03X00-新云平台启停控制*)","RFCU03X00_C             AT%M1248.0     :BOOL; (*风机盘管03X00-新云平台启停控制*)"]
["风机盘管","R","M","04X00","启停控制","1250.0",null,"验证通过","BOOL","风机盘管04X00-新云平台启停控制",{"$f":"B784&VLOOKUP(A784,List!$B$3:$D$445,2,FALSE)&D784&\"_\"&VLOOKUP(E784,List!$K$2:$M$447,2,FALSE)","v":"RFCU04X00_C"},"RFCU04X00_C AT%M1250.0 :BOOL; (*风机盘管04X00-新云平台启停控制*)","RFCU04X00_C             AT%M1250.0     :BOOL; (*风机盘管04X00-新云平台启停控制*)"]
["风机盘管","R","M","05X00","启停控制","1252.0",null,"验证通过","BOOL","风机盘管05X00-新云平台启停控制",{"$f":"B785&VLOOKUP(A785,List!$B$3:$D$445,2,FALSE)&D785&\"_\"&VLOOKUP(E785,List!$K$2:$M$447,2,FALSE)","v":"RFCU05X00_C"},"RFCU05X00_C AT%M1252.0 :BOOL; (*风机盘管05X00-新云平台启停控制*)","RFCU05X00_C             AT%M1252.0     :BOOL; (*风机盘管05X00-新云平台启停控制*)"]
["风机盘管","R","M","06X00","启停控制","1254.0",null,"验证通过","BOOL","风机盘管06X00-新云平台启停控制",{"$f":"B786&VLOOKUP(A786,List!$B$3:$D$445,2,FALSE)&D786&\"_\"&VLOOKUP(E786,List!$K$2:$M$447,2,FALSE)","v":"RFCU06X00_C"},"RFCU06X00_C AT%M1254.0 :BOOL; (*风机盘管06X00-新云平台启停控制*)","RFCU06X00_C             AT%M1254.0     :BOOL; (*风机盘管06X00-新云平台启停控制*)"]
["风机盘管","R","M","07X00","启停控制","1256.0",null,{"$f":"IF((IF(OR(I787=\"INT\",I787=\"WORD\",I787=\"BOOL\"),MOD(F787,2),MOD(F787,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A787&D787&\"-新云平台\"&E787","v":"风机盘管07X00-新云平台启停控制"},{"$f":"B787&VLOOKUP(A787,List!$B$3:$D$445,2,FALSE)&D787&\"_\"&VLOOKUP(E787,List!$K$2:$M$447,2,FALSE)","v":"RFCU07X00_C"},{"$f":"K787&\" \"&\"AT%\"&C787&F787&\" \"&\":\"&I787&\";\"&\" \"&\"(*\"&J787&\"*)\"","v":"RFCU07X00_C AT%M1256.0 :BOOL; (*风机盘管07X00-新云平台启停控制*)"},{"$f":"REPLACE(REPLACE(L787,SEARCH(\"AT%\",L787),,REPT(\" \",25-SEARCH(\"AT%\",L787))),SEARCH(\":\",REPLACE(L787,SEARCH(\"AT%\",L787),,REPT(\" \",25-SEARCH(\"AT%\",L787)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L787,SEARCH(\"AT%\",L787),,REPT(\" \",25-SEARCH(\"AT%\",L787))))))","v":"RFCU07X00_C             AT%M1256.0     :BOOL; (*风机盘管07X00-新云平台启停控制*)"}]
["风机盘管","R","M","08X00","启停控制",{"$f":"IF(OR(I787=\"REAL\",I787=\"DWORD\",I787=\"DINT\"),(IF(OR(I788=\"REAL\",I788=\"DWORD\",I788=\"DINT\"),F787+4+MOD(F787,4),F787+4)),(IF(OR(I788=\"REAL\",I788=\"DWORD\",I788=\"DINT\"),F787+4+MOD(F787,4),F787+2)))&\".0\"","v":"1258.0"},null,"验证通过","BOOL","风机盘管08X00-新云平台启停控制",{"$f":"B788&VLOOKUP(A788,List!$B$3:$D$445,2,FALSE)&D788&\"_\"&VLOOKUP(E788,List!$K$2:$M$447,2,FALSE)","v":"RFCU08X00_C"},"RFCU08X00_C AT%M1258.0 :BOOL; (*风机盘管08X00-新云平台启停控制*)","RFCU08X00_C             AT%M1258.0     :BOOL; (*风机盘管08X00-新云平台启停控制*)"]
["P新风机组","L","M","05X00","设定温度值","1264.0",null,{"$f":"IF((IF(OR(I789=\"INT\",I789=\"WORD\",I789=\"BOOL\"),MOD(F789,2),MOD(F789,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"REAL","P新风机组05X00-新云平台设定温度值",{"$f":"B789&VLOOKUP(A789,List!$B$3:$D$445,2,FALSE)&D789&\"_\"&VLOOKUP(E789,List!$K$2:$M$447,2,FALSE)","v":"LPAU05X00_TSET"},{"$f":"K789&\" \"&\"AT%\"&C789&F789&\" \"&\":\"&I789&\";\"&\" \"&\"(*\"&J789&\"*)\"","v":"LPAU05X00_TSET AT%M1264.0 :REAL; (*P新风机组05X00-新云平台设定温度值*)"},{"$f":"REPLACE(REPLACE(L789,SEARCH(\"AT%\",L789),,REPT(\" \",25-SEARCH(\"AT%\",L789))),SEARCH(\":\",REPLACE(L789,SEARCH(\"AT%\",L789),,REPT(\" \",25-SEARCH(\"AT%\",L789)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L789,SEARCH(\"AT%\",L789),,REPT(\" \",25-SEARCH(\"AT%\",L789))))))","v":"LPAU05X00_TSET          AT%M1264.0     :REAL; (*P新风机组05X00-新云平台设定温度值*)"}]
["P新风机组","L","M","06X00","设定温度值","1268.0",null,"验证通过","REAL","P新风机组06X00-新云平台设定温度值",{"$f":"B790&VLOOKUP(A790,List!$B$3:$D$445,2,FALSE)&D790&\"_\"&VLOOKUP(E790,List!$K$2:$M$447,2,FALSE)","v":"LPAU06X00_TSET"},"LPAU06X00_TSET AT%M1268.0 :REAL; (*P新风机组06X00-新云平台设定温度值*)","LPAU06X00_TSET          AT%M1268.0     :REAL; (*P新风机组06X00-新云平台设定温度值*)"]
["P新风机组","L","M","07X00","设定温度值","1272.0",null,"验证通过","REAL","P新风机组07X00-新云平台设定温度值",{"$f":"B791&VLOOKUP(A791,List!$B$3:$D$445,2,FALSE)&D791&\"_\"&VLOOKUP(E791,List!$K$2:$M$447,2,FALSE)","v":"LPAU07X00_TSET"},"LPAU07X00_TSET AT%M1272.0 :REAL; (*P新风机组07X00-新云平台设定温度值*)","LPAU07X00_TSET          AT%M1272.0     :REAL; (*P新风机组07X00-新云平台设定温度值*)"]
["P新风机组","L","M","08X00","设定温度值","1276.0",null,"验证通过","REAL","P新风机组08X00-新云平台设定温度值",{"$f":"B792&VLOOKUP(A792,List!$B$3:$D$445,2,FALSE)&D792&\"_\"&VLOOKUP(E792,List!$K$2:$M$447,2,FALSE)","v":"LPAU08X00_TSET"},"LPAU08X00_TSET AT%M1276.0 :REAL; (*P新风机组08X00-新云平台设定温度值*)","LPAU08X00_TSET          AT%M1276.0     :REAL; (*P新风机组08X00-新云平台设定温度值*)"]
["P新风机组","L","M","09X00","设定温度值","1280.0",null,"验证通过","REAL","P新风机组09X00-新云平台设定温度值",{"$f":"B793&VLOOKUP(A793,List!$B$3:$D$445,2,FALSE)&D793&\"_\"&VLOOKUP(E793,List!$K$2:$M$447,2,FALSE)","v":"LPAU09X00_TSET"},"LPAU09X00_TSET AT%M1280.0 :REAL; (*P新风机组09X00-新云平台设定温度值*)","LPAU09X00_TSET          AT%M1280.0     :REAL; (*P新风机组09X00-新云平台设定温度值*)"]
["P新风机组","L","M","05X00","季节模式","1284.0",null,"验证通过","INT","P新风机组05X00-新云平台季节模式",{"$f":"B794&VLOOKUP(A794,List!$B$3:$D$445,2,FALSE)&D794&\"_\"&VLOOKUP(E794,List!$K$2:$M$447,2,FALSE)","v":"LPAU05X00_SM"},"LPAU05X00_SM AT%M1284.0 :INT; (*P新风机组05X00-新云平台季节模式*)","LPAU05X00_SM            AT%M1284.0     :INT; (*P新风机组05X00-新云平台季节模式*)"]
["P新风机组","L","M","06X00","季节模式","1286.0",null,"验证通过","INT","P新风机组06X00-新云平台季节模式",{"$f":"B795&VLOOKUP(A795,List!$B$3:$D$445,2,FALSE)&D795&\"_\"&VLOOKUP(E795,List!$K$2:$M$447,2,FALSE)","v":"LPAU06X00_SM"},"LPAU06X00_SM AT%M1286.0 :INT; (*P新风机组06X00-新云平台季节模式*)","LPAU06X00_SM            AT%M1286.0     :INT; (*P新风机组06X00-新云平台季节模式*)"]
["P新风机组","L","M","07X00","季节模式","1288.0",null,"验证通过","INT","P新风机组07X00-新云平台季节模式",{"$f":"B796&VLOOKUP(A796,List!$B$3:$D$445,2,FALSE)&D796&\"_\"&VLOOKUP(E796,List!$K$2:$M$447,2,FALSE)","v":"LPAU07X00_SM"},"LPAU07X00_SM AT%M1288.0 :INT; (*P新风机组07X00-新云平台季节模式*)","LPAU07X00_SM            AT%M1288.0     :INT; (*P新风机组07X00-新云平台季节模式*)"]
["P新风机组","L","M","08X00","季节模式","1290.0",null,"验证通过","INT","P新风机组08X00-新云平台季节模式",{"$f":"B797&VLOOKUP(A797,List!$B$3:$D$445,2,FALSE)&D797&\"_\"&VLOOKUP(E797,List!$K$2:$M$447,2,FALSE)","v":"LPAU08X00_SM"},"LPAU08X00_SM AT%M1290.0 :INT; (*P新风机组08X00-新云平台季节模式*)","LPAU08X00_SM            AT%M1290.0     :INT; (*P新风机组08X00-新云平台季节模式*)"]
["P新风机组","L","M","09X00","季节模式","1292.0",null,"验证通过","INT","P新风机组09X00-新云平台季节模式",{"$f":"B798&VLOOKUP(A798,List!$B$3:$D$445,2,FALSE)&D798&\"_\"&VLOOKUP(E798,List!$K$2:$M$447,2,FALSE)","v":"LPAU09X00_SM"},"LPAU09X00_SM AT%M1292.0 :INT; (*P新风机组09X00-新云平台季节模式*)","LPAU09X00_SM            AT%M1292.0     :INT; (*P新风机组09X00-新云平台季节模式*)"]
["P新风机组","L","M","05X00","启停控制","1294.0",null,"验证通过","BOOL","P新风机组05X00-新云平台启停控制",{"$f":"B799&VLOOKUP(A799,List!$B$3:$D$445,2,FALSE)&D799&\"_\"&VLOOKUP(E799,List!$K$2:$M$447,2,FALSE)","v":"LPAU05X00_C"},"LPAU05X00_C AT%M1294.0 :BOOL; (*P新风机组05X00-新云平台启停控制*)","LPAU05X00_C             AT%M1294.0     :BOOL; (*P新风机组05X00-新云平台启停控制*)"]
["P新风机组","L","M","06X00","启停控制","1296.0",null,"验证通过","BOOL","P新风机组06X00-新云平台启停控制",{"$f":"B800&VLOOKUP(A800,List!$B$3:$D$445,2,FALSE)&D800&\"_\"&VLOOKUP(E800,List!$K$2:$M$447,2,FALSE)","v":"LPAU06X00_C"},"LPAU06X00_C AT%M1296.0 :BOOL; (*P新风机组06X00-新云平台启停控制*)","LPAU06X00_C             AT%M1296.0     :BOOL; (*P新风机组06X00-新云平台启停控制*)"]
["P新风机组","L","M","07X00","启停控制","1298.0",null,"验证通过","BOOL","P新风机组07X00-新云平台启停控制",{"$f":"B801&VLOOKUP(A801,List!$B$3:$D$445,2,FALSE)&D801&\"_\"&VLOOKUP(E801,List!$K$2:$M$447,2,FALSE)","v":"LPAU07X00_C"},"LPAU07X00_C AT%M1298.0 :BOOL; (*P新风机组07X00-新云平台启停控制*)","LPAU07X00_C             AT%M1298.0     :BOOL; (*P新风机组07X00-新云平台启停控制*)"]
["P新风机组","L","M","08X00","启停控制","1300.0",null,"验证通过","BOOL","P新风机组08X00-新云平台启停控制",{"$f":"B802&VLOOKUP(A802,List!$B$3:$D$445,2,FALSE)&D802&\"_\"&VLOOKUP(E802,List!$K$2:$M$447,2,FALSE)","v":"LPAU08X00_C"},"LPAU08X00_C AT%M1300.0 :BOOL; (*P新风机组08X00-新云平台启停控制*)","LPAU08X00_C             AT%M1300.0     :BOOL; (*P新风机组08X00-新云平台启停控制*)"]
["P新风机组","L","M","09X00","启停控制","1302.0",null,"验证通过","BOOL","P新风机组09X00-新云平台启停控制",{"$f":"B803&VLOOKUP(A803,List!$B$3:$D$445,2,FALSE)&D803&\"_\"&VLOOKUP(E803,List!$K$2:$M$447,2,FALSE)","v":"LPAU09X00_C"},"LPAU09X00_C AT%M1302.0 :BOOL; (*P新风机组09X00-新云平台启停控制*)","LPAU09X00_C             AT%M1302.0     :BOOL; (*P新风机组09X00-新云平台启停控制*)"]
["P新风机组","R","M","05X00","设定温度值","1308.0",null,"验证通过","REAL",{"$f":"A804&D804&\"-新云平台\"&E804","v":"P新风机组05X00-新云平台设定温度值"},{"$f":"B804&VLOOKUP(A804,List!$B$3:$D$445,2,FALSE)&D804&\"_\"&VLOOKUP(E804,List!$K$2:$M$447,2,FALSE)","v":"RPAU05X00_TSET"},"RPAU05X00_TSET AT%M1308.0 :REAL; (*P新风机组05X00-新云平台设定温度值*)","RPAU05X00_TSET          AT%M1308.0     :REAL; (*P新风机组05X00-新云平台设定温度值*)"]
["P新风机组","R","M","06X00","设定温度值","1312.0",null,"验证通过","REAL","P新风机组06X00-新云平台设定温度值",{"$f":"B805&VLOOKUP(A805,List!$B$3:$D$445,2,FALSE)&D805&\"_\"&VLOOKUP(E805,List!$K$2:$M$447,2,FALSE)","v":"RPAU06X00_TSET"},"RPAU06X00_TSET AT%M1312.0 :REAL; (*P新风机组06X00-新云平台设定温度值*)","RPAU06X00_TSET          AT%M1312.0     :REAL; (*P新风机组06X00-新云平台设定温度值*)"]
["P新风机组","R","M","07X00","设定温度值","1316.0",null,"验证通过","REAL","P新风机组07X00-新云平台设定温度值",{"$f":"B806&VLOOKUP(A806,List!$B$3:$D$445,2,FALSE)&D806&\"_\"&VLOOKUP(E806,List!$K$2:$M$447,2,FALSE)","v":"RPAU07X00_TSET"},"RPAU07X00_TSET AT%M1316.0 :REAL; (*P新风机组07X00-新云平台设定温度值*)","RPAU07X00_TSET          AT%M1316.0     :REAL; (*P新风机组07X00-新云平台设定温度值*)"]
["P新风机组","R","M","08X00","设定温度值","1320.0",null,"验证通过","REAL","P新风机组08X00-新云平台设定温度值",{"$f":"B807&VLOOKUP(A807,List!$B$3:$D$445,2,FALSE)&D807&\"_\"&VLOOKUP(E807,List!$K$2:$M$447,2,FALSE)","v":"RPAU08X00_TSET"},"RPAU08X00_TSET AT%M1320.0 :REAL; (*P新风机组08X00-新云平台设定温度值*)","RPAU08X00_TSET          AT%M1320.0     :REAL; (*P新风机组08X00-新云平台设定温度值*)"]
["P新风机组","R","M","09X00","设定温度值","1324.0",null,{"$f":"IF((IF(OR(I808=\"INT\",I808=\"WORD\",I808=\"BOOL\"),MOD(F808,2),MOD(F808,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"REAL",{"$f":"A808&D808&\"-新云平台\"&E808","v":"P新风机组09X00-新云平台设定温度值"},{"$f":"B808&VLOOKUP(A808,List!$B$3:$D$445,2,FALSE)&D808&\"_\"&VLOOKUP(E808,List!$K$2:$M$447,2,FALSE)","v":"RPAU09X00_TSET"},{"$f":"K808&\" \"&\"AT%\"&C808&F808&\" \"&\":\"&I808&\";\"&\" \"&\"(*\"&J808&\"*)\"","v":"RPAU09X00_TSET AT%M1324.0 :REAL; (*P新风机组09X00-新云平台设定温度值*)"},{"$f":"REPLACE(REPLACE(L808,SEARCH(\"AT%\",L808),,REPT(\" \",25-SEARCH(\"AT%\",L808))),SEARCH(\":\",REPLACE(L808,SEARCH(\"AT%\",L808),,REPT(\" \",25-SEARCH(\"AT%\",L808)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L808,SEARCH(\"AT%\",L808),,REPT(\" \",25-SEARCH(\"AT%\",L808))))))","v":"RPAU09X00_TSET          AT%M1324.0     :REAL; (*P新风机组09X00-新云平台设定温度值*)"}]
["P新风机组","R","M","05X00","季节模式","1328.0",null,"验证通过","INT","P新风机组05X00-新云平台季节模式",{"$f":"B809&VLOOKUP(A809,List!$B$3:$D$445,2,FALSE)&D809&\"_\"&VLOOKUP(E809,List!$K$2:$M$447,2,FALSE)","v":"RPAU05X00_SM"},"RPAU05X00_SM AT%M1328.0 :INT; (*P新风机组05X00-新云平台季节模式*)","RPAU05X00_SM            AT%M1328.0     :INT; (*P新风机组05X00-新云平台季节模式*)"]
["P新风机组","R","M","06X00","季节模式","1330.0",null,"验证通过","INT","P新风机组06X00-新云平台季节模式",{"$f":"B810&VLOOKUP(A810,List!$B$3:$D$445,2,FALSE)&D810&\"_\"&VLOOKUP(E810,List!$K$2:$M$447,2,FALSE)","v":"RPAU06X00_SM"},"RPAU06X00_SM AT%M1330.0 :INT; (*P新风机组06X00-新云平台季节模式*)","RPAU06X00_SM            AT%M1330.0     :INT; (*P新风机组06X00-新云平台季节模式*)"]
["P新风机组","R","M","07X00","季节模式","1332.0",null,"验证通过","INT","P新风机组07X00-新云平台季节模式",{"$f":"B811&VLOOKUP(A811,List!$B$3:$D$445,2,FALSE)&D811&\"_\"&VLOOKUP(E811,List!$K$2:$M$447,2,FALSE)","v":"RPAU07X00_SM"},"RPAU07X00_SM AT%M1332.0 :INT; (*P新风机组07X00-新云平台季节模式*)","RPAU07X00_SM            AT%M1332.0     :INT; (*P新风机组07X00-新云平台季节模式*)"]
["P新风机组","R","M","08X00","季节模式","1334.0",null,"验证通过","INT","P新风机组08X00-新云平台季节模式",{"$f":"B812&VLOOKUP(A812,List!$B$3:$D$445,2,FALSE)&D812&\"_\"&VLOOKUP(E812,List!$K$2:$M$447,2,FALSE)","v":"RPAU08X00_SM"},"RPAU08X00_SM AT%M1334.0 :INT; (*P新风机组08X00-新云平台季节模式*)","RPAU08X00_SM            AT%M1334.0     :INT; (*P新风机组08X00-新云平台季节模式*)"]
["P新风机组","R","M","09X00","季节模式","1336.0",null,{"$f":"IF((IF(OR(I813=\"INT\",I813=\"WORD\",I813=\"BOOL\"),MOD(F813,2),MOD(F813,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"INT",{"$f":"A813&D813&\"-新云平台\"&E813","v":"P新风机组09X00-新云平台季节模式"},{"$f":"B813&VLOOKUP(A813,List!$B$3:$D$445,2,FALSE)&D813&\"_\"&VLOOKUP(E813,List!$K$2:$M$447,2,FALSE)","v":"RPAU09X00_SM"},{"$f":"K813&\" \"&\"AT%\"&C813&F813&\" \"&\":\"&I813&\";\"&\" \"&\"(*\"&J813&\"*)\"","v":"RPAU09X00_SM AT%M1336.0 :INT; (*P新风机组09X00-新云平台季节模式*)"},{"$f":"REPLACE(REPLACE(L813,SEARCH(\"AT%\",L813),,REPT(\" \",25-SEARCH(\"AT%\",L813))),SEARCH(\":\",REPLACE(L813,SEARCH(\"AT%\",L813),,REPT(\" \",25-SEARCH(\"AT%\",L813)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L813,SEARCH(\"AT%\",L813),,REPT(\" \",25-SEARCH(\"AT%\",L813))))))","v":"RPAU09X00_SM            AT%M1336.0     :INT; (*P新风机组09X00-新云平台季节模式*)"}]
["P新风机组","R","M","05X00","启停控制","1338.0",null,"验证通过","BOOL","P新风机组05X00-新云平台启停控制",{"$f":"B814&VLOOKUP(A814,List!$B$3:$D$445,2,FALSE)&D814&\"_\"&VLOOKUP(E814,List!$K$2:$M$447,2,FALSE)","v":"RPAU05X00_C"},"RPAU05X00_C AT%M1338.0 :BOOL; (*P新风机组05X00-新云平台启停控制*)","RPAU05X00_C             AT%M1338.0     :BOOL; (*P新风机组05X00-新云平台启停控制*)"]
["P新风机组","R","M","06X00","启停控制","1340.0",null,"验证通过","BOOL","P新风机组06X00-新云平台启停控制",{"$f":"B815&VLOOKUP(A815,List!$B$3:$D$445,2,FALSE)&D815&\"_\"&VLOOKUP(E815,List!$K$2:$M$447,2,FALSE)","v":"RPAU06X00_C"},"RPAU06X00_C AT%M1340.0 :BOOL; (*P新风机组06X00-新云平台启停控制*)","RPAU06X00_C             AT%M1340.0     :BOOL; (*P新风机组06X00-新云平台启停控制*)"]
["P新风机组","R","M","07X00","启停控制","1342.0",null,"验证通过","BOOL","P新风机组07X00-新云平台启停控制",{"$f":"B816&VLOOKUP(A816,List!$B$3:$D$445,2,FALSE)&D816&\"_\"&VLOOKUP(E816,List!$K$2:$M$447,2,FALSE)","v":"RPAU07X00_C"},"RPAU07X00_C AT%M1342.0 :BOOL; (*P新风机组07X00-新云平台启停控制*)","RPAU07X00_C             AT%M1342.0     :BOOL; (*P新风机组07X00-新云平台启停控制*)"]
["P新风机组","R","M","08X00","启停控制","1344.0",null,"验证通过","BOOL","P新风机组08X00-新云平台启停控制",{"$f":"B817&VLOOKUP(A817,List!$B$3:$D$445,2,FALSE)&D817&\"_\"&VLOOKUP(E817,List!$K$2:$M$447,2,FALSE)","v":"RPAU08X00_C"},"RPAU08X00_C AT%M1344.0 :BOOL; (*P新风机组08X00-新云平台启停控制*)","RPAU08X00_C             AT%M1344.0     :BOOL; (*P新风机组08X00-新云平台启停控制*)"]
["P新风机组","R","M","09X00","启停控制","1346.0",null,{"$f":"IF((IF(OR(I818=\"INT\",I818=\"WORD\",I818=\"BOOL\"),MOD(F818,2),MOD(F818,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL",{"$f":"A818&D818&\"-新云平台\"&E818","v":"P新风机组09X00-新云平台启停控制"},{"$f":"B818&VLOOKUP(A818,List!$B$3:$D$445,2,FALSE)&D818&\"_\"&VLOOKUP(E818,List!$K$2:$M$447,2,FALSE)","v":"RPAU09X00_C"},{"$f":"K818&\" \"&\"AT%\"&C818&F818&\" \"&\":\"&I818&\";\"&\" \"&\"(*\"&J818&\"*)\"","v":"RPAU09X00_C AT%M1346.0 :BOOL; (*P新风机组09X00-新云平台启停控制*)"},{"$f":"REPLACE(REPLACE(L818,SEARCH(\"AT%\",L818),,REPT(\" \",25-SEARCH(\"AT%\",L818))),SEARCH(\":\",REPLACE(L818,SEARCH(\"AT%\",L818),,REPT(\" \",25-SEARCH(\"AT%\",L818)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L818,SEARCH(\"AT%\",L818),,REPT(\" \",25-SEARCH(\"AT%\",L818))))))","v":"RPAU09X00_C             AT%M1346.0     :BOOL; (*P新风机组09X00-新云平台启停控制*)"}]
["送风机","L","M","B3X00","启停控制","1348.0",null,"验证通过","BOOL","送风机B3层启停控制",{"$f":"B819&VLOOKUP(A819,List!$B$3:$D$445,2,FALSE)&D819&\"_\"&VLOOKUP(E819,List!$K$2:$M$447,2,FALSE)","v":"LSAFB3X00_C"},"LSAFB3X00_C AT%M1348.0 :BOOL; (*送风机B3层启停控制*)","LSAFB3X00_C             AT%M1348.0     :BOOL; (*送风机B3层启停控制*)"]
["送风机","L","M","B2X00","启停控制","1350.0",null,"验证通过","BOOL","送风机B2层启停控制",{"$f":"B820&VLOOKUP(A820,List!$B$3:$D$445,2,FALSE)&D820&\"_\"&VLOOKUP(E820,List!$K$2:$M$447,2,FALSE)","v":"LSAFB2X00_C"},"LSAFB2X00_C AT%M1350.0 :BOOL; (*送风机B2层启停控制*)","LSAFB2X00_C             AT%M1350.0     :BOOL; (*送风机B2层启停控制*)"]
["送风机","L","M","B1X00","启停控制","1352.0",null,"验证通过","BOOL","送风机B1层启停控制",{"$f":"B821&VLOOKUP(A821,List!$B$3:$D$445,2,FALSE)&D821&\"_\"&VLOOKUP(E821,List!$K$2:$M$447,2,FALSE)","v":"LSAFB1X00_C"},"LSAFB1X00_C AT%M1352.0 :BOOL; (*送风机B1层启停控制*)","LSAFB1X00_C             AT%M1352.0     :BOOL; (*送风机B1层启停控制*)"]
["送风机","L","M","05X00","启停控制","1354.0",null,"验证通过","BOOL","送风机5层启停控制",{"$f":"B822&VLOOKUP(A822,List!$B$3:$D$445,2,FALSE)&D822&\"_\"&VLOOKUP(E822,List!$K$2:$M$447,2,FALSE)","v":"LSAF05X00_C"},"LSAF05X00_C AT%M1354.0 :BOOL; (*送风机5层启停控制*)","LSAF05X00_C             AT%M1354.0     :BOOL; (*送风机5层启停控制*)"]
["送风机","L","M","06X00","启停控制","1356.0",null,"验证通过","BOOL","送风机6层启停控制",{"$f":"B823&VLOOKUP(A823,List!$B$3:$D$445,2,FALSE)&D823&\"_\"&VLOOKUP(E823,List!$K$2:$M$447,2,FALSE)","v":"LSAF06X00_C"},"LSAF06X00_C AT%M1356.0 :BOOL; (*送风机6层启停控制*)","LSAF06X00_C             AT%M1356.0     :BOOL; (*送风机6层启停控制*)"]
["送风机","L","M","07X00","启停控制","1358.0",null,"验证通过","BOOL","送风机7层启停控制",{"$f":"B824&VLOOKUP(A824,List!$B$3:$D$445,2,FALSE)&D824&\"_\"&VLOOKUP(E824,List!$K$2:$M$447,2,FALSE)","v":"LSAF07X00_C"},"LSAF07X00_C AT%M1358.0 :BOOL; (*送风机7层启停控制*)","LSAF07X00_C             AT%M1358.0     :BOOL; (*送风机7层启停控制*)"]
["送风机","L","M","08X00","启停控制","1360.0",null,"验证通过","BOOL","送风机8层启停控制",{"$f":"B825&VLOOKUP(A825,List!$B$3:$D$445,2,FALSE)&D825&\"_\"&VLOOKUP(E825,List!$K$2:$M$447,2,FALSE)","v":"LSAF08X00_C"},"LSAF08X00_C AT%M1360.0 :BOOL; (*送风机8层启停控制*)","LSAF08X00_C             AT%M1360.0     :BOOL; (*送风机8层启停控制*)"]
["送风机","L","M","09X00","启停控制","1362.0",null,"验证通过","BOOL","送风机9层启停控制",{"$f":"B826&VLOOKUP(A826,List!$B$3:$D$445,2,FALSE)&D826&\"_\"&VLOOKUP(E826,List!$K$2:$M$447,2,FALSE)","v":"LSAF09X00_C"},"LSAF09X00_C AT%M1362.0 :BOOL; (*送风机9层启停控制*)","LSAF09X00_C             AT%M1362.0     :BOOL; (*送风机9层启停控制*)"]
["排风机","L","M","B3X00","启停控制","1364.0",null,"验证通过","BOOL","排风机B3层启停控制",{"$f":"B827&VLOOKUP(A827,List!$B$3:$D$445,2,FALSE)&D827&\"_\"&VLOOKUP(E827,List!$K$2:$M$447,2,FALSE)","v":"LEAFB3X00_C"},"LEAFB3X00_C AT%M1364.0 :BOOL; (*排风机B3层启停控制*)","LEAFB3X00_C             AT%M1364.0     :BOOL; (*排风机B3层启停控制*)"]
["排风机","L","M","B2X00","启停控制","1366.0",null,"验证通过","BOOL","排风机B2层启停控制",{"$f":"B828&VLOOKUP(A828,List!$B$3:$D$445,2,FALSE)&D828&\"_\"&VLOOKUP(E828,List!$K$2:$M$447,2,FALSE)","v":"LEAFB2X00_C"},"LEAFB2X00_C AT%M1366.0 :BOOL; (*排风机B2层启停控制*)","LEAFB2X00_C             AT%M1366.0     :BOOL; (*排风机B2层启停控制*)"]
["排风机","L","M","B1X00","启停控制","1368.0",null,"验证通过","BOOL","排风机B1层启停控制",{"$f":"B829&VLOOKUP(A829,List!$B$3:$D$445,2,FALSE)&D829&\"_\"&VLOOKUP(E829,List!$K$2:$M$447,2,FALSE)","v":"LEAFB1X00_C"},"LEAFB1X00_C AT%M1368.0 :BOOL; (*排风机B1层启停控制*)","LEAFB1X00_C             AT%M1368.0     :BOOL; (*排风机B1层启停控制*)"]
["排风机","L","M","05X00","启停控制","1370.0",null,"验证通过","BOOL","排风机5层启停控制",{"$f":"B830&VLOOKUP(A830,List!$B$3:$D$445,2,FALSE)&D830&\"_\"&VLOOKUP(E830,List!$K$2:$M$447,2,FALSE)","v":"LEAF05X00_C"},"LEAF05X00_C AT%M1370.0 :BOOL; (*排风机5层启停控制*)","LEAF05X00_C             AT%M1370.0     :BOOL; (*排风机5层启停控制*)"]
["排风机","L","M","06X00","启停控制","1372.0",null,"验证通过","BOOL","排风机6层启停控制",{"$f":"B831&VLOOKUP(A831,List!$B$3:$D$445,2,FALSE)&D831&\"_\"&VLOOKUP(E831,List!$K$2:$M$447,2,FALSE)","v":"LEAF06X00_C"},"LEAF06X00_C AT%M1372.0 :BOOL; (*排风机6层启停控制*)","LEAF06X00_C             AT%M1372.0     :BOOL; (*排风机6层启停控制*)"]
["排风机","L","M","07X00","启停控制","1374.0",null,"验证通过","BOOL","排风机7层启停控制",{"$f":"B832&VLOOKUP(A832,List!$B$3:$D$445,2,FALSE)&D832&\"_\"&VLOOKUP(E832,List!$K$2:$M$447,2,FALSE)","v":"LEAF07X00_C"},"LEAF07X00_C AT%M1374.0 :BOOL; (*排风机7层启停控制*)","LEAF07X00_C             AT%M1374.0     :BOOL; (*排风机7层启停控制*)"]
["排风机","L","M","08X00","启停控制","1376.0",null,"验证通过","BOOL","排风机8层启停控制",{"$f":"B833&VLOOKUP(A833,List!$B$3:$D$445,2,FALSE)&D833&\"_\"&VLOOKUP(E833,List!$K$2:$M$447,2,FALSE)","v":"LEAF08X00_C"},"LEAF08X00_C AT%M1376.0 :BOOL; (*排风机8层启停控制*)","LEAF08X00_C             AT%M1376.0     :BOOL; (*排风机8层启停控制*)"]
["排风机","L","M","09X00","启停控制","1378.0",null,"验证通过","BOOL","排风机9层启停控制",{"$f":"B834&VLOOKUP(A834,List!$B$3:$D$445,2,FALSE)&D834&\"_\"&VLOOKUP(E834,List!$K$2:$M$447,2,FALSE)","v":"LEAF09X00_C"},"LEAF09X00_C AT%M1378.0 :BOOL; (*排风机9层启停控制*)","LEAF09X00_C             AT%M1378.0     :BOOL; (*排风机9层启停控制*)"]
["送风机","R","M","B3X00","启停控制","1380.0",null,{"$f":"IF((IF(OR(I835=\"INT\",I835=\"WORD\",I835=\"BOOL\"),MOD(F835,2),MOD(F835,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","送风机B3层启停控制",{"$f":"B835&VLOOKUP(A835,List!$B$3:$D$445,2,FALSE)&D835&\"_\"&VLOOKUP(E835,List!$K$2:$M$447,2,FALSE)","v":"RSAFB3X00_C"},{"$f":"K835&\" \"&\"AT%\"&C835&F835&\" \"&\":\"&I835&\";\"&\" \"&\"(*\"&J835&\"*)\"","v":"RSAFB3X00_C AT%M1380.0 :BOOL; (*送风机B3层启停控制*)"},{"$f":"REPLACE(REPLACE(L835,SEARCH(\"AT%\",L835),,REPT(\" \",25-SEARCH(\"AT%\",L835))),SEARCH(\":\",REPLACE(L835,SEARCH(\"AT%\",L835),,REPT(\" \",25-SEARCH(\"AT%\",L835)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L835,SEARCH(\"AT%\",L835),,REPT(\" \",25-SEARCH(\"AT%\",L835))))))","v":"RSAFB3X00_C             AT%M1380.0     :BOOL; (*送风机B3层启停控制*)"}]
["送风机","R","M","B2X00","启停控制","1382.0",null,"验证通过","BOOL","送风机B2层启停控制",{"$f":"B836&VLOOKUP(A836,List!$B$3:$D$445,2,FALSE)&D836&\"_\"&VLOOKUP(E836,List!$K$2:$M$447,2,FALSE)","v":"RSAFB2X00_C"},"RSAFB2X00_C AT%M1382.0 :BOOL; (*送风机B2层启停控制*)","RSAFB2X00_C             AT%M1382.0     :BOOL; (*送风机B2层启停控制*)"]
["送风机","R","M","B1X00","启停控制","1384.0",null,"验证通过","BOOL","送风机B1层启停控制",{"$f":"B837&VLOOKUP(A837,List!$B$3:$D$445,2,FALSE)&D837&\"_\"&VLOOKUP(E837,List!$K$2:$M$447,2,FALSE)","v":"RSAFB1X00_C"},"RSAFB1X00_C AT%M1384.0 :BOOL; (*送风机B1层启停控制*)","RSAFB1X00_C             AT%M1384.0     :BOOL; (*送风机B1层启停控制*)"]
["送风机","R","M","05X00","启停控制","1386.0",null,"验证通过","BOOL","送风机5层启停控制",{"$f":"B838&VLOOKUP(A838,List!$B$3:$D$445,2,FALSE)&D838&\"_\"&VLOOKUP(E838,List!$K$2:$M$447,2,FALSE)","v":"RSAF05X00_C"},"RSAF05X00_C AT%M1386.0 :BOOL; (*送风机5层启停控制*)","RSAF05X00_C             AT%M1386.0     :BOOL; (*送风机5层启停控制*)"]
["送风机","R","M","06X00","启停控制","1388.0",null,"验证通过","BOOL","送风机6层启停控制",{"$f":"B839&VLOOKUP(A839,List!$B$3:$D$445,2,FALSE)&D839&\"_\"&VLOOKUP(E839,List!$K$2:$M$447,2,FALSE)","v":"RSAF06X00_C"},"RSAF06X00_C AT%M1388.0 :BOOL; (*送风机6层启停控制*)","RSAF06X00_C             AT%M1388.0     :BOOL; (*送风机6层启停控制*)"]
["送风机","R","M","07X00","启停控制","1390.0",null,"验证通过","BOOL","送风机7层启停控制",{"$f":"B840&VLOOKUP(A840,List!$B$3:$D$445,2,FALSE)&D840&\"_\"&VLOOKUP(E840,List!$K$2:$M$447,2,FALSE)","v":"RSAF07X00_C"},"RSAF07X00_C AT%M1390.0 :BOOL; (*送风机7层启停控制*)","RSAF07X00_C             AT%M1390.0     :BOOL; (*送风机7层启停控制*)"]
["送风机","R","M","08X00","启停控制","1392.0",null,"验证通过","BOOL","送风机8层启停控制",{"$f":"B841&VLOOKUP(A841,List!$B$3:$D$445,2,FALSE)&D841&\"_\"&VLOOKUP(E841,List!$K$2:$M$447,2,FALSE)","v":"RSAF08X00_C"},"RSAF08X00_C AT%M1392.0 :BOOL; (*送风机8层启停控制*)","RSAF08X00_C             AT%M1392.0     :BOOL; (*送风机8层启停控制*)"]
["送风机","R","M","09X00","启停控制","1394.0",null,"验证通过","BOOL","送风机9层启停控制",{"$f":"B842&VLOOKUP(A842,List!$B$3:$D$445,2,FALSE)&D842&\"_\"&VLOOKUP(E842,List!$K$2:$M$447,2,FALSE)","v":"RSAF09X00_C"},"RSAF09X00_C AT%M1394.0 :BOOL; (*送风机9层启停控制*)","RSAF09X00_C             AT%M1394.0     :BOOL; (*送风机9层启停控制*)"]
["排风机","R","M","B3X00","启停控制","1396.0",null,"验证通过","BOOL","排风机B3层启停控制",{"$f":"B843&VLOOKUP(A843,List!$B$3:$D$445,2,FALSE)&D843&\"_\"&VLOOKUP(E843,List!$K$2:$M$447,2,FALSE)","v":"REAFB3X00_C"},"REAFB3X00_C AT%M1396.0 :BOOL; (*排风机B3层启停控制*)","REAFB3X00_C             AT%M1396.0     :BOOL; (*排风机B3层启停控制*)"]
["排风机","R","M","B2X00","启停控制","1398.0",null,"验证通过","BOOL","排风机B2层启停控制",{"$f":"B844&VLOOKUP(A844,List!$B$3:$D$445,2,FALSE)&D844&\"_\"&VLOOKUP(E844,List!$K$2:$M$447,2,FALSE)","v":"REAFB2X00_C"},"REAFB2X00_C AT%M1398.0 :BOOL; (*排风机B2层启停控制*)","REAFB2X00_C             AT%M1398.0     :BOOL; (*排风机B2层启停控制*)"]
["排风机","R","M","B1X00","启停控制","1400.0",null,"验证通过","BOOL","排风机B1层启停控制",{"$f":"B845&VLOOKUP(A845,List!$B$3:$D$445,2,FALSE)&D845&\"_\"&VLOOKUP(E845,List!$K$2:$M$447,2,FALSE)","v":"REAFB1X00_C"},"REAFB1X00_C AT%M1400.0 :BOOL; (*排风机B1层启停控制*)","REAFB1X00_C             AT%M1400.0     :BOOL; (*排风机B1层启停控制*)"]
["排风机","R","M","05X00","启停控制","1402.0",null,"验证通过","BOOL","排风机5层启停控制",{"$f":"B846&VLOOKUP(A846,List!$B$3:$D$445,2,FALSE)&D846&\"_\"&VLOOKUP(E846,List!$K$2:$M$447,2,FALSE)","v":"REAF05X00_C"},"REAF05X00_C AT%M1402.0 :BOOL; (*排风机5层启停控制*)","REAF05X00_C             AT%M1402.0     :BOOL; (*排风机5层启停控制*)"]
["排风机","R","M","06X00","启停控制","1404.0",null,"验证通过","BOOL","排风机6层启停控制",{"$f":"B847&VLOOKUP(A847,List!$B$3:$D$445,2,FALSE)&D847&\"_\"&VLOOKUP(E847,List!$K$2:$M$447,2,FALSE)","v":"REAF06X00_C"},"REAF06X00_C AT%M1404.0 :BOOL; (*排风机6层启停控制*)","REAF06X00_C             AT%M1404.0     :BOOL; (*排风机6层启停控制*)"]
["排风机","R","M","07X00","启停控制","1406.0",null,"验证通过","BOOL","排风机7层启停控制",{"$f":"B848&VLOOKUP(A848,List!$B$3:$D$445,2,FALSE)&D848&\"_\"&VLOOKUP(E848,List!$K$2:$M$447,2,FALSE)","v":"REAF07X00_C"},"REAF07X00_C AT%M1406.0 :BOOL; (*排风机7层启停控制*)","REAF07X00_C             AT%M1406.0     :BOOL; (*排风机7层启停控制*)"]
["排风机","R","M","08X00","启停控制","1408.0",null,"验证通过","BOOL","排风机8层启停控制",{"$f":"B849&VLOOKUP(A849,List!$B$3:$D$445,2,FALSE)&D849&\"_\"&VLOOKUP(E849,List!$K$2:$M$447,2,FALSE)","v":"REAF08X00_C"},"REAF08X00_C AT%M1408.0 :BOOL; (*排风机8层启停控制*)","REAF08X00_C             AT%M1408.0     :BOOL; (*排风机8层启停控制*)"]
["排风机","R","M","09X00","启停控制","1410.0",null,"验证通过","BOOL","排风机9层启停控制",{"$f":"B850&VLOOKUP(A850,List!$B$3:$D$445,2,FALSE)&D850&\"_\"&VLOOKUP(E850,List!$K$2:$M$447,2,FALSE)","v":"REAF09X00_C"},"REAF09X00_C AT%M1410.0 :BOOL; (*排风机9层启停控制*)","REAF09X00_C             AT%M1410.0     :BOOL; (*排风机9层启停控制*)"]
["风幕机","L","M","B3X00","启停控制","1412.0",null,"验证通过","BOOL","风幕机B3层启停控制",{"$f":"B851&VLOOKUP(A851,List!$B$3:$D$445,2,FALSE)&D851&\"_\"&VLOOKUP(E851,List!$K$2:$M$447,2,FALSE)","v":"LACB3X00_C"},"LACB3X00_C AT%M1412.0 :BOOL; (*风幕机B3层启停控制*)","LACB3X00_C              AT%M1412.0     :BOOL; (*风幕机B3层启停控制*)"]
["风幕机","L","M","B2X00","启停控制",{"$f":"IF(OR(I851=\"REAL\",I851=\"DWORD\",I851=\"DINT\"),(IF(OR(I852=\"REAL\",I852=\"DWORD\",I852=\"DINT\"),F851+4+MOD(F851,4),F851+4)),(IF(OR(I852=\"REAL\",I852=\"DWORD\",I852=\"DINT\"),F851+4+MOD(F851,4),F851+2)))&\".0\"","v":"1414.0"},null,"验证通过","BOOL","风幕机B2层启停控制",{"$f":"B852&VLOOKUP(A852,List!$B$3:$D$445,2,FALSE)&D852&\"_\"&VLOOKUP(E852,List!$K$2:$M$447,2,FALSE)","v":"LACB2X00_C"},"LACB2X00_C AT%M1414.0 :BOOL; (*风幕机B2层启停控制*)","LACB2X00_C              AT%M1414.0     :BOOL; (*风幕机B2层启停控制*)"]
["风幕机","L","M","B1X00","启停控制","1416.0",null,"验证通过","BOOL","风幕机B1层启停控制",{"$f":"B853&VLOOKUP(A853,List!$B$3:$D$445,2,FALSE)&D853&\"_\"&VLOOKUP(E853,List!$K$2:$M$447,2,FALSE)","v":"LACB1X00_C"},"LACB1X00_C AT%M1416.0 :BOOL; (*风幕机B1层启停控制*)","LACB1X00_C              AT%M1416.0     :BOOL; (*风幕机B1层启停控制*)"]
["风幕机","L","M","01X00","启停控制","1418.0",null,"验证通过","BOOL","风幕机1层启停控制",{"$f":"B854&VLOOKUP(A854,List!$B$3:$D$445,2,FALSE)&D854&\"_\"&VLOOKUP(E854,List!$K$2:$M$447,2,FALSE)","v":"LAC01X00_C"},"LAC01X00_C AT%M1418.0 :BOOL; (*风幕机1层启停控制*)","LAC01X00_C              AT%M1418.0     :BOOL; (*风幕机1层启停控制*)"]
["风幕机","L","M","02X00","启停控制","1420.0",null,"验证通过","BOOL","风幕机2层启停控制",{"$f":"B855&VLOOKUP(A855,List!$B$3:$D$445,2,FALSE)&D855&\"_\"&VLOOKUP(E855,List!$K$2:$M$447,2,FALSE)","v":"LAC02X00_C"},"LAC02X00_C AT%M1420.0 :BOOL; (*风幕机2层启停控制*)","LAC02X00_C              AT%M1420.0     :BOOL; (*风幕机2层启停控制*)"]
["风幕机","L","M","03X00","启停控制","1422.0",null,"验证通过","BOOL","风幕机3层启停控制",{"$f":"B856&VLOOKUP(A856,List!$B$3:$D$445,2,FALSE)&D856&\"_\"&VLOOKUP(E856,List!$K$2:$M$447,2,FALSE)","v":"LAC03X00_C"},"LAC03X00_C AT%M1422.0 :BOOL; (*风幕机3层启停控制*)","LAC03X00_C              AT%M1422.0     :BOOL; (*风幕机3层启停控制*)"]
["风幕机","L","M","04X00","启停控制","1424.0",null,"验证通过","BOOL","风幕机4层启停控制",{"$f":"B857&VLOOKUP(A857,List!$B$3:$D$445,2,FALSE)&D857&\"_\"&VLOOKUP(E857,List!$K$2:$M$447,2,FALSE)","v":"LAC04X00_C"},"LAC04X00_C AT%M1424.0 :BOOL; (*风幕机4层启停控制*)","LAC04X00_C              AT%M1424.0     :BOOL; (*风幕机4层启停控制*)"]
["风幕机","L","M","05X00","启停控制","1426.0",null,"验证通过","BOOL","风幕机5层启停控制",{"$f":"B858&VLOOKUP(A858,List!$B$3:$D$445,2,FALSE)&D858&\"_\"&VLOOKUP(E858,List!$K$2:$M$447,2,FALSE)","v":"LAC05X00_C"},"LAC05X00_C AT%M1426.0 :BOOL; (*风幕机5层启停控制*)","LAC05X00_C              AT%M1426.0     :BOOL; (*风幕机5层启停控制*)"]
["风幕机","L","M","06X00","启停控制","1428.0",null,"验证通过","BOOL","风幕机6层启停控制",{"$f":"B859&VLOOKUP(A859,List!$B$3:$D$445,2,FALSE)&D859&\"_\"&VLOOKUP(E859,List!$K$2:$M$447,2,FALSE)","v":"LAC06X00_C"},"LAC06X00_C AT%M1428.0 :BOOL; (*风幕机6层启停控制*)","LAC06X00_C              AT%M1428.0     :BOOL; (*风幕机6层启停控制*)"]
["风幕机","L","M","07X00","启停控制","1430.0",null,"验证通过","BOOL","风幕机7层启停控制",{"$f":"B860&VLOOKUP(A860,List!$B$3:$D$445,2,FALSE)&D860&\"_\"&VLOOKUP(E860,List!$K$2:$M$447,2,FALSE)","v":"LAC07X00_C"},"LAC07X00_C AT%M1430.0 :BOOL; (*风幕机7层启停控制*)","LAC07X00_C              AT%M1430.0     :BOOL; (*风幕机7层启停控制*)"]
["风幕机","L","M","08X00","启停控制","1432.0",null,"验证通过","BOOL","风幕机8层启停控制",{"$f":"B861&VLOOKUP(A861,List!$B$3:$D$445,2,FALSE)&D861&\"_\"&VLOOKUP(E861,List!$K$2:$M$447,2,FALSE)","v":"LAC08X00_C"},"LAC08X00_C AT%M1432.0 :BOOL; (*风幕机8层启停控制*)","LAC08X00_C              AT%M1432.0     :BOOL; (*风幕机8层启停控制*)"]
["水幕机","L","M","B3X00","启停控制","1434.0",null,"验证通过","BOOL","水幕机B3层启停控制",{"$f":"B862&VLOOKUP(A862,List!$B$3:$D$445,2,FALSE)&D862&\"_\"&VLOOKUP(E862,List!$K$2:$M$447,2,FALSE)","v":"LWACB3X00_C"},"LWACB3X00_C AT%M1434.0 :BOOL; (*水幕机B3层启停控制*)","LWACB3X00_C             AT%M1434.0     :BOOL; (*水幕机B3层启停控制*)"]
["水幕机","L","M","B2X00","启停控制","1436.0",null,"验证通过","BOOL","水幕机B2层启停控制",{"$f":"B863&VLOOKUP(A863,List!$B$3:$D$445,2,FALSE)&D863&\"_\"&VLOOKUP(E863,List!$K$2:$M$447,2,FALSE)","v":"LWACB2X00_C"},"LWACB2X00_C AT%M1436.0 :BOOL; (*水幕机B2层启停控制*)","LWACB2X00_C             AT%M1436.0     :BOOL; (*水幕机B2层启停控制*)"]
["水幕机","L","M","B1X00","启停控制","1438.0",null,"验证通过","BOOL","水幕机B1层启停控制",{"$f":"B864&VLOOKUP(A864,List!$B$3:$D$445,2,FALSE)&D864&\"_\"&VLOOKUP(E864,List!$K$2:$M$447,2,FALSE)","v":"LWACB1X00_C"},"LWACB1X00_C AT%M1438.0 :BOOL; (*水幕机B1层启停控制*)","LWACB1X00_C             AT%M1438.0     :BOOL; (*水幕机B1层启停控制*)"]
["水幕机","L","M","01X00","启停控制","1440.0",null,"验证通过","BOOL","水幕机1层启停控制",{"$f":"B865&VLOOKUP(A865,List!$B$3:$D$445,2,FALSE)&D865&\"_\"&VLOOKUP(E865,List!$K$2:$M$447,2,FALSE)","v":"LWAC01X00_C"},"LWAC01X00_C AT%M1440.0 :BOOL; (*水幕机1层启停控制*)","LWAC01X00_C             AT%M1440.0     :BOOL; (*水幕机1层启停控制*)"]
["水幕机","L","M","02X00","启停控制","1442.0",null,"验证通过","BOOL","水幕机2层启停控制",{"$f":"B866&VLOOKUP(A866,List!$B$3:$D$445,2,FALSE)&D866&\"_\"&VLOOKUP(E866,List!$K$2:$M$447,2,FALSE)","v":"LWAC02X00_C"},"LWAC02X00_C AT%M1442.0 :BOOL; (*水幕机2层启停控制*)","LWAC02X00_C             AT%M1442.0     :BOOL; (*水幕机2层启停控制*)"]
["水幕机","L","M","03X00","启停控制","1444.0",null,"验证通过","BOOL","水幕机3层启停控制",{"$f":"B867&VLOOKUP(A867,List!$B$3:$D$445,2,FALSE)&D867&\"_\"&VLOOKUP(E867,List!$K$2:$M$447,2,FALSE)","v":"LWAC03X00_C"},"LWAC03X00_C AT%M1444.0 :BOOL; (*水幕机3层启停控制*)","LWAC03X00_C             AT%M1444.0     :BOOL; (*水幕机3层启停控制*)"]
["水幕机","L","M","04X00","启停控制","1446.0",null,"验证通过","BOOL","水幕机4层启停控制",{"$f":"B868&VLOOKUP(A868,List!$B$3:$D$445,2,FALSE)&D868&\"_\"&VLOOKUP(E868,List!$K$2:$M$447,2,FALSE)","v":"LWAC04X00_C"},"LWAC04X00_C AT%M1446.0 :BOOL; (*水幕机4层启停控制*)","LWAC04X00_C             AT%M1446.0     :BOOL; (*水幕机4层启停控制*)"]
["水幕机","L","M","05X00","启停控制","1448.0",null,"验证通过","BOOL","水幕机5层启停控制",{"$f":"B869&VLOOKUP(A869,List!$B$3:$D$445,2,FALSE)&D869&\"_\"&VLOOKUP(E869,List!$K$2:$M$447,2,FALSE)","v":"LWAC05X00_C"},"LWAC05X00_C AT%M1448.0 :BOOL; (*水幕机5层启停控制*)","LWAC05X00_C             AT%M1448.0     :BOOL; (*水幕机5层启停控制*)"]
["水幕机","L","M","06X00","启停控制","1450.0",null,"验证通过","BOOL","水幕机6层启停控制",{"$f":"B870&VLOOKUP(A870,List!$B$3:$D$445,2,FALSE)&D870&\"_\"&VLOOKUP(E870,List!$K$2:$M$447,2,FALSE)","v":"LWAC06X00_C"},"LWAC06X00_C AT%M1450.0 :BOOL; (*水幕机6层启停控制*)","LWAC06X00_C             AT%M1450.0     :BOOL; (*水幕机6层启停控制*)"]
["水幕机","L","M","07X00","启停控制","1452.0",null,"验证通过","BOOL","水幕机7层启停控制",{"$f":"B871&VLOOKUP(A871,List!$B$3:$D$445,2,FALSE)&D871&\"_\"&VLOOKUP(E871,List!$K$2:$M$447,2,FALSE)","v":"LWAC07X00_C"},"LWAC07X00_C AT%M1452.0 :BOOL; (*水幕机7层启停控制*)","LWAC07X00_C             AT%M1452.0     :BOOL; (*水幕机7层启停控制*)"]
["水幕机","L","M","08X00","启停控制","1454.0",null,"验证通过","BOOL","水幕机8层启停控制",{"$f":"B872&VLOOKUP(A872,List!$B$3:$D$445,2,FALSE)&D872&\"_\"&VLOOKUP(E872,List!$K$2:$M$447,2,FALSE)","v":"LWAC08X00_C"},"LWAC08X00_C AT%M1454.0 :BOOL; (*水幕机8层启停控制*)","LWAC08X00_C             AT%M1454.0     :BOOL; (*水幕机8层启停控制*)"]
["风幕机","R","M","B3X00","启停控制","1456.0",null,{"$f":"IF((IF(OR(I873=\"INT\",I873=\"WORD\",I873=\"BOOL\"),MOD(F873,2),MOD(F873,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","风幕机B3层启停控制",{"$f":"B873&VLOOKUP(A873,List!$B$3:$D$445,2,FALSE)&D873&\"_\"&VLOOKUP(E873,List!$K$2:$M$447,2,FALSE)","v":"RACB3X00_C"},{"$f":"K873&\" \"&\"AT%\"&C873&F873&\" \"&\":\"&I873&\";\"&\" \"&\"(*\"&J873&\"*)\"","v":"RACB3X00_C AT%M1456.0 :BOOL; (*风幕机B3层启停控制*)"},{"$f":"REPLACE(REPLACE(L873,SEARCH(\"AT%\",L873),,REPT(\" \",25-SEARCH(\"AT%\",L873))),SEARCH(\":\",REPLACE(L873,SEARCH(\"AT%\",L873),,REPT(\" \",25-SEARCH(\"AT%\",L873)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L873,SEARCH(\"AT%\",L873),,REPT(\" \",25-SEARCH(\"AT%\",L873))))))","v":"RACB3X00_C              AT%M1456.0     :BOOL; (*风幕机B3层启停控制*)"}]
["风幕机","R","M","B2X00","启停控制","1458.0",null,"验证通过","BOOL","风幕机B2层启停控制",{"$f":"B874&VLOOKUP(A874,List!$B$3:$D$445,2,FALSE)&D874&\"_\"&VLOOKUP(E874,List!$K$2:$M$447,2,FALSE)","v":"RACB2X00_C"},"RACB2X00_C AT%M1458.0 :BOOL; (*风幕机B2层启停控制*)","RACB2X00_C              AT%M1458.0     :BOOL; (*风幕机B2层启停控制*)"]
["风幕机","R","M","B1X00","启停控制","1460.0",null,"验证通过","BOOL","风幕机B1层启停控制",{"$f":"B875&VLOOKUP(A875,List!$B$3:$D$445,2,FALSE)&D875&\"_\"&VLOOKUP(E875,List!$K$2:$M$447,2,FALSE)","v":"RACB1X00_C"},"RACB1X00_C AT%M1460.0 :BOOL; (*风幕机B1层启停控制*)","RACB1X00_C              AT%M1460.0     :BOOL; (*风幕机B1层启停控制*)"]
["风幕机","R","M","01X00","启停控制","1462.0",null,"验证通过","BOOL","风幕机1层启停控制",{"$f":"B876&VLOOKUP(A876,List!$B$3:$D$445,2,FALSE)&D876&\"_\"&VLOOKUP(E876,List!$K$2:$M$447,2,FALSE)","v":"RAC01X00_C"},"RAC01X00_C AT%M1462.0 :BOOL; (*风幕机1层启停控制*)","RAC01X00_C              AT%M1462.0     :BOOL; (*风幕机1层启停控制*)"]
["风幕机","R","M","02X00","启停控制","1464.0",null,"验证通过","BOOL","风幕机2层启停控制",{"$f":"B877&VLOOKUP(A877,List!$B$3:$D$445,2,FALSE)&D877&\"_\"&VLOOKUP(E877,List!$K$2:$M$447,2,FALSE)","v":"RAC02X00_C"},"RAC02X00_C AT%M1464.0 :BOOL; (*风幕机2层启停控制*)","RAC02X00_C              AT%M1464.0     :BOOL; (*风幕机2层启停控制*)"]
["风幕机","R","M","03X00","启停控制","1466.0",null,"验证通过","BOOL","风幕机3层启停控制",{"$f":"B878&VLOOKUP(A878,List!$B$3:$D$445,2,FALSE)&D878&\"_\"&VLOOKUP(E878,List!$K$2:$M$447,2,FALSE)","v":"RAC03X00_C"},"RAC03X00_C AT%M1466.0 :BOOL; (*风幕机3层启停控制*)","RAC03X00_C              AT%M1466.0     :BOOL; (*风幕机3层启停控制*)"]
["风幕机","R","M","04X00","启停控制","1468.0",null,"验证通过","BOOL","风幕机4层启停控制",{"$f":"B879&VLOOKUP(A879,List!$B$3:$D$445,2,FALSE)&D879&\"_\"&VLOOKUP(E879,List!$K$2:$M$447,2,FALSE)","v":"RAC04X00_C"},"RAC04X00_C AT%M1468.0 :BOOL; (*风幕机4层启停控制*)","RAC04X00_C              AT%M1468.0     :BOOL; (*风幕机4层启停控制*)"]
["风幕机","R","M","05X00","启停控制","1470.0",null,"验证通过","BOOL","风幕机5层启停控制",{"$f":"B880&VLOOKUP(A880,List!$B$3:$D$445,2,FALSE)&D880&\"_\"&VLOOKUP(E880,List!$K$2:$M$447,2,FALSE)","v":"RAC05X00_C"},"RAC05X00_C AT%M1470.0 :BOOL; (*风幕机5层启停控制*)","RAC05X00_C              AT%M1470.0     :BOOL; (*风幕机5层启停控制*)"]
["风幕机","R","M","06X00","启停控制","1472.0",null,"验证通过","BOOL","风幕机6层启停控制",{"$f":"B881&VLOOKUP(A881,List!$B$3:$D$445,2,FALSE)&D881&\"_\"&VLOOKUP(E881,List!$K$2:$M$447,2,FALSE)","v":"RAC06X00_C"},"RAC06X00_C AT%M1472.0 :BOOL; (*风幕机6层启停控制*)","RAC06X00_C              AT%M1472.0     :BOOL; (*风幕机6层启停控制*)"]
["风幕机","R","M","07X00","启停控制","1474.0",null,"验证通过","BOOL","风幕机7层启停控制",{"$f":"B882&VLOOKUP(A882,List!$B$3:$D$445,2,FALSE)&D882&\"_\"&VLOOKUP(E882,List!$K$2:$M$447,2,FALSE)","v":"RAC07X00_C"},"RAC07X00_C AT%M1474.0 :BOOL; (*风幕机7层启停控制*)","RAC07X00_C              AT%M1474.0     :BOOL; (*风幕机7层启停控制*)"]
["风幕机","R","M","08X00","启停控制","1476.0",null,"验证通过","BOOL","风幕机8层启停控制",{"$f":"B883&VLOOKUP(A883,List!$B$3:$D$445,2,FALSE)&D883&\"_\"&VLOOKUP(E883,List!$K$2:$M$447,2,FALSE)","v":"RAC08X00_C"},"RAC08X00_C AT%M1476.0 :BOOL; (*风幕机8层启停控制*)","RAC08X00_C              AT%M1476.0     :BOOL; (*风幕机8层启停控制*)"]
["水幕机","R","M","B3X00","启停控制","1478.0",null,"验证通过","BOOL","水幕机B3层启停控制",{"$f":"B884&VLOOKUP(A884,List!$B$3:$D$445,2,FALSE)&D884&\"_\"&VLOOKUP(E884,List!$K$2:$M$447,2,FALSE)","v":"RWACB3X00_C"},"RWACB3X00_C AT%M1478.0 :BOOL; (*水幕机B3层启停控制*)","RWACB3X00_C             AT%M1478.0     :BOOL; (*水幕机B3层启停控制*)"]
["水幕机","R","M","B2X00","启停控制","1480.0",null,"验证通过","BOOL","水幕机B2层启停控制",{"$f":"B885&VLOOKUP(A885,List!$B$3:$D$445,2,FALSE)&D885&\"_\"&VLOOKUP(E885,List!$K$2:$M$447,2,FALSE)","v":"RWACB2X00_C"},"RWACB2X00_C AT%M1480.0 :BOOL; (*水幕机B2层启停控制*)","RWACB2X00_C             AT%M1480.0     :BOOL; (*水幕机B2层启停控制*)"]
["水幕机","R","M","B1X00","启停控制","1482.0",null,"验证通过","BOOL","水幕机B1层启停控制",{"$f":"B886&VLOOKUP(A886,List!$B$3:$D$445,2,FALSE)&D886&\"_\"&VLOOKUP(E886,List!$K$2:$M$447,2,FALSE)","v":"RWACB1X00_C"},"RWACB1X00_C AT%M1482.0 :BOOL; (*水幕机B1层启停控制*)","RWACB1X00_C             AT%M1482.0     :BOOL; (*水幕机B1层启停控制*)"]
["水幕机","R","M","01X00","启停控制","1484.0",null,"验证通过","BOOL","水幕机1层启停控制",{"$f":"B887&VLOOKUP(A887,List!$B$3:$D$445,2,FALSE)&D887&\"_\"&VLOOKUP(E887,List!$K$2:$M$447,2,FALSE)","v":"RWAC01X00_C"},"RWAC01X00_C AT%M1484.0 :BOOL; (*水幕机1层启停控制*)","RWAC01X00_C             AT%M1484.0     :BOOL; (*水幕机1层启停控制*)"]
["水幕机","R","M","02X00","启停控制","1486.0",null,"验证通过","BOOL","水幕机2层启停控制",{"$f":"B888&VLOOKUP(A888,List!$B$3:$D$445,2,FALSE)&D888&\"_\"&VLOOKUP(E888,List!$K$2:$M$447,2,FALSE)","v":"RWAC02X00_C"},"RWAC02X00_C AT%M1486.0 :BOOL; (*水幕机2层启停控制*)","RWAC02X00_C             AT%M1486.0     :BOOL; (*水幕机2层启停控制*)"]
["水幕机","R","M","03X00","启停控制","1488.0",null,"验证通过","BOOL","水幕机3层启停控制",{"$f":"B889&VLOOKUP(A889,List!$B$3:$D$445,2,FALSE)&D889&\"_\"&VLOOKUP(E889,List!$K$2:$M$447,2,FALSE)","v":"RWAC03X00_C"},"RWAC03X00_C AT%M1488.0 :BOOL; (*水幕机3层启停控制*)","RWAC03X00_C             AT%M1488.0     :BOOL; (*水幕机3层启停控制*)"]
["水幕机","R","M","04X00","启停控制","1490.0",null,"验证通过","BOOL","水幕机4层启停控制",{"$f":"B890&VLOOKUP(A890,List!$B$3:$D$445,2,FALSE)&D890&\"_\"&VLOOKUP(E890,List!$K$2:$M$447,2,FALSE)","v":"RWAC04X00_C"},"RWAC04X00_C AT%M1490.0 :BOOL; (*水幕机4层启停控制*)","RWAC04X00_C             AT%M1490.0     :BOOL; (*水幕机4层启停控制*)"]
["水幕机","R","M","05X00","启停控制","1492.0",null,"验证通过","BOOL","水幕机5层启停控制",{"$f":"B891&VLOOKUP(A891,List!$B$3:$D$445,2,FALSE)&D891&\"_\"&VLOOKUP(E891,List!$K$2:$M$447,2,FALSE)","v":"RWAC05X00_C"},"RWAC05X00_C AT%M1492.0 :BOOL; (*水幕机5层启停控制*)","RWAC05X00_C             AT%M1492.0     :BOOL; (*水幕机5层启停控制*)"]
["水幕机","R","M","06X00","启停控制","1494.0",null,"验证通过","BOOL","水幕机6层启停控制",{"$f":"B892&VLOOKUP(A892,List!$B$3:$D$445,2,FALSE)&D892&\"_\"&VLOOKUP(E892,List!$K$2:$M$447,2,FALSE)","v":"RWAC06X00_C"},"RWAC06X00_C AT%M1494.0 :BOOL; (*水幕机6层启停控制*)","RWAC06X00_C             AT%M1494.0     :BOOL; (*水幕机6层启停控制*)"]
["水幕机","R","M","07X00","启停控制","1496.0",null,"验证通过","BOOL","水幕机7层启停控制",{"$f":"B893&VLOOKUP(A893,List!$B$3:$D$445,2,FALSE)&D893&\"_\"&VLOOKUP(E893,List!$K$2:$M$447,2,FALSE)","v":"RWAC07X00_C"},"RWAC07X00_C AT%M1496.0 :BOOL; (*水幕机7层启停控制*)","RWAC07X00_C             AT%M1496.0     :BOOL; (*水幕机7层启停控制*)"]
["水幕机","R","M","08X00","启停控制","1498.0",null,"验证通过","BOOL","水幕机8层启停控制",{"$f":"B894&VLOOKUP(A894,List!$B$3:$D$445,2,FALSE)&D894&\"_\"&VLOOKUP(E894,List!$K$2:$M$447,2,FALSE)","v":"RWAC08X00_C"},"RWAC08X00_C AT%M1498.0 :BOOL; (*水幕机8层启停控制*)","RWAC08X00_C             AT%M1498.0     :BOOL; (*水幕机8层启停控制*)"]
["风幕机","L","M","B3X00","定时控制","1500.0",null,"验证通过","BOOL",{"$f":"A895&D895&\"-\"&E895","v":"风幕机B3X00-定时控制"},{"$f":"B895&VLOOKUP(A895,List!$B$3:$D$445,2,FALSE)&D895&\"_\"&VLOOKUP(E895,List!$K$2:$M$447,2,FALSE)","v":"LACB3X00_TC"},{"$f":"K895&\" \"&\"AT%\"&C895&F895&\" \"&\":\"&I895&\";\"&\" \"&\"(*\"&J895&\"*)\"","v":"LACB3X00_TC AT%M1500.0 :BOOL; (*风幕机B3X00-定时控制*)"},{"$f":"REPLACE(REPLACE(L895,SEARCH(\"AT%\",L895),,REPT(\" \",25-SEARCH(\"AT%\",L895))),SEARCH(\":\",REPLACE(L895,SEARCH(\"AT%\",L895),,REPT(\" \",25-SEARCH(\"AT%\",L895)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L895,SEARCH(\"AT%\",L895),,REPT(\" \",25-SEARCH(\"AT%\",L895))))))","v":"LACB3X00_TC             AT%M1500.0     :BOOL; (*风幕机B3X00-定时控制*)"}]
["风幕机","L","M","B2X00","定时控制","1502.0",null,"验证通过","BOOL","风幕机B2X00-定时控制",{"$f":"B896&VLOOKUP(A896,List!$B$3:$D$445,2,FALSE)&D896&\"_\"&VLOOKUP(E896,List!$K$2:$M$447,2,FALSE)","v":"LACB2X00_TC"},"LACB2X00_TC AT%M1502.0 :BOOL; (*风幕机B2X00-定时控制*)","LACB2X00_TC             AT%M1502.0     :BOOL; (*风幕机B2X00-定时控制*)"]
["风幕机","L","M","B1X00","定时控制","1504.0",null,"验证通过","BOOL","风幕机B1X00-定时控制",{"$f":"B897&VLOOKUP(A897,List!$B$3:$D$445,2,FALSE)&D897&\"_\"&VLOOKUP(E897,List!$K$2:$M$447,2,FALSE)","v":"LACB1X00_TC"},"LACB1X00_TC AT%M1504.0 :BOOL; (*风幕机B1X00-定时控制*)","LACB1X00_TC             AT%M1504.0     :BOOL; (*风幕机B1X00-定时控制*)"]
["风幕机","L","M","01X00","定时控制","1506.0",null,"验证通过","BOOL","风幕机01X00-定时控制",{"$f":"B898&VLOOKUP(A898,List!$B$3:$D$445,2,FALSE)&D898&\"_\"&VLOOKUP(E898,List!$K$2:$M$447,2,FALSE)","v":"LAC01X00_TC"},"LAC01X00_TC AT%M1506.0 :BOOL; (*风幕机01X00-定时控制*)","LAC01X00_TC             AT%M1506.0     :BOOL; (*风幕机01X00-定时控制*)"]
["风幕机","L","M","02X00","定时控制","1508.0",null,{"$f":"IF((IF(OR(I899=\"INT\",I899=\"WORD\",I899=\"BOOL\"),MOD(F899,2),MOD(F899,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","风幕机02X00-定时控制",{"$f":"B899&VLOOKUP(A899,List!$B$3:$D$445,2,FALSE)&D899&\"_\"&VLOOKUP(E899,List!$K$2:$M$447,2,FALSE)","v":"LAC02X00_TC"},"LAC02X00_TC AT%M1508.0 :BOOL; (*风幕机02X00-定时控制*)","LAC02X00_TC             AT%M1508.0     :BOOL; (*风幕机02X00-定时控制*)"]
["风幕机","L","M","03X00","定时控制","1510.0",null,"验证通过","BOOL","风幕机03X00-定时控制",{"$f":"B900&VLOOKUP(A900,List!$B$3:$D$445,2,FALSE)&D900&\"_\"&VLOOKUP(E900,List!$K$2:$M$447,2,FALSE)","v":"LAC03X00_TC"},"LAC03X00_TC AT%M1510.0 :BOOL; (*风幕机03X00-定时控制*)","LAC03X00_TC             AT%M1510.0     :BOOL; (*风幕机03X00-定时控制*)"]
["风幕机","L","M","04X00","定时控制","1512.0",null,"验证通过","BOOL","风幕机04X00-定时控制",{"$f":"B901&VLOOKUP(A901,List!$B$3:$D$445,2,FALSE)&D901&\"_\"&VLOOKUP(E901,List!$K$2:$M$447,2,FALSE)","v":"LAC04X00_TC"},"LAC04X00_TC AT%M1512.0 :BOOL; (*风幕机04X00-定时控制*)","LAC04X00_TC             AT%M1512.0     :BOOL; (*风幕机04X00-定时控制*)"]
["风幕机","L","M","05X00","定时控制","1514.0",null,"验证通过","BOOL","风幕机05X00-定时控制",{"$f":"B902&VLOOKUP(A902,List!$B$3:$D$445,2,FALSE)&D902&\"_\"&VLOOKUP(E902,List!$K$2:$M$447,2,FALSE)","v":"LAC05X00_TC"},"LAC05X00_TC AT%M1514.0 :BOOL; (*风幕机05X00-定时控制*)","LAC05X00_TC             AT%M1514.0     :BOOL; (*风幕机05X00-定时控制*)"]
["风幕机","L","M","06X00","定时控制","1516.0",null,"验证通过","BOOL","风幕机06X00-定时控制",{"$f":"B903&VLOOKUP(A903,List!$B$3:$D$445,2,FALSE)&D903&\"_\"&VLOOKUP(E903,List!$K$2:$M$447,2,FALSE)","v":"LAC06X00_TC"},"LAC06X00_TC AT%M1516.0 :BOOL; (*风幕机06X00-定时控制*)","LAC06X00_TC             AT%M1516.0     :BOOL; (*风幕机06X00-定时控制*)"]
["风幕机","L","M","07X00","定时控制","1518.0",null,"验证通过","BOOL","风幕机07X00-定时控制",{"$f":"B904&VLOOKUP(A904,List!$B$3:$D$445,2,FALSE)&D904&\"_\"&VLOOKUP(E904,List!$K$2:$M$447,2,FALSE)","v":"LAC07X00_TC"},"LAC07X00_TC AT%M1518.0 :BOOL; (*风幕机07X00-定时控制*)","LAC07X00_TC             AT%M1518.0     :BOOL; (*风幕机07X00-定时控制*)"]
["风幕机","L","M","08X00","定时控制","1520.0",null,"验证通过","BOOL","风幕机08X00-定时控制",{"$f":"B905&VLOOKUP(A905,List!$B$3:$D$445,2,FALSE)&D905&\"_\"&VLOOKUP(E905,List!$K$2:$M$447,2,FALSE)","v":"LAC08X00_TC"},"LAC08X00_TC AT%M1520.0 :BOOL; (*风幕机08X00-定时控制*)","LAC08X00_TC             AT%M1520.0     :BOOL; (*风幕机08X00-定时控制*)"]
["风幕机","L","M","B3X00","定时模式","1522.0",null,"验证通过","BOOL","风幕机B3X00-定时模式",{"$f":"B906&VLOOKUP(A906,List!$B$3:$D$445,2,FALSE)&D906&\"_\"&VLOOKUP(E906,List!$K$2:$M$447,2,FALSE)","v":"LACB3X00_TM"},"LACB3X00_TM AT%M1522.0 :BOOL; (*风幕机B3X00-定时模式*)","LACB3X00_TM             AT%M1522.0     :BOOL; (*风幕机B3X00-定时模式*)"]
["风幕机","L","M","B2X00","定时模式","1524.0",null,"验证通过","BOOL","风幕机B2X00-定时模式",{"$f":"B907&VLOOKUP(A907,List!$B$3:$D$445,2,FALSE)&D907&\"_\"&VLOOKUP(E907,List!$K$2:$M$447,2,FALSE)","v":"LACB2X00_TM"},"LACB2X00_TM AT%M1524.0 :BOOL; (*风幕机B2X00-定时模式*)","LACB2X00_TM             AT%M1524.0     :BOOL; (*风幕机B2X00-定时模式*)"]
["风幕机","L","M","B1X00","定时模式","1526.0",null,"验证通过","BOOL","风幕机B1X00-定时模式",{"$f":"B908&VLOOKUP(A908,List!$B$3:$D$445,2,FALSE)&D908&\"_\"&VLOOKUP(E908,List!$K$2:$M$447,2,FALSE)","v":"LACB1X00_TM"},"LACB1X00_TM AT%M1526.0 :BOOL; (*风幕机B1X00-定时模式*)","LACB1X00_TM             AT%M1526.0     :BOOL; (*风幕机B1X00-定时模式*)"]
["风幕机","L","M","01X00","定时模式","1528.0",null,"验证通过","BOOL","风幕机01X00-定时模式",{"$f":"B909&VLOOKUP(A909,List!$B$3:$D$445,2,FALSE)&D909&\"_\"&VLOOKUP(E909,List!$K$2:$M$447,2,FALSE)","v":"LAC01X00_TM"},"LAC01X00_TM AT%M1528.0 :BOOL; (*风幕机01X00-定时模式*)","LAC01X00_TM             AT%M1528.0     :BOOL; (*风幕机01X00-定时模式*)"]
["风幕机","L","M","02X00","定时模式","1530.0",null,{"$f":"IF((IF(OR(I910=\"INT\",I910=\"WORD\",I910=\"BOOL\"),MOD(F910,2),MOD(F910,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","风幕机02X00-定时模式",{"$f":"B910&VLOOKUP(A910,List!$B$3:$D$445,2,FALSE)&D910&\"_\"&VLOOKUP(E910,List!$K$2:$M$447,2,FALSE)","v":"LAC02X00_TM"},"LAC02X00_TM AT%M1530.0 :BOOL; (*风幕机02X00-定时模式*)","LAC02X00_TM             AT%M1530.0     :BOOL; (*风幕机02X00-定时模式*)"]
["风幕机","L","M","03X00","定时模式","1532.0",null,"验证通过","BOOL","风幕机03X00-定时模式",{"$f":"B911&VLOOKUP(A911,List!$B$3:$D$445,2,FALSE)&D911&\"_\"&VLOOKUP(E911,List!$K$2:$M$447,2,FALSE)","v":"LAC03X00_TM"},"LAC03X00_TM AT%M1532.0 :BOOL; (*风幕机03X00-定时模式*)","LAC03X00_TM             AT%M1532.0     :BOOL; (*风幕机03X00-定时模式*)"]
["风幕机","L","M","04X00","定时模式","1534.0",null,"验证通过","BOOL","风幕机04X00-定时模式",{"$f":"B912&VLOOKUP(A912,List!$B$3:$D$445,2,FALSE)&D912&\"_\"&VLOOKUP(E912,List!$K$2:$M$447,2,FALSE)","v":"LAC04X00_TM"},"LAC04X00_TM AT%M1534.0 :BOOL; (*风幕机04X00-定时模式*)","LAC04X00_TM             AT%M1534.0     :BOOL; (*风幕机04X00-定时模式*)"]
["风幕机","L","M","05X00","定时模式","1536.0",null,"验证通过","BOOL","风幕机05X00-定时模式",{"$f":"B913&VLOOKUP(A913,List!$B$3:$D$445,2,FALSE)&D913&\"_\"&VLOOKUP(E913,List!$K$2:$M$447,2,FALSE)","v":"LAC05X00_TM"},"LAC05X00_TM AT%M1536.0 :BOOL; (*风幕机05X00-定时模式*)","LAC05X00_TM             AT%M1536.0     :BOOL; (*风幕机05X00-定时模式*)"]
["风幕机","L","M","06X00","定时模式","1538.0",null,"验证通过","BOOL","风幕机06X00-定时模式",{"$f":"B914&VLOOKUP(A914,List!$B$3:$D$445,2,FALSE)&D914&\"_\"&VLOOKUP(E914,List!$K$2:$M$447,2,FALSE)","v":"LAC06X00_TM"},"LAC06X00_TM AT%M1538.0 :BOOL; (*风幕机06X00-定时模式*)","LAC06X00_TM             AT%M1538.0     :BOOL; (*风幕机06X00-定时模式*)"]
["风幕机","L","M","07X00","定时模式","1540.0",null,"验证通过","BOOL","风幕机07X00-定时模式",{"$f":"B915&VLOOKUP(A915,List!$B$3:$D$445,2,FALSE)&D915&\"_\"&VLOOKUP(E915,List!$K$2:$M$447,2,FALSE)","v":"LAC07X00_TM"},"LAC07X00_TM AT%M1540.0 :BOOL; (*风幕机07X00-定时模式*)","LAC07X00_TM             AT%M1540.0     :BOOL; (*风幕机07X00-定时模式*)"]
["风幕机","L","M","08X00","定时模式",{"$f":"IF(OR(I915=\"REAL\",I915=\"DWORD\",I915=\"DINT\"),(IF(OR(I916=\"REAL\",I916=\"DWORD\",I916=\"DINT\"),F915+4+MOD(F915,4),F915+4)),(IF(OR(I916=\"REAL\",I916=\"DWORD\",I916=\"DINT\"),F915+4+MOD(F915,4),F915+2)))&\".0\"","v":"1542.0"},null,"验证通过","BOOL","风幕机08X00-定时模式",{"$f":"B916&VLOOKUP(A916,List!$B$3:$D$445,2,FALSE)&D916&\"_\"&VLOOKUP(E916,List!$K$2:$M$447,2,FALSE)","v":"LAC08X00_TM"},"LAC08X00_TM AT%M1542.0 :BOOL; (*风幕机08X00-定时模式*)","LAC08X00_TM             AT%M1542.0     :BOOL; (*风幕机08X00-定时模式*)"]
["水幕机","L","M","B3X00","定时控制","1544.0",null,"验证通过","BOOL",{"$f":"A917&D917&\"-\"&E917","v":"水幕机B3X00-定时控制"},{"$f":"B917&VLOOKUP(A917,List!$B$3:$D$445,2,FALSE)&D917&\"_\"&VLOOKUP(E917,List!$K$2:$M$447,2,FALSE)","v":"LWACB3X00_TC"},"LWACB3X00_TC AT%M1544.0 :BOOL; (*水幕机B3X00-定时控制*)","LWACB3X00_TC            AT%M1544.0     :BOOL; (*水幕机B3X00-定时控制*)"]
["水幕机","L","M","B2X00","定时控制","1546.0",null,"验证通过","BOOL","水幕机B2X00-定时控制",{"$f":"B918&VLOOKUP(A918,List!$B$3:$D$445,2,FALSE)&D918&\"_\"&VLOOKUP(E918,List!$K$2:$M$447,2,FALSE)","v":"LWACB2X00_TC"},"LWACB2X00_TC AT%M1546.0 :BOOL; (*水幕机B2X00-定时控制*)","LWACB2X00_TC            AT%M1546.0     :BOOL; (*水幕机B2X00-定时控制*)"]
["水幕机","L","M","B1X00","定时控制","1548.0",null,"验证通过","BOOL","水幕机B1X00-定时控制",{"$f":"B919&VLOOKUP(A919,List!$B$3:$D$445,2,FALSE)&D919&\"_\"&VLOOKUP(E919,List!$K$2:$M$447,2,FALSE)","v":"LWACB1X00_TC"},"LWACB1X00_TC AT%M1548.0 :BOOL; (*水幕机B1X00-定时控制*)","LWACB1X00_TC            AT%M1548.0     :BOOL; (*水幕机B1X00-定时控制*)"]
["水幕机","L","M","01X00","定时控制","1550.0",null,"验证通过","BOOL","水幕机01X00-定时控制",{"$f":"B920&VLOOKUP(A920,List!$B$3:$D$445,2,FALSE)&D920&\"_\"&VLOOKUP(E920,List!$K$2:$M$447,2,FALSE)","v":"LWAC01X00_TC"},"LWAC01X00_TC AT%M1550.0 :BOOL; (*水幕机01X00-定时控制*)","LWAC01X00_TC            AT%M1550.0     :BOOL; (*水幕机01X00-定时控制*)"]
["水幕机","L","M","02X00","定时控制","1552.0",null,{"$f":"IF((IF(OR(I921=\"INT\",I921=\"WORD\",I921=\"BOOL\"),MOD(F921,2),MOD(F921,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","水幕机02X00-定时控制",{"$f":"B921&VLOOKUP(A921,List!$B$3:$D$445,2,FALSE)&D921&\"_\"&VLOOKUP(E921,List!$K$2:$M$447,2,FALSE)","v":"LWAC02X00_TC"},"LWAC02X00_TC AT%M1552.0 :BOOL; (*水幕机02X00-定时控制*)","LWAC02X00_TC            AT%M1552.0     :BOOL; (*水幕机02X00-定时控制*)"]
["水幕机","L","M","03X00","定时控制","1554.0",null,"验证通过","BOOL","水幕机03X00-定时控制",{"$f":"B922&VLOOKUP(A922,List!$B$3:$D$445,2,FALSE)&D922&\"_\"&VLOOKUP(E922,List!$K$2:$M$447,2,FALSE)","v":"LWAC03X00_TC"},"LWAC03X00_TC AT%M1554.0 :BOOL; (*水幕机03X00-定时控制*)","LWAC03X00_TC            AT%M1554.0     :BOOL; (*水幕机03X00-定时控制*)"]
["水幕机","L","M","04X00","定时控制","1556.0",null,"验证通过","BOOL","水幕机04X00-定时控制",{"$f":"B923&VLOOKUP(A923,List!$B$3:$D$445,2,FALSE)&D923&\"_\"&VLOOKUP(E923,List!$K$2:$M$447,2,FALSE)","v":"LWAC04X00_TC"},"LWAC04X00_TC AT%M1556.0 :BOOL; (*水幕机04X00-定时控制*)","LWAC04X00_TC            AT%M1556.0     :BOOL; (*水幕机04X00-定时控制*)"]
["水幕机","L","M","05X00","定时控制","1558.0",null,"验证通过","BOOL","水幕机05X00-定时控制",{"$f":"B924&VLOOKUP(A924,List!$B$3:$D$445,2,FALSE)&D924&\"_\"&VLOOKUP(E924,List!$K$2:$M$447,2,FALSE)","v":"LWAC05X00_TC"},"LWAC05X00_TC AT%M1558.0 :BOOL; (*水幕机05X00-定时控制*)","LWAC05X00_TC            AT%M1558.0     :BOOL; (*水幕机05X00-定时控制*)"]
["水幕机","L","M","06X00","定时控制","1560.0",null,"验证通过","BOOL","水幕机06X00-定时控制",{"$f":"B925&VLOOKUP(A925,List!$B$3:$D$445,2,FALSE)&D925&\"_\"&VLOOKUP(E925,List!$K$2:$M$447,2,FALSE)","v":"LWAC06X00_TC"},"LWAC06X00_TC AT%M1560.0 :BOOL; (*水幕机06X00-定时控制*)","LWAC06X00_TC            AT%M1560.0     :BOOL; (*水幕机06X00-定时控制*)"]
["水幕机","L","M","07X00","定时控制","1562.0",null,"验证通过","BOOL","水幕机07X00-定时控制",{"$f":"B926&VLOOKUP(A926,List!$B$3:$D$445,2,FALSE)&D926&\"_\"&VLOOKUP(E926,List!$K$2:$M$447,2,FALSE)","v":"LWAC07X00_TC"},"LWAC07X00_TC AT%M1562.0 :BOOL; (*水幕机07X00-定时控制*)","LWAC07X00_TC            AT%M1562.0     :BOOL; (*水幕机07X00-定时控制*)"]
["水幕机","L","M","08X00","定时控制","1564.0",null,"验证通过","BOOL","水幕机08X00-定时控制",{"$f":"B927&VLOOKUP(A927,List!$B$3:$D$445,2,FALSE)&D927&\"_\"&VLOOKUP(E927,List!$K$2:$M$447,2,FALSE)","v":"LWAC08X00_TC"},"LWAC08X00_TC AT%M1564.0 :BOOL; (*水幕机08X00-定时控制*)","LWAC08X00_TC            AT%M1564.0     :BOOL; (*水幕机08X00-定时控制*)"]
["水幕机","L","M","B3X00","定时模式","1566.0",null,"验证通过","BOOL","水幕机B3X00-定时模式",{"$f":"B928&VLOOKUP(A928,List!$B$3:$D$445,2,FALSE)&D928&\"_\"&VLOOKUP(E928,List!$K$2:$M$447,2,FALSE)","v":"LWACB3X00_TM"},"LWACB3X00_TM AT%M1566.0 :BOOL; (*水幕机B3X00-定时模式*)","LWACB3X00_TM            AT%M1566.0     :BOOL; (*水幕机B3X00-定时模式*)"]
["水幕机","L","M","B2X00","定时模式","1568.0",null,"验证通过","BOOL","水幕机B2X00-定时模式",{"$f":"B929&VLOOKUP(A929,List!$B$3:$D$445,2,FALSE)&D929&\"_\"&VLOOKUP(E929,List!$K$2:$M$447,2,FALSE)","v":"LWACB2X00_TM"},"LWACB2X00_TM AT%M1568.0 :BOOL; (*水幕机B2X00-定时模式*)","LWACB2X00_TM            AT%M1568.0     :BOOL; (*水幕机B2X00-定时模式*)"]
["水幕机","L","M","B1X00","定时模式","1570.0",null,"验证通过","BOOL","水幕机B1X00-定时模式",{"$f":"B930&VLOOKUP(A930,List!$B$3:$D$445,2,FALSE)&D930&\"_\"&VLOOKUP(E930,List!$K$2:$M$447,2,FALSE)","v":"LWACB1X00_TM"},"LWACB1X00_TM AT%M1570.0 :BOOL; (*水幕机B1X00-定时模式*)","LWACB1X00_TM            AT%M1570.0     :BOOL; (*水幕机B1X00-定时模式*)"]
["水幕机","L","M","01X00","定时模式","1572.0",null,"验证通过","BOOL","水幕机01X00-定时模式",{"$f":"B931&VLOOKUP(A931,List!$B$3:$D$445,2,FALSE)&D931&\"_\"&VLOOKUP(E931,List!$K$2:$M$447,2,FALSE)","v":"LWAC01X00_TM"},"LWAC01X00_TM AT%M1572.0 :BOOL; (*水幕机01X00-定时模式*)","LWAC01X00_TM            AT%M1572.0     :BOOL; (*水幕机01X00-定时模式*)"]
["水幕机","L","M","02X00","定时模式","1574.0",null,{"$f":"IF((IF(OR(I932=\"INT\",I932=\"WORD\",I932=\"BOOL\"),MOD(F932,2),MOD(F932,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","水幕机02X00-定时模式",{"$f":"B932&VLOOKUP(A932,List!$B$3:$D$445,2,FALSE)&D932&\"_\"&VLOOKUP(E932,List!$K$2:$M$447,2,FALSE)","v":"LWAC02X00_TM"},"LWAC02X00_TM AT%M1574.0 :BOOL; (*水幕机02X00-定时模式*)","LWAC02X00_TM            AT%M1574.0     :BOOL; (*水幕机02X00-定时模式*)"]
["水幕机","L","M","03X00","定时模式","1576.0",null,"验证通过","BOOL","水幕机03X00-定时模式",{"$f":"B933&VLOOKUP(A933,List!$B$3:$D$445,2,FALSE)&D933&\"_\"&VLOOKUP(E933,List!$K$2:$M$447,2,FALSE)","v":"LWAC03X00_TM"},"LWAC03X00_TM AT%M1576.0 :BOOL; (*水幕机03X00-定时模式*)","LWAC03X00_TM            AT%M1576.0     :BOOL; (*水幕机03X00-定时模式*)"]
["水幕机","L","M","04X00","定时模式","1578.0",null,"验证通过","BOOL","水幕机04X00-定时模式",{"$f":"B934&VLOOKUP(A934,List!$B$3:$D$445,2,FALSE)&D934&\"_\"&VLOOKUP(E934,List!$K$2:$M$447,2,FALSE)","v":"LWAC04X00_TM"},"LWAC04X00_TM AT%M1578.0 :BOOL; (*水幕机04X00-定时模式*)","LWAC04X00_TM            AT%M1578.0     :BOOL; (*水幕机04X00-定时模式*)"]
["水幕机","L","M","05X00","定时模式","1580.0",null,"验证通过","BOOL","水幕机05X00-定时模式",{"$f":"B935&VLOOKUP(A935,List!$B$3:$D$445,2,FALSE)&D935&\"_\"&VLOOKUP(E935,List!$K$2:$M$447,2,FALSE)","v":"LWAC05X00_TM"},"LWAC05X00_TM AT%M1580.0 :BOOL; (*水幕机05X00-定时模式*)","LWAC05X00_TM            AT%M1580.0     :BOOL; (*水幕机05X00-定时模式*)"]
["水幕机","L","M","06X00","定时模式","1582.0",null,"验证通过","BOOL","水幕机06X00-定时模式",{"$f":"B936&VLOOKUP(A936,List!$B$3:$D$445,2,FALSE)&D936&\"_\"&VLOOKUP(E936,List!$K$2:$M$447,2,FALSE)","v":"LWAC06X00_TM"},"LWAC06X00_TM AT%M1582.0 :BOOL; (*水幕机06X00-定时模式*)","LWAC06X00_TM            AT%M1582.0     :BOOL; (*水幕机06X00-定时模式*)"]
["水幕机","L","M","07X00","定时模式","1584.0",null,"验证通过","BOOL","水幕机07X00-定时模式",{"$f":"B937&VLOOKUP(A937,List!$B$3:$D$445,2,FALSE)&D937&\"_\"&VLOOKUP(E937,List!$K$2:$M$447,2,FALSE)","v":"LWAC07X00_TM"},"LWAC07X00_TM AT%M1584.0 :BOOL; (*水幕机07X00-定时模式*)","LWAC07X00_TM            AT%M1584.0     :BOOL; (*水幕机07X00-定时模式*)"]
["水幕机","L","M","08X00","定时模式","1586.0",null,"验证通过","BOOL","水幕机08X00-定时模式",{"$f":"B938&VLOOKUP(A938,List!$B$3:$D$445,2,FALSE)&D938&\"_\"&VLOOKUP(E938,List!$K$2:$M$447,2,FALSE)","v":"LWAC08X00_TM"},"LWAC08X00_TM AT%M1586.0 :BOOL; (*水幕机08X00-定时模式*)","LWAC08X00_TM            AT%M1586.0     :BOOL; (*水幕机08X00-定时模式*)"]
[]
["命令","RNI","M","00001","心跳值","5000.0",null,{"$f":"IF((IF(OR(I940=\"INT\",I940=\"WORD\",I940=\"BOOL\"),MOD(F940,2),MOD(F940,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"INT","心跳值",{"$f":"B940&VLOOKUP(A940,List!$B$3:$D$445,2,FALSE)&D940&\"_\"&VLOOKUP(E940,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00001_DHV"},{"$f":"K940&\" \"&\"AT%\"&C940&F940&\" \"&\":\"&I940&\";\"&\" \"&\"(*\"&J940&\"*)\"","v":"RNICMD00001_DHV AT%M5000.0 :INT; (*心跳值*)"},{"$f":"REPLACE(REPLACE(L940,SEARCH(\"AT%\",L940),,REPT(\" \",25-SEARCH(\"AT%\",L940))),SEARCH(\":\",REPLACE(L940,SEARCH(\"AT%\",L940),,REPT(\" \",25-SEARCH(\"AT%\",L940)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L940,SEARCH(\"AT%\",L940),,REPT(\" \",25-SEARCH(\"AT%\",L940))))))","v":"RNICMD00001_DHV         AT%M5000.0     :INT; (*心跳值*)"}]
["命令","RNI","M","00002","心跳值",{"$f":"IF(OR(I940=\"REAL\",I940=\"DWORD\",I940=\"DINT\"),(IF(OR(I941=\"REAL\",I941=\"DWORD\",I941=\"DINT\"),F940+4+MOD(F940,4),F940+4)),(IF(OR(I941=\"REAL\",I941=\"DWORD\",I941=\"DINT\"),F940+4+MOD(F940,4),F940+2)))&\".0\"","v":"5002.0"},null,{"$f":"IF((IF(OR(I941=\"INT\",I941=\"WORD\",I941=\"BOOL\"),MOD(F941,2),MOD(F941,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"INT","心跳值",{"$f":"B941&VLOOKUP(A941,List!$B$3:$D$445,2,FALSE)&D941&\"_\"&VLOOKUP(E941,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00002_DHV"},{"$f":"K941&\" \"&\"AT%\"&C941&F941&\" \"&\":\"&I941&\";\"&\" \"&\"(*\"&J941&\"*)\"","v":"RNICMD00002_DHV AT%M5002.0 :INT; (*心跳值*)"},{"$f":"REPLACE(REPLACE(L941,SEARCH(\"AT%\",L941),,REPT(\" \",25-SEARCH(\"AT%\",L941))),SEARCH(\":\",REPLACE(L941,SEARCH(\"AT%\",L941),,REPT(\" \",25-SEARCH(\"AT%\",L941)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L941,SEARCH(\"AT%\",L941),,REPT(\" \",25-SEARCH(\"AT%\",L941))))))","v":"RNICMD00002_DHV         AT%M5002.0     :INT; (*心跳值*)"}]
["命令","RNI","M","00003","心跳值","5004.0",null,"验证通过","INT","心跳值",{"$f":"B942&VLOOKUP(A942,List!$B$3:$D$445,2,FALSE)&D942&\"_\"&VLOOKUP(E942,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00003_DHV"},"RNICMD00003_DHV AT%M5004.0 :INT; (*心跳值*)","RNICMD00003_DHV         AT%M5004.0     :INT; (*心跳值*)"]
["命令","RNI","M","00004","心跳值","5006.0",null,"验证通过","INT","心跳值",{"$f":"B943&VLOOKUP(A943,List!$B$3:$D$445,2,FALSE)&D943&\"_\"&VLOOKUP(E943,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00004_DHV"},"RNICMD00004_DHV AT%M5006.0 :INT; (*心跳值*)","RNICMD00004_DHV         AT%M5006.0     :INT; (*心跳值*)"]
["命令","RNI","M","00005","心跳值","5008.0",null,"验证通过","INT","心跳值",{"$f":"B944&VLOOKUP(A944,List!$B$3:$D$445,2,FALSE)&D944&\"_\"&VLOOKUP(E944,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00005_DHV"},"RNICMD00005_DHV AT%M5008.0 :INT; (*心跳值*)","RNICMD00005_DHV         AT%M5008.0     :INT; (*心跳值*)"]
["命令","RNI","M","00006","心跳值","5010.0",null,"验证通过","INT","心跳值",{"$f":"B945&VLOOKUP(A945,List!$B$3:$D$445,2,FALSE)&D945&\"_\"&VLOOKUP(E945,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00006_DHV"},"RNICMD00006_DHV AT%M5010.0 :INT; (*心跳值*)","RNICMD00006_DHV         AT%M5010.0     :INT; (*心跳值*)"]
["命令","RNI","M","00007","心跳值","5012.0",null,"验证通过","INT","心跳值",{"$f":"B946&VLOOKUP(A946,List!$B$3:$D$445,2,FALSE)&D946&\"_\"&VLOOKUP(E946,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00007_DHV"},"RNICMD00007_DHV AT%M5012.0 :INT; (*心跳值*)","RNICMD00007_DHV         AT%M5012.0     :INT; (*心跳值*)"]
["命令","RNI","M","00008","心跳值","5014.0",null,"验证通过","INT","心跳值",{"$f":"B947&VLOOKUP(A947,List!$B$3:$D$445,2,FALSE)&D947&\"_\"&VLOOKUP(E947,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00008_DHV"},"RNICMD00008_DHV AT%M5014.0 :INT; (*心跳值*)","RNICMD00008_DHV         AT%M5014.0     :INT; (*心跳值*)"]
["命令","RNI","M","00009","心跳值","5016.0",null,"验证通过","INT","心跳值",{"$f":"B948&VLOOKUP(A948,List!$B$3:$D$445,2,FALSE)&D948&\"_\"&VLOOKUP(E948,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00009_DHV"},"RNICMD00009_DHV AT%M5016.0 :INT; (*心跳值*)","RNICMD00009_DHV         AT%M5016.0     :INT; (*心跳值*)"]
["命令","RNI","M","00010","心跳值","5018.0",null,"验证通过","INT","心跳值",{"$f":"B949&VLOOKUP(A949,List!$B$3:$D$445,2,FALSE)&D949&\"_\"&VLOOKUP(E949,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00010_DHV"},"RNICMD00010_DHV AT%M5018.0 :INT; (*心跳值*)","RNICMD00010_DHV         AT%M5018.0     :INT; (*心跳值*)"]
["命令","RNI","M","00011","心跳值","5020.0",null,"验证通过","INT","心跳值",{"$f":"B950&VLOOKUP(A950,List!$B$3:$D$445,2,FALSE)&D950&\"_\"&VLOOKUP(E950,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00011_DHV"},"RNICMD00011_DHV AT%M5020.0 :INT; (*心跳值*)","RNICMD00011_DHV         AT%M5020.0     :INT; (*心跳值*)"]
["命令","RNI","M","00012","心跳值","5022.0",null,"验证通过","INT","心跳值",{"$f":"B951&VLOOKUP(A951,List!$B$3:$D$445,2,FALSE)&D951&\"_\"&VLOOKUP(E951,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00012_DHV"},"RNICMD00012_DHV AT%M5022.0 :INT; (*心跳值*)","RNICMD00012_DHV         AT%M5022.0     :INT; (*心跳值*)"]
["命令","RNI","M","00013","心跳值","5024.0",null,"验证通过","INT","心跳值",{"$f":"B952&VLOOKUP(A952,List!$B$3:$D$445,2,FALSE)&D952&\"_\"&VLOOKUP(E952,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00013_DHV"},"RNICMD00013_DHV AT%M5024.0 :INT; (*心跳值*)","RNICMD00013_DHV         AT%M5024.0     :INT; (*心跳值*)"]
["命令","RNI","M","00014","心跳值","5026.0",null,"验证通过","INT","心跳值",{"$f":"B953&VLOOKUP(A953,List!$B$3:$D$445,2,FALSE)&D953&\"_\"&VLOOKUP(E953,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00014_DHV"},"RNICMD00014_DHV AT%M5026.0 :INT; (*心跳值*)","RNICMD00014_DHV         AT%M5026.0     :INT; (*心跳值*)"]
["命令","RNI","M","00015","心跳值","5028.0",null,"验证通过","INT","心跳值",{"$f":"B954&VLOOKUP(A954,List!$B$3:$D$445,2,FALSE)&D954&\"_\"&VLOOKUP(E954,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00015_DHV"},"RNICMD00015_DHV AT%M5028.0 :INT; (*心跳值*)","RNICMD00015_DHV         AT%M5028.0     :INT; (*心跳值*)"]
["命令","RNI","M","00016","心跳值","5030.0",null,"验证通过","INT","心跳值",{"$f":"B955&VLOOKUP(A955,List!$B$3:$D$445,2,FALSE)&D955&\"_\"&VLOOKUP(E955,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00016_DHV"},"RNICMD00016_DHV AT%M5030.0 :INT; (*心跳值*)","RNICMD00016_DHV         AT%M5030.0     :INT; (*心跳值*)"]
["命令","RNI","M","00017","心跳值","5032.0",null,"验证通过","INT","心跳值",{"$f":"B956&VLOOKUP(A956,List!$B$3:$D$445,2,FALSE)&D956&\"_\"&VLOOKUP(E956,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00017_DHV"},"RNICMD00017_DHV AT%M5032.0 :INT; (*心跳值*)","RNICMD00017_DHV         AT%M5032.0     :INT; (*心跳值*)"]
["命令","RNI","M","00018","心跳值","5034.0",null,"验证通过","INT","心跳值",{"$f":"B957&VLOOKUP(A957,List!$B$3:$D$445,2,FALSE)&D957&\"_\"&VLOOKUP(E957,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00018_DHV"},"RNICMD00018_DHV AT%M5034.0 :INT; (*心跳值*)","RNICMD00018_DHV         AT%M5034.0     :INT; (*心跳值*)"]
["命令","RNI","M","00019","心跳值","5036.0",null,"验证通过","INT","心跳值",{"$f":"B958&VLOOKUP(A958,List!$B$3:$D$445,2,FALSE)&D958&\"_\"&VLOOKUP(E958,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00019_DHV"},"RNICMD00019_DHV AT%M5036.0 :INT; (*心跳值*)","RNICMD00019_DHV         AT%M5036.0     :INT; (*心跳值*)"]
["命令","RNI","M","00020","心跳值","5038.0",null,"验证通过","INT","心跳值",{"$f":"B959&VLOOKUP(A959,List!$B$3:$D$445,2,FALSE)&D959&\"_\"&VLOOKUP(E959,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00020_DHV"},"RNICMD00020_DHV AT%M5038.0 :INT; (*心跳值*)","RNICMD00020_DHV         AT%M5038.0     :INT; (*心跳值*)"]
["命令","RNI","M","00021","心跳值",{"$f":"IF(OR(I959=\"REAL\",I959=\"DWORD\",I959=\"DINT\"),(IF(OR(I960=\"REAL\",I960=\"DWORD\",I960=\"DINT\"),F959+4+MOD(F959,4),F959+4)),(IF(OR(I960=\"REAL\",I960=\"DWORD\",I960=\"DINT\"),F959+4+MOD(F959,4),F959+2)))&\".0\"","v":"5040.0"},null,{"$f":"IF((IF(OR(I960=\"INT\",I960=\"WORD\",I960=\"BOOL\"),MOD(F960,2),MOD(F960,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"INT","心跳值",{"$f":"B960&VLOOKUP(A960,List!$B$3:$D$445,2,FALSE)&D960&\"_\"&VLOOKUP(E960,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00021_DHV"},{"$f":"K960&\" \"&\"AT%\"&C960&F960&\" \"&\":\"&I960&\";\"&\" \"&\"(*\"&J960&\"*)\"","v":"RNICMD00021_DHV AT%M5040.0 :INT; (*心跳值*)"},{"$f":"REPLACE(REPLACE(L960,SEARCH(\"AT%\",L960),,REPT(\" \",25-SEARCH(\"AT%\",L960))),SEARCH(\":\",REPLACE(L960,SEARCH(\"AT%\",L960),,REPT(\" \",25-SEARCH(\"AT%\",L960)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L960,SEARCH(\"AT%\",L960),,REPT(\" \",25-SEARCH(\"AT%\",L960))))))","v":"RNICMD00021_DHV         AT%M5040.0     :INT; (*心跳值*)"}]
["命令","RNI","M","00022","心跳值","5042.0",null,"验证通过","INT","心跳值",{"$f":"B961&VLOOKUP(A961,List!$B$3:$D$445,2,FALSE)&D961&\"_\"&VLOOKUP(E961,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00022_DHV"},"RNICMD00022_DHV AT%M5042.0 :INT; (*心跳值*)","RNICMD00022_DHV         AT%M5042.0     :INT; (*心跳值*)"]
["命令","RNI","M","00023","心跳值","5044.0",null,"验证通过","INT","心跳值",{"$f":"B962&VLOOKUP(A962,List!$B$3:$D$445,2,FALSE)&D962&\"_\"&VLOOKUP(E962,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00023_DHV"},"RNICMD00023_DHV AT%M5044.0 :INT; (*心跳值*)","RNICMD00023_DHV         AT%M5044.0     :INT; (*心跳值*)"]
["命令","RNI","M","00024","心跳值","5046.0",null,"验证通过","INT","心跳值",{"$f":"B963&VLOOKUP(A963,List!$B$3:$D$445,2,FALSE)&D963&\"_\"&VLOOKUP(E963,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00024_DHV"},"RNICMD00024_DHV AT%M5046.0 :INT; (*心跳值*)","RNICMD00024_DHV         AT%M5046.0     :INT; (*心跳值*)"]
["命令","RNI","M","00025","心跳值","5048.0",null,"验证通过","INT","心跳值",{"$f":"B964&VLOOKUP(A964,List!$B$3:$D$445,2,FALSE)&D964&\"_\"&VLOOKUP(E964,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00025_DHV"},"RNICMD00025_DHV AT%M5048.0 :INT; (*心跳值*)","RNICMD00025_DHV         AT%M5048.0     :INT; (*心跳值*)"]
["命令","RNI","M","00026","心跳值","5050.0",null,"验证通过","INT","心跳值",{"$f":"B965&VLOOKUP(A965,List!$B$3:$D$445,2,FALSE)&D965&\"_\"&VLOOKUP(E965,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00026_DHV"},"RNICMD00026_DHV AT%M5050.0 :INT; (*心跳值*)","RNICMD00026_DHV         AT%M5050.0     :INT; (*心跳值*)"]
["命令","RNI","M","00027","心跳值","5052.0",null,"验证通过","INT","心跳值",{"$f":"B966&VLOOKUP(A966,List!$B$3:$D$445,2,FALSE)&D966&\"_\"&VLOOKUP(E966,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00027_DHV"},"RNICMD00027_DHV AT%M5052.0 :INT; (*心跳值*)","RNICMD00027_DHV         AT%M5052.0     :INT; (*心跳值*)"]
["命令","RNI","M","00028","心跳值","5054.0",null,"验证通过","INT","心跳值",{"$f":"B967&VLOOKUP(A967,List!$B$3:$D$445,2,FALSE)&D967&\"_\"&VLOOKUP(E967,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00028_DHV"},"RNICMD00028_DHV AT%M5054.0 :INT; (*心跳值*)","RNICMD00028_DHV         AT%M5054.0     :INT; (*心跳值*)"]
["命令","RNI","M","00029","心跳值","5056.0",null,"验证通过","INT","心跳值",{"$f":"B968&VLOOKUP(A968,List!$B$3:$D$445,2,FALSE)&D968&\"_\"&VLOOKUP(E968,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00029_DHV"},"RNICMD00029_DHV AT%M5056.0 :INT; (*心跳值*)","RNICMD00029_DHV         AT%M5056.0     :INT; (*心跳值*)"]
["命令","RNI","M","00030","心跳值","5058.0",null,"验证通过","INT","心跳值",{"$f":"B969&VLOOKUP(A969,List!$B$3:$D$445,2,FALSE)&D969&\"_\"&VLOOKUP(E969,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00030_DHV"},"RNICMD00030_DHV AT%M5058.0 :INT; (*心跳值*)","RNICMD00030_DHV         AT%M5058.0     :INT; (*心跳值*)"]
["命令","RNI","M","00031","心跳值","5060.0",null,"验证通过","INT","心跳值",{"$f":"B970&VLOOKUP(A970,List!$B$3:$D$445,2,FALSE)&D970&\"_\"&VLOOKUP(E970,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00031_DHV"},"RNICMD00031_DHV AT%M5060.0 :INT; (*心跳值*)","RNICMD00031_DHV         AT%M5060.0     :INT; (*心跳值*)"]
["命令","RNI","M","00032","心跳值",{"$f":"IF(OR(I970=\"REAL\",I970=\"DWORD\",I970=\"DINT\"),(IF(OR(I971=\"REAL\",I971=\"DWORD\",I971=\"DINT\"),F970+4+MOD(F970,4),F970+4)),(IF(OR(I971=\"REAL\",I971=\"DWORD\",I971=\"DINT\"),F970+4+MOD(F970,4),F970+2)))&\".0\"","v":"5062.0"},null,{"$f":"IF((IF(OR(I971=\"INT\",I971=\"WORD\",I971=\"BOOL\"),MOD(F971,2),MOD(F971,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"INT","心跳值",{"$f":"B971&VLOOKUP(A971,List!$B$3:$D$445,2,FALSE)&D971&\"_\"&VLOOKUP(E971,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00032_DHV"},{"$f":"K971&\" \"&\"AT%\"&C971&F971&\" \"&\":\"&I971&\";\"&\" \"&\"(*\"&J971&\"*)\"","v":"RNICMD00032_DHV AT%M5062.0 :INT; (*心跳值*)"},{"$f":"REPLACE(REPLACE(L971,SEARCH(\"AT%\",L971),,REPT(\" \",25-SEARCH(\"AT%\",L971))),SEARCH(\":\",REPLACE(L971,SEARCH(\"AT%\",L971),,REPT(\" \",25-SEARCH(\"AT%\",L971)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L971,SEARCH(\"AT%\",L971),,REPT(\" \",25-SEARCH(\"AT%\",L971))))))","v":"RNICMD00032_DHV         AT%M5062.0     :INT; (*心跳值*)"}]

{"sheet":"从CPU","index":4,"n_rows":597,"n_cols":13,"rows_kept":597,"cut":false,"hidden":false,"merged":[[0,0,0,12],[1,0,2,0],[1,1,2,1],[1,2,2,2],[1,3,2,3],[1,4,2,4],[1,7,2,7],[1,8,2,8],[1,9,2,9],[1,10,2,10],[1,11,2,11],[1,12,2,12],[1,5,2,6]]}
["NI 0-1023 NQ 1024-2047"]
["设备类型","总线编号","P2P标记","程序编号","点位功能","发送地址\n接收地址",null,"数据类型\n整除验证","数据类型","变量备注","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto"]
[]
["从CPU（地上）接收",{"$nulls":4},"接收地址","发送地址.auto"]
["命令","RNI","M","00000","心跳值","5000.0",null,{"$f":"IF((IF(OR(I5=\"INT\",I5=\"WORD\",I5=\"BOOL\"),MOD(F5,2),MOD(F5,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"INT","心跳值",{"$f":"B5&VLOOKUP(A5,List!$B$3:$D$445,2,FALSE)&D5&\"_\"&VLOOKUP(E5,List!$K$2:$M$447,2,FALSE)","v":"RNICMD00000_DHV"},{"$f":"K5&\" \"&\"AT%\"&C5&F5&\" \"&\":\"&I5&\";\"&\" \"&\"(*\"&J5&\"*)\"","v":"RNICMD00000_DHV AT%M5000.0 :INT; (*心跳值*)"},{"$f":"REPLACE(REPLACE(L5,SEARCH(\"AT%\",L5),,REPT(\" \",25-SEARCH(\"AT%\",L5))),SEARCH(\":\",REPLACE(L5,SEARCH(\"AT%\",L5),,REPT(\" \",25-SEARCH(\"AT%\",L5)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L5,SEARCH(\"AT%\",L5),,REPT(\" \",25-SEARCH(\"AT%\",L5))))))","v":"RNICMD00000_DHV         AT%M5000.0     :INT; (*心跳值*)"}]
["空调机组","RNI","M","00000","新云模式",{"$f":"IF(OR(I5=\"REAL\",I5=\"DWORD\",I5=\"DINT\"),(IF(OR(I6=\"REAL\",I6=\"DWORD\",I6=\"DINT\"),F5+4+MOD(F5,4),F5+4)),(IF(OR(I6=\"REAL\",I6=\"DWORD\",I6=\"DINT\"),F5+4+MOD(F5,4),F5+2)))&\".0\"","v":"5002.0"},null,"验证通过","BOOL","空调机组新云模式",{"$f":"B6&VLOOKUP(A6,List!$B$3:$D$445,2,FALSE)&D6&\"_\"&VLOOKUP(E6,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU00000_CM"},"RNIAHU00000_CM AT%M5002.0 :BOOL; (*空调机组新云模式*)","RNIAHU00000_CM          AT%M5002.0     :BOOL; (*空调机组新云模式*)"]
["风机盘管","RNI","M","00000","新云模式",{"$f":"IF(OR(I6=\"REAL\",I6=\"DWORD\",I6=\"DINT\"),(IF(OR(I7=\"REAL\",I7=\"DWORD\",I7=\"DINT\"),F6+4+MOD(F6,4),F6+4)),(IF(OR(I7=\"REAL\",I7=\"DWORD\",I7=\"DINT\"),F6+4+MOD(F6,4),F6+2)))&\".0\"","v":"5004.0"},null,"验证通过","BOOL","风机盘管新云模式",{"$f":"B7&VLOOKUP(A7,List!$B$3:$D$445,2,FALSE)&D7&\"_\"&VLOOKUP(E7,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU00000_CM"},"RNIFCU00000_CM AT%M5004.0 :BOOL; (*风机盘管新云模式*)","RNIFCU00000_CM          AT%M5004.0     :BOOL; (*风机盘管新云模式*)"]
["照明控制箱","RNI","M","00000","新云模式","5006.0",null,"验证通过","BOOL","照明控制箱新云模式",{"$f":"B8&VLOOKUP(A8,List!$B$3:$D$445,2,FALSE)&D8&\"_\"&VLOOKUP(E8,List!$K$2:$M$447,2,FALSE)","v":"RNILCB00000_CM"},{"$f":"K8&\" \"&\"AT%\"&C8&F8&\" \"&\":\"&I8&\";\"&\" \"&\"(*\"&J8&\"*)\"","v":"RNILCB00000_CM AT%M5006.0 :BOOL; (*照明控制箱新云模式*)"},{"$f":"REPLACE(REPLACE(L8,SEARCH(\"AT%\",L8),,REPT(\" \",25-SEARCH(\"AT%\",L8))),SEARCH(\":\",REPLACE(L8,SEARCH(\"AT%\",L8),,REPT(\" \",25-SEARCH(\"AT%\",L8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L8,SEARCH(\"AT%\",L8),,REPT(\" \",25-SEARCH(\"AT%\",L8))))))","v":"RNILCB00000_CM          AT%M5006.0     :BOOL; (*照明控制箱新云模式*)"}]
["排风机","RNI","M","00000","新云模式","5008.0",null,"验证通过","BOOL","送排风机新云模式",{"$f":"B9&VLOOKUP(A9,List!$B$3:$D$445,2,FALSE)&D9&\"_\"&VLOOKUP(E9,List!$K$2:$M$447,2,FALSE)","v":"RNIEAF00000_CM"},{"$f":"K9&\" \"&\"AT%\"&C9&F9&\" \"&\":\"&I9&\";\"&\" \"&\"(*\"&J9&\"*)\"","v":"RNIEAF00000_CM AT%M5008.0 :BOOL; (*送排风机新云模式*)"},{"$f":"REPLACE(REPLACE(L9,SEARCH(\"AT%\",L9),,REPT(\" \",25-SEARCH(\"AT%\",L9))),SEARCH(\":\",REPLACE(L9,SEARCH(\"AT%\",L9),,REPT(\" \",25-SEARCH(\"AT%\",L9)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L9,SEARCH(\"AT%\",L9),,REPT(\" \",25-SEARCH(\"AT%\",L9))))))","v":"RNIEAF00000_CM          AT%M5008.0     :BOOL; (*送排风机新云模式*)"}]
["P新风机组","RNI","M","00000","新云模式","5010.0",null,"验证通过","BOOL","新风机组新云模式",{"$f":"B10&VLOOKUP(A10,List!$B$3:$D$445,2,FALSE)&D10&\"_\"&VLOOKUP(E10,List!$K$2:$M$447,2,FALSE)","v":"RNIPAU00000_CM"},"RNIPAU00000_CM AT%M5010.0 :BOOL; (*新风机组新云模式*)","RNIPAU00000_CM          AT%M5010.0     :BOOL; (*新风机组新云模式*)"]
["风幕机","RNI","M","00000","新云模式","5012.0",null,"验证通过","BOOL","风幕机新云模式",{"$f":"B11&VLOOKUP(A11,List!$B$3:$D$445,2,FALSE)&D11&\"_\"&VLOOKUP(E11,List!$K$2:$M$447,2,FALSE)","v":"RNIAC00000_CM"},"RNIAC00000_CM AT%M5012.0 :BOOL; (*风幕机新云模式*)","RNIAC00000_CM           AT%M5012.0     :BOOL; (*风幕机新云模式*)"]
["冷水机组","RNI","M","00000","新云模式","5014.0",null,"验证通过","BOOL","冷源新云模式",{"$f":"B12&VLOOKUP(A12,List!$B$3:$D$445,2,FALSE)&D12&\"_\"&VLOOKUP(E12,List!$K$2:$M$447,2,FALSE)","v":"RNICHR00000_CM"},"RNICHR00000_CM AT%M5014.0 :BOOL; (*冷源新云模式*)","RNICHR00000_CM          AT%M5014.0     :BOOL; (*冷源新云模式*)"]
["空调机组","RNI","M","B3X00","设定温度值","5020.0",null,"验证通过","REAL","空调机组B3层温度全局设定",{"$f":"B13&VLOOKUP(A13,List!$B$3:$D$445,2,FALSE)&D13&\"_\"&VLOOKUP(E13,List!$K$2:$M$447,2,FALSE)","v":"RNIAHUB3X00_TSET"},{"$f":"K13&\" \"&\"AT%\"&C13&F13&\" \"&\":\"&I13&\";\"&\" \"&\"(*\"&J13&\"*)\"","v":"RNIAHUB3X00_TSET AT%M5020.0 :REAL; (*空调机组B3层温度全局设定*)"},{"$f":"REPLACE(REPLACE(L13,SEARCH(\"AT%\",L13),,REPT(\" \",25-SEARCH(\"AT%\",L13))),SEARCH(\":\",REPLACE(L13,SEARCH(\"AT%\",L13),,REPT(\" \",25-SEARCH(\"AT%\",L13)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L13,SEARCH(\"AT%\",L13),,REPT(\" \",25-SEARCH(\"AT%\",L13))))))","v":"RNIAHUB3X00_TSET        AT%M5020.0     :REAL; (*空调机组B3层温度全局设定*)"}]
["空调机组","RNI","M","B2X00","设定温度值","5024.0",null,"验证通过","REAL","空调机组B2层温度全局设定",{"$f":"B14&VLOOKUP(A14,List!$B$3:$D$445,2,FALSE)&D14&\"_\"&VLOOKUP(E14,List!$K$2:$M$447,2,FALSE)","v":"RNIAHUB2X00_TSET"},"RNIAHUB2X00_TSET AT%M5024.0 :REAL; (*空调机组B2层温度全局设定*)","RNIAHUB2X00_TSET        AT%M5024.0     :REAL; (*空调机组B2层温度全局设定*)"]
["空调机组","RNI","M","B1X00","设定温度值","5028.0",null,"验证通过","REAL","空调机组B1层温度全局设定",{"$f":"B15&VLOOKUP(A15,List!$B$3:$D$445,2,FALSE)&D15&\"_\"&VLOOKUP(E15,List!$K$2:$M$447,2,FALSE)","v":"RNIAHUB1X00_TSET"},"RNIAHUB1X00_TSET AT%M5028.0 :REAL; (*空调机组B1层温度全局设定*)","RNIAHUB1X00_TSET        AT%M5028.0     :REAL; (*空调机组B1层温度全局设定*)"]
["空调机组","RNI","M","01X00","设定温度值","5032.0",null,"验证通过","REAL","空调机组1层温度全局设定",{"$f":"B16&VLOOKUP(A16,List!$B$3:$D$445,2,FALSE)&D16&\"_\"&VLOOKUP(E16,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU01X00_TSET"},"RNIAHU01X00_TSET AT%M5032.0 :REAL; (*空调机组1层温度全局设定*)","RNIAHU01X00_TSET        AT%M5032.0     :REAL; (*空调机组1层温度全局设定*)"]
["空调机组","RNI","M","02X00","设定温度值","5036.0",null,"验证通过","REAL","空调机组2层温度全局设定",{"$f":"B17&VLOOKUP(A17,List!$B$3:$D$445,2,FALSE)&D17&\"_\"&VLOOKUP(E17,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU02X00_TSET"},"RNIAHU02X00_TSET AT%M5036.0 :REAL; (*空调机组2层温度全局设定*)","RNIAHU02X00_TSET        AT%M5036.0     :REAL; (*空调机组2层温度全局设定*)"]
["空调机组","RNI","M","03X00","设定温度值","5040.0",null,"验证通过","REAL","空调机组3层温度全局设定",{"$f":"B18&VLOOKUP(A18,List!$B$3:$D$445,2,FALSE)&D18&\"_\"&VLOOKUP(E18,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU03X00_TSET"},"RNIAHU03X00_TSET AT%M5040.0 :REAL; (*空调机组3层温度全局设定*)","RNIAHU03X00_TSET        AT%M5040.0     :REAL; (*空调机组3层温度全局设定*)"]
["空调机组","RNI","M","04X00","设定温度值","5044.0",null,"验证通过","REAL","空调机组4层温度全局设定",{"$f":"B19&VLOOKUP(A19,List!$B$3:$D$445,2,FALSE)&D19&\"_\"&VLOOKUP(E19,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU04X00_TSET"},"RNIAHU04X00_TSET AT%M5044.0 :REAL; (*空调机组4层温度全局设定*)","RNIAHU04X00_TSET        AT%M5044.0     :REAL; (*空调机组4层温度全局设定*)"]
["空调机组","RNI","M","05X00","设定温度值","5048.0",null,"验证通过","REAL","空调机组5层温度全局设定",{"$f":"B20&VLOOKUP(A20,List!$B$3:$D$445,2,FALSE)&D20&\"_\"&VLOOKUP(E20,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU05X00_TSET"},"RNIAHU05X00_TSET AT%M5048.0 :REAL; (*空调机组5层温度全局设定*)","RNIAHU05X00_TSET        AT%M5048.0     :REAL; (*空调机组5层温度全局设定*)"]
["空调机组","RNI","M","06X00","设定温度值","5052.0",null,"验证通过","REAL","空调机组6层温度全局设定",{"$f":"B21&VLOOKUP(A21,List!$B$3:$D$445,2,FALSE)&D21&\"_\"&VLOOKUP(E21,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU06X00_TSET"},"RNIAHU06X00_TSET AT%M5052.0 :REAL; (*空调机组6层温度全局设定*)","RNIAHU06X00_TSET        AT%M5052.0     :REAL; (*空调机组6层温度全局设定*)"]
["空调机组","RNI","M","07X00","设定温度值","5056.0",null,"验证通过","REAL","空调机组7层温度全局设定",{"$f":"B22&VLOOKUP(A22,List!$B$3:$D$445,2,FALSE)&D22&\"_\"&VLOOKUP(E22,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU07X00_TSET"},"RNIAHU07X00_TSET AT%M5056.0 :REAL; (*空调机组7层温度全局设定*)","RNIAHU07X00_TSET        AT%M5056.0     :REAL; (*空调机组7层温度全局设定*)"]
["空调机组","RNI","M","08X00","设定温度值","5060.0",null,"验证通过","REAL","空调机组8层温度全局设定",{"$f":"B23&VLOOKUP(A23,List!$B$3:$D$445,2,FALSE)&D23&\"_\"&VLOOKUP(E23,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU08X00_TSET"},"RNIAHU08X00_TSET AT%M5060.0 :REAL; (*空调机组8层温度全局设定*)","RNIAHU08X00_TSET        AT%M5060.0     :REAL; (*空调机组8层温度全局设定*)"]
["空调机组","RNI","M","B3X00","季节模式","5064.0",null,"验证通过","INT","空调机组B3层季节模式全局设定",{"$f":"B24&VLOOKUP(A24,List!$B$3:$D$445,2,FALSE)&D24&\"_\"&VLOOKUP(E24,List!$K$2:$M$447,2,FALSE)","v":"RNIAHUB3X00_SM"},"RNIAHUB3X00_SM AT%M5064.0 :INT; (*空调机组B3层季节模式全局设定*)","RNIAHUB3X00_SM          AT%M5064.0     :INT; (*空调机组B3层季节模式全局设定*)"]
["空调机组","RNI","M","B2X00","季节模式","5066.0",null,"验证通过","INT","空调机组B2层季节模式全局设定",{"$f":"B25&VLOOKUP(A25,List!$B$3:$D$445,2,FALSE)&D25&\"_\"&VLOOKUP(E25,List!$K$2:$M$447,2,FALSE)","v":"RNIAHUB2X00_SM"},"RNIAHUB2X00_SM AT%M5066.0 :INT; (*空调机组B2层季节模式全局设定*)","RNIAHUB2X00_SM          AT%M5066.0     :INT; (*空调机组B2层季节模式全局设定*)"]
["空调机组","RNI","M","B1X00","季节模式","5068.0",null,"验证通过","INT","空调机组B1层季节模式全局设定",{"$f":"B26&VLOOKUP(A26,List!$B$3:$D$445,2,FALSE)&D26&\"_\"&VLOOKUP(E26,List!$K$2:$M$447,2,FALSE)","v":"RNIAHUB1X00_SM"},"RNIAHUB1X00_SM AT%M5068.0 :INT; (*空调机组B1层季节模式全局设定*)","RNIAHUB1X00_SM          AT%M5068.0     :INT; (*空调机组B1层季节模式全局设定*)"]
["空调机组","RNI","M","01X00","季节模式","5070.0",null,"验证通过","INT","空调机组1层季节模式全局设定",{"$f":"B27&VLOOKUP(A27,List!$B$3:$D$445,2,FALSE)&D27&\"_\"&VLOOKUP(E27,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU01X00_SM"},"RNIAHU01X00_SM AT%M5070.0 :INT; (*空调机组1层季节模式全局设定*)","RNIAHU01X00_SM          AT%M5070.0     :INT; (*空调机组1层季节模式全局设定*)"]
["空调机组","RNI","M","02X00","季节模式","5072.0",null,"验证通过","INT","空调机组2层季节模式全局设定",{"$f":"B28&VLOOKUP(A28,List!$B$3:$D$445,2,FALSE)&D28&\"_\"&VLOOKUP(E28,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU02X00_SM"},"RNIAHU02X00_SM AT%M5072.0 :INT; (*空调机组2层季节模式全局设定*)","RNIAHU02X00_SM          AT%M5072.0     :INT; (*空调机组2层季节模式全局设定*)"]
["空调机组","RNI","M","03X00","季节模式","5074.0",null,"验证通过","INT","空调机组3层季节模式全局设定",{"$f":"B29&VLOOKUP(A29,List!$B$3:$D$445,2,FALSE)&D29&\"_\"&VLOOKUP(E29,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU03X00_SM"},"RNIAHU03X00_SM AT%M5074.0 :INT; (*空调机组3层季节模式全局设定*)","RNIAHU03X00_SM          AT%M5074.0     :INT; (*空调机组3层季节模式全局设定*)"]
["空调机组","RNI","M","04X00","季节模式","5076.0",null,"验证通过","INT","空调机组4层季节模式全局设定",{"$f":"B30&VLOOKUP(A30,List!$B$3:$D$445,2,FALSE)&D30&\"_\"&VLOOKUP(E30,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU04X00_SM"},"RNIAHU04X00_SM AT%M5076.0 :INT; (*空调机组4层季节模式全局设定*)","RNIAHU04X00_SM          AT%M5076.0     :INT; (*空调机组4层季节模式全局设定*)"]
["空调机组","RNI","M","05X00","季节模式","5078.0",null,"验证通过","INT","空调机组5层季节模式全局设定",{"$f":"B31&VLOOKUP(A31,List!$B$3:$D$445,2,FALSE)&D31&\"_\"&VLOOKUP(E31,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU05X00_SM"},"RNIAHU05X00_SM AT%M5078.0 :INT; (*空调机组5层季节模式全局设定*)","RNIAHU05X00_SM          AT%M5078.0     :INT; (*空调机组5层季节模式全局设定*)"]
["空调机组","RNI","M","06X00","季节模式","5080.0",null,"验证通过","INT","空调机组6层季节模式全局设定",{"$f":"B32&VLOOKUP(A32,List!$B$3:$D$445,2,FALSE)&D32&\"_\"&VLOOKUP(E32,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU06X00_SM"},"RNIAHU06X00_SM AT%M5080.0 :INT; (*空调机组6层季节模式全局设定*)","RNIAHU06X00_SM          AT%M5080.0     :INT; (*空调机组6层季节模式全局设定*)"]
["空调机组","RNI","M","07X00","季节模式","5082.0",null,"验证通过","INT","空调机组7层季节模式全局设定",{"$f":"B33&VLOOKUP(A33,List!$B$3:$D$445,2,FALSE)&D33&\"_\"&VLOOKUP(E33,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU07X00_SM"},"RNIAHU07X00_SM AT%M5082.0 :INT; (*空调机组7层季节模式全局设定*)","RNIAHU07X00_SM          AT%M5082.0     :INT; (*空调机组7层季节模式全局设定*)"]
["空调机组","RNI","M","08X00","季节模式","5084.0",null,"验证通过","INT","空调机组8层季节模式全局设定",{"$f":"B34&VLOOKUP(A34,List!$B$3:$D$445,2,FALSE)&D34&\"_\"&VLOOKUP(E34,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU08X00_SM"},"RNIAHU08X00_SM AT%M5084.0 :INT; (*空调机组8层季节模式全局设定*)","RNIAHU08X00_SM          AT%M5084.0     :INT; (*空调机组8层季节模式全局设定*)"]
["空调机组","RNI","M","B3X00","程序控制","5086.0",null,"验证通过","BOOL","空调机组B3层启停控制",{"$f":"B35&VLOOKUP(A35,List!$B$3:$D$445,2,FALSE)&D35&\"_\"&VLOOKUP(E35,List!$K$2:$M$447,2,FALSE)","v":"RNIAHUB3X00_PC"},"RNIAHUB3X00_PC AT%M5086.0 :BOOL; (*空调机组B3层启停控制*)","RNIAHUB3X00_PC          AT%M5086.0     :BOOL; (*空调机组B3层启停控制*)"]
["空调机组","RNI","M","B2X00","程序控制","5088.0",null,"验证通过","BOOL","空调机组B2层启停控制",{"$f":"B36&VLOOKUP(A36,List!$B$3:$D$445,2,FALSE)&D36&\"_\"&VLOOKUP(E36,List!$K$2:$M$447,2,FALSE)","v":"RNIAHUB2X00_PC"},"RNIAHUB2X00_PC AT%M5088.0 :BOOL; (*空调机组B2层启停控制*)","RNIAHUB2X00_PC          AT%M5088.0     :BOOL; (*空调机组B2层启停控制*)"]
["空调机组","RNI","M","B1X00","程序控制","5090.0",null,"验证通过","BOOL","空调机组B1层启停控制",{"$f":"B37&VLOOKUP(A37,List!$B$3:$D$445,2,FALSE)&D37&\"_\"&VLOOKUP(E37,List!$K$2:$M$447,2,FALSE)","v":"RNIAHUB1X00_PC"},"RNIAHUB1X00_PC AT%M5090.0 :BOOL; (*空调机组B1层启停控制*)","RNIAHUB1X00_PC          AT%M5090.0     :BOOL; (*空调机组B1层启停控制*)"]
["空调机组","RNI","M","01X00","程序控制","5092.0",null,"验证通过","BOOL","空调机组1层启停控制",{"$f":"B38&VLOOKUP(A38,List!$B$3:$D$445,2,FALSE)&D38&\"_\"&VLOOKUP(E38,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU01X00_PC"},"RNIAHU01X00_PC AT%M5092.0 :BOOL; (*空调机组1层启停控制*)","RNIAHU01X00_PC          AT%M5092.0     :BOOL; (*空调机组1层启停控制*)"]
["空调机组","RNI","M","02X00","程序控制","5094.0",null,"验证通过","BOOL","空调机组2层启停控制",{"$f":"B39&VLOOKUP(A39,List!$B$3:$D$445,2,FALSE)&D39&\"_\"&VLOOKUP(E39,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU02X00_PC"},"RNIAHU02X00_PC AT%M5094.0 :BOOL; (*空调机组2层启停控制*)","RNIAHU02X00_PC          AT%M5094.0     :BOOL; (*空调机组2层启停控制*)"]
["空调机组","RNI","M","03X00","程序控制","5096.0",null,"验证通过","BOOL","空调机组3层启停控制",{"$f":"B40&VLOOKUP(A40,List!$B$3:$D$445,2,FALSE)&D40&\"_\"&VLOOKUP(E40,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU03X00_PC"},"RNIAHU03X00_PC AT%M5096.0 :BOOL; (*空调机组3层启停控制*)","RNIAHU03X00_PC          AT%M5096.0     :BOOL; (*空调机组3层启停控制*)"]
["空调机组","RNI","M","04X00","程序控制","5098.0",null,"验证通过","BOOL","空调机组4层启停控制",{"$f":"B41&VLOOKUP(A41,List!$B$3:$D$445,2,FALSE)&D41&\"_\"&VLOOKUP(E41,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU04X00_PC"},"RNIAHU04X00_PC AT%M5098.0 :BOOL; (*空调机组4层启停控制*)","RNIAHU04X00_PC          AT%M5098.0     :BOOL; (*空调机组4层启停控制*)"]
["空调机组","RNI","M","05X00","程序控制","5100.0",null,"验证通过","BOOL","空调机组5层启停控制",{"$f":"B42&VLOOKUP(A42,List!$B$3:$D$445,2,FALSE)&D42&\"_\"&VLOOKUP(E42,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU05X00_PC"},"RNIAHU05X00_PC AT%M5100.0 :BOOL; (*空调机组5层启停控制*)","RNIAHU05X00_PC          AT%M5100.0     :BOOL; (*空调机组5层启停控制*)"]
["空调机组","RNI","M","06X00","程序控制","5102.0",null,"验证通过","BOOL","空调机组6层启停控制",{"$f":"B43&VLOOKUP(A43,List!$B$3:$D$445,2,FALSE)&D43&\"_\"&VLOOKUP(E43,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU06X00_PC"},"RNIAHU06X00_PC AT%M5102.0 :BOOL; (*空调机组6层启停控制*)","RNIAHU06X00_PC          AT%M5102.0     :BOOL; (*空调机组6层启停控制*)"]
["空调机组","RNI","M","07X00","程序控制","5104.0",null,"验证通过","BOOL","空调机组7层启停控制",{"$f":"B44&VLOOKUP(A44,List!$B$3:$D$445,2,FALSE)&D44&\"_\"&VLOOKUP(E44,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU07X00_PC"},"RNIAHU07X00_PC AT%M5104.0 :BOOL; (*空调机组7层启停控制*)","RNIAHU07X00_PC          AT%M5104.0     :BOOL; (*空调机组7层启停控制*)"]
["空调机组","RNI","M","08X00","程序控制","5106.0",null,"验证通过","BOOL","空调机组8层启停控制",{"$f":"B45&VLOOKUP(A45,List!$B$3:$D$445,2,FALSE)&D45&\"_\"&VLOOKUP(E45,List!$K$2:$M$447,2,FALSE)","v":"RNIAHU08X00_PC"},"RNIAHU08X00_PC AT%M5106.0 :BOOL; (*空调机组8层启停控制*)","RNIAHU08X00_PC          AT%M5106.0     :BOOL; (*空调机组8层启停控制*)"]
["风机盘管","RNI","M","B3X00","设定温度值","5112.0",null,"验证通过","REAL","风机盘管B3层温度全局设定",{"$f":"B46&VLOOKUP(A46,List!$B$3:$D$445,2,FALSE)&D46&\"_\"&VLOOKUP(E46,List!$K$2:$M$447,2,FALSE)","v":"RNIFCUB3X00_TSET"},"RNIFCUB3X00_TSET AT%M5112.0 :REAL; (*风机盘管B3层温度全局设定*)","RNIFCUB3X00_TSET        AT%M5112.0     :REAL; (*风机盘管B3层温度全局设定*)"]
["风机盘管","RNI","M","B2X00","设定温度值","5116.0",null,"验证通过","REAL","风机盘管B2层温度全局设定",{"$f":"B47&VLOOKUP(A47,List!$B$3:$D$445,2,FALSE)&D47&\"_\"&VLOOKUP(E47,List!$K$2:$M$447,2,FALSE)","v":"RNIFCUB2X00_TSET"},"RNIFCUB2X00_TSET AT%M5116.0 :REAL; (*风机盘管B2层温度全局设定*)","RNIFCUB2X00_TSET        AT%M5116.0     :REAL; (*风机盘管B2层温度全局设定*)"]
["风机盘管","RNI","M","B1X00","设定温度值","5120.0",null,"验证通过","REAL","风机盘管B1层温度全局设定",{"$f":"B48&VLOOKUP(A48,List!$B$3:$D$445,2,FALSE)&D48&\"_\"&VLOOKUP(E48,List!$K$2:$M$447,2,FALSE)","v":"RNIFCUB1X00_TSET"},"RNIFCUB1X00_TSET AT%M5120.0 :REAL; (*风机盘管B1层温度全局设定*)","RNIFCUB1X00_TSET        AT%M5120.0     :REAL; (*风机盘管B1层温度全局设定*)"]
["风机盘管","RNI","M","01X00","设定温度值","5124.0",null,"验证通过","REAL","风机盘管1层温度全局设定",{"$f":"B49&VLOOKUP(A49,List!$B$3:$D$445,2,FALSE)&D49&\"_\"&VLOOKUP(E49,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU01X00_TSET"},"RNIFCU01X00_TSET AT%M5124.0 :REAL; (*风机盘管1层温度全局设定*)","RNIFCU01X00_TSET        AT%M5124.0     :REAL; (*风机盘管1层温度全局设定*)"]
["风机盘管","RNI","M","02X00","设定温度值","5128.0",null,"验证通过","REAL","风机盘管2层温度全局设定",{"$f":"B50&VLOOKUP(A50,List!$B$3:$D$445,2,FALSE)&D50&\"_\"&VLOOKUP(E50,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU02X00_TSET"},"RNIFCU02X00_TSET AT%M5128.0 :REAL; (*风机盘管2层温度全局设定*)","RNIFCU02X00_TSET        AT%M5128.0     :REAL; (*风机盘管2层温度全局设定*)"]
["风机盘管","RNI","M","03X00","设定温度值","5132.0",null,"验证通过","REAL","风机盘管3层温度全局设定",{"$f":"B51&VLOOKUP(A51,List!$B$3:$D$445,2,FALSE)&D51&\"_\"&VLOOKUP(E51,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU03X00_TSET"},"RNIFCU03X00_TSET AT%M5132.0 :REAL; (*风机盘管3层温度全局设定*)","RNIFCU03X00_TSET        AT%M5132.0     :REAL; (*风机盘管3层温度全局设定*)"]
["风机盘管","RNI","M","04X00","设定温度值","5136.0",null,"验证通过","REAL","风机盘管4层温度全局设定",{"$f":"B52&VLOOKUP(A52,List!$B$3:$D$445,2,FALSE)&D52&\"_\"&VLOOKUP(E52,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU04X00_TSET"},"RNIFCU04X00_TSET AT%M5136.0 :REAL; (*风机盘管4层温度全局设定*)","RNIFCU04X00_TSET        AT%M5136.0     :REAL; (*风机盘管4层温度全局设定*)"]
["风机盘管","RNI","M","05X00","设定温度值","5140.0",null,"验证通过","REAL","风机盘管5层温度全局设定",{"$f":"B53&VLOOKUP(A53,List!$B$3:$D$445,2,FALSE)&D53&\"_\"&VLOOKUP(E53,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU05X00_TSET"},"RNIFCU05X00_TSET AT%M5140.0 :REAL; (*风机盘管5层温度全局设定*)","RNIFCU05X00_TSET        AT%M5140.0     :REAL; (*风机盘管5层温度全局设定*)"]
["风机盘管","RNI","M","06X00","设定温度值","5144.0",null,"验证通过","REAL","风机盘管6层温度全局设定",{"$f":"B54&VLOOKUP(A54,List!$B$3:$D$445,2,FALSE)&D54&\"_\"&VLOOKUP(E54,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU06X00_TSET"},"RNIFCU06X00_TSET AT%M5144.0 :REAL; (*风机盘管6层温度全局设定*)","RNIFCU06X00_TSET        AT%M5144.0     :REAL; (*风机盘管6层温度全局设定*)"]
["风机盘管","RNI","M","07X00","设定温度值","5148.0",null,"验证通过","REAL","风机盘管7层温度全局设定",{"$f":"B55&VLOOKUP(A55,List!$B$3:$D$445,2,FALSE)&D55&\"_\"&VLOOKUP(E55,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU07X00_TSET"},"RNIFCU07X00_TSET AT%M5148.0 :REAL; (*风机盘管7层温度全局设定*)","RNIFCU07X00_TSET        AT%M5148.0     :REAL; (*风机盘管7层温度全局设定*)"]
["风机盘管","RNI","M","08X00","设定温度值","5152.0",null,"验证通过","REAL","风机盘管8层温度全局设定",{"$f":"B56&VLOOKUP(A56,List!$B$3:$D$445,2,FALSE)&D56&\"_\"&VLOOKUP(E56,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU08X00_TSET"},"RNIFCU08X00_TSET AT%M5152.0 :REAL; (*风机盘管8层温度全局设定*)","RNIFCU08X00_TSET        AT%M5152.0     :REAL; (*风机盘管8层温度全局设定*)"]
["风机盘管","RNI","M","B3X00","季节模式","5156.0",null,"验证通过","INT","风机盘管B3层季节模式全局设定",{"$f":"B57&VLOOKUP(A57,List!$B$3:$D$445,2,FALSE)&D57&\"_\"&VLOOKUP(E57,List!$K$2:$M$447,2,FALSE)","v":"RNIFCUB3X00_SM"},"RNIFCUB3X00_SM AT%M5156.0 :INT; (*风机盘管B3层季节模式全局设定*)","RNIFCUB3X00_SM          AT%M5156.0     :INT; (*风机盘管B3层季节模式全局设定*)"]
["风机盘管","RNI","M","B2X00","季节模式","5158.0",null,"验证通过","INT","风机盘管B2层季节模式全局设定",{"$f":"B58&VLOOKUP(A58,List!$B$3:$D$445,2,FALSE)&D58&\"_\"&VLOOKUP(E58,List!$K$2:$M$447,2,FALSE)","v":"RNIFCUB2X00_SM"},"RNIFCUB2X00_SM AT%M5158.0 :INT; (*风机盘管B2层季节模式全局设定*)","RNIFCUB2X00_SM          AT%M5158.0     :INT; (*风机盘管B2层季节模式全局设定*)"]
["风机盘管","RNI","M","B1X00","季节模式","5160.0",null,"验证通过","INT","风机盘管B1层季节模式全局设定",{"$f":"B59&VLOOKUP(A59,List!$B$3:$D$445,2,FALSE)&D59&\"_\"&VLOOKUP(E59,List!$K$2:$M$447,2,FALSE)","v":"RNIFCUB1X00_SM"},"RNIFCUB1X00_SM AT%M5160.0 :INT; (*风机盘管B1层季节模式全局设定*)","RNIFCUB1X00_SM          AT%M5160.0     :INT; (*风机盘管B1层季节模式全局设定*)"]
["风机盘管","RNI","M","01X00","季节模式","5162.0",null,"验证通过","INT","风机盘管1层季节模式全局设定",{"$f":"B60&VLOOKUP(A60,List!$B$3:$D$445,2,FALSE)&D60&\"_\"&VLOOKUP(E60,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU01X00_SM"},"RNIFCU01X00_SM AT%M5162.0 :INT; (*风机盘管1层季节模式全局设定*)","RNIFCU01X00_SM          AT%M5162.0     :INT; (*风机盘管1层季节模式全局设定*)"]
["风机盘管","RNI","M","02X00","季节模式","5164.0",null,"验证通过","INT","风机盘管2层季节模式全局设定",{"$f":"B61&VLOOKUP(A61,List!$B$3:$D$445,2,FALSE)&D61&\"_\"&VLOOKUP(E61,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU02X00_SM"},"RNIFCU02X00_SM AT%M5164.0 :INT; (*风机盘管2层季节模式全局设定*)","RNIFCU02X00_SM          AT%M5164.0     :INT; (*风机盘管2层季节模式全局设定*)"]
["风机盘管","RNI","M","03X00","季节模式","5166.0",null,"验证通过","INT","风机盘管3层季节模式全局设定",{"$f":"B62&VLOOKUP(A62,List!$B$3:$D$445,2,FALSE)&D62&\"_\"&VLOOKUP(E62,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU03X00_SM"},"RNIFCU03X00_SM AT%M5166.0 :INT; (*风机盘管3层季节模式全局设定*)","RNIFCU03X00_SM          AT%M5166.0     :INT; (*风机盘管3层季节模式全局设定*)"]
["风机盘管","RNI","M","04X00","季节模式","5168.0",null,"验证通过","INT","风机盘管4层季节模式全局设定",{"$f":"B63&VLOOKUP(A63,List!$B$3:$D$445,2,FALSE)&D63&\"_\"&VLOOKUP(E63,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU04X00_SM"},"RNIFCU04X00_SM AT%M5168.0 :INT; (*风机盘管4层季节模式全局设定*)","RNIFCU04X00_SM          AT%M5168.0     :INT; (*风机盘管4层季节模式全局设定*)"]
["风机盘管","RNI","M","05X00","季节模式","5170.0",null,"验证通过","INT","风机盘管5层季节模式全局设定",{"$f":"B64&VLOOKUP(A64,List!$B$3:$D$445,2,FALSE)&D64&\"_\"&VLOOKUP(E64,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU05X00_SM"},"RNIFCU05X00_SM AT%M5170.0 :INT; (*风机盘管5层季节模式全局设定*)","RNIFCU05X00_SM          AT%M5170.0     :INT; (*风机盘管5层季节模式全局设定*)"]
["风机盘管","RNI","M","06X00","季节模式","5172.0",null,"验证通过","INT","风机盘管6层季节模式全局设定",{"$f":"B65&VLOOKUP(A65,List!$B$3:$D$445,2,FALSE)&D65&\"_\"&VLOOKUP(E65,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU06X00_SM"},"RNIFCU06X00_SM AT%M5172.0 :INT; (*风机盘管6层季节模式全局设定*)","RNIFCU06X00_SM          AT%M5172.0     :INT; (*风机盘管6层季节模式全局设定*)"]
["风机盘管","RNI","M","07X00","季节模式","5174.0",null,"验证通过","INT","风机盘管7层季节模式全局设定",{"$f":"B66&VLOOKUP(A66,List!$B$3:$D$445,2,FALSE)&D66&\"_\"&VLOOKUP(E66,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU07X00_SM"},"RNIFCU07X00_SM AT%M5174.0 :INT; (*风机盘管7层季节模式全局设定*)","RNIFCU07X00_SM          AT%M5174.0     :INT; (*风机盘管7层季节模式全局设定*)"]
["风机盘管","RNI","M","08X00","季节模式","5176.0",null,"验证通过","INT","风机盘管8层季节模式全局设定",{"$f":"B67&VLOOKUP(A67,List!$B$3:$D$445,2,FALSE)&D67&\"_\"&VLOOKUP(E67,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU08X00_SM"},"RNIFCU08X00_SM AT%M5176.0 :INT; (*风机盘管8层季节模式全局设定*)","RNIFCU08X00_SM          AT%M5176.0     :INT; (*风机盘管8层季节模式全局设定*)"]
["风机盘管","RNI","M","B3X00","程序控制","5178.0",null,"验证通过","BOOL","风机盘管B3层启停控制",{"$f":"B68&VLOOKUP(A68,List!$B$3:$D$445,2,FALSE)&D68&\"_\"&VLOOKUP(E68,List!$K$2:$M$447,2,FALSE)","v":"RNIFCUB3X00_PC"},"RNIFCUB3X00_PC AT%M5178.0 :BOOL; (*风机盘管B3层启停控制*)","RNIFCUB3X00_PC          AT%M5178.0     :BOOL; (*风机盘管B3层启停控制*)"]
["风机盘管","RNI","M","B2X00","程序控制","5180.0",null,"验证通过","BOOL","风机盘管B2层启停控制",{"$f":"B69&VLOOKUP(A69,List!$B$3:$D$445,2,FALSE)&D69&\"_\"&VLOOKUP(E69,List!$K$2:$M$447,2,FALSE)","v":"RNIFCUB2X00_PC"},"RNIFCUB2X00_PC AT%M5180.0 :BOOL; (*风机盘管B2层启停控制*)","RNIFCUB2X00_PC          AT%M5180.0     :BOOL; (*风机盘管B2层启停控制*)"]
["风机盘管","RNI","M","B1X00","程序控制","5182.0",null,"验证通过","BOOL","风机盘管B1层启停控制",{"$f":"B70&VLOOKUP(A70,List!$B$3:$D$445,2,FALSE)&D70&\"_\"&VLOOKUP(E70,List!$K$2:$M$447,2,FALSE)","v":"RNIFCUB1X00_PC"},"RNIFCUB1X00_PC AT%M5182.0 :BOOL; (*风机盘管B1层启停控制*)","RNIFCUB1X00_PC          AT%M5182.0     :BOOL; (*风机盘管B1层启停控制*)"]
["风机盘管","RNI","M","01X00","程序控制",{"$f":"IF(OR(I70=\"REAL\",I70=\"DWORD\",I70=\"DINT\"),(IF(OR(I71=\"REAL\",I71=\"DWORD\",I71=\"DINT\"),F70+4+MOD(F70,4),F70+4)),(IF(OR(I71=\"REAL\",I71=\"DWORD\",I71=\"DINT\"),F70+4+MOD(F70,4),F70+2)))&\".0\"","v":"5184.0"},null,"验证通过","BOOL","风机盘管1层启停控制",{"$f":"B71&VLOOKUP(A71,List!$B$3:$D$445,2,FALSE)&D71&\"_\"&VLOOKUP(E71,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU01X00_PC"},"RNIFCU01X00_PC AT%M5184.0 :BOOL; (*风机盘管1层启停控制*)","RNIFCU01X00_PC          AT%M5184.0     :BOOL; (*风机盘管1层启停控制*)"]
["风机盘管","RNI","M","02X00","程序控制","5186.0",null,"验证通过","BOOL","风机盘管2层启停控制",{"$f":"B72&VLOOKUP(A72,List!$B$3:$D$445,2,FALSE)&D72&\"_\"&VLOOKUP(E72,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU02X00_PC"},"RNIFCU02X00_PC AT%M5186.0 :BOOL; (*风机盘管2层启停控制*)","RNIFCU02X00_PC          AT%M5186.0     :BOOL; (*风机盘管2层启停控制*)"]
["风机盘管","RNI","M","03X00","程序控制","5188.0",null,"验证通过","BOOL","风机盘管3层启停控制",{"$f":"B73&VLOOKUP(A73,List!$B$3:$D$445,2,FALSE)&D73&\"_\"&VLOOKUP(E73,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU03X00_PC"},"RNIFCU03X00_PC AT%M5188.0 :BOOL; (*风机盘管3层启停控制*)","RNIFCU03X00_PC          AT%M5188.0     :BOOL; (*风机盘管3层启停控制*)"]
["风机盘管","RNI","M","04X00","程序控制","5190.0",null,"验证通过","BOOL","风机盘管4层启停控制",{"$f":"B74&VLOOKUP(A74,List!$B$3:$D$445,2,FALSE)&D74&\"_\"&VLOOKUP(E74,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU04X00_PC"},"RNIFCU04X00_PC AT%M5190.0 :BOOL; (*风机盘管4层启停控制*)","RNIFCU04X00_PC          AT%M5190.0     :BOOL; (*风机盘管4层启停控制*)"]
["风机盘管","RNI","M","05X00","程序控制","5192.0",null,"验证通过","BOOL","风机盘管5层启停控制",{"$f":"B75&VLOOKUP(A75,List!$B$3:$D$445,2,FALSE)&D75&\"_\"&VLOOKUP(E75,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU05X00_PC"},"RNIFCU05X00_PC AT%M5192.0 :BOOL; (*风机盘管5层启停控制*)","RNIFCU05X00_PC          AT%M5192.0     :BOOL; (*风机盘管5层启停控制*)"]
["风机盘管","RNI","M","06X00","程序控制","5194.0",null,"验证通过","BOOL","风机盘管6层启停控制",{"$f":"B76&VLOOKUP(A76,List!$B$3:$D$445,2,FALSE)&D76&\"_\"&VLOOKUP(E76,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU06X00_PC"},"RNIFCU06X00_PC AT%M5194.0 :BOOL; (*风机盘管6层启停控制*)","RNIFCU06X00_PC          AT%M5194.0     :BOOL; (*风机盘管6层启停控制*)"]
["风机盘管","RNI","M","07X00","程序控制","5196.0",null,"验证通过","BOOL","风机盘管7层启停控制",{"$f":"B77&VLOOKUP(A77,List!$B$3:$D$445,2,FALSE)&D77&\"_\"&VLOOKUP(E77,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU07X00_PC"},{"$f":"K77&\" \"&\"AT%\"&C77&F77&\" \"&\":\"&I77&\";\"&\" \"&\"(*\"&J77&\"*)\"","v":"RNIFCU07X00_PC AT%M5196.0 :BOOL; (*风机盘管7层启停控制*)"},{"$f":"REPLACE(REPLACE(L77,SEARCH(\"AT%\",L77),,REPT(\" \",25-SEARCH(\"AT%\",L77))),SEARCH(\":\",REPLACE(L77,SEARCH(\"AT%\",L77),,REPT(\" \",25-SEARCH(\"AT%\",L77)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L77,SEARCH(\"AT%\",L77),,REPT(\" \",25-SEARCH(\"AT%\",L77))))))","v":"RNIFCU07X00_PC          AT%M5196.0     :BOOL; (*风机盘管7层启停控制*)"}]
["风机盘管","RNI","M","08X00","程序控制",{"$f":"IF(OR(I77=\"REAL\",I77=\"DWORD\",I77=\"DINT\"),(IF(OR(I78=\"REAL\",I78=\"DWORD\",I78=\"DINT\"),F77+4+MOD(F77,4),F77+4)),(IF(OR(I78=\"REAL\",I78=\"DWORD\",I78=\"DINT\"),F77+4+MOD(F77,4),F77+2)))&\".0\"","v":"5198.0"},null,"验证通过","BOOL","风机盘管8层启停控制",{"$f":"B78&VLOOKUP(A78,List!$B$3:$D$445,2,FALSE)&D78&\"_\"&VLOOKUP(E78,List!$K$2:$M$447,2,FALSE)","v":"RNIFCU08X00_PC"},"RNIFCU08X00_PC AT%M5198.0 :BOOL; (*风机盘管8层启停控制*)","RNIFCU08X00_PC          AT%M5198.0     :BOOL; (*风机盘管8层启停控制*)"]
["照明控制箱","RNI","M","B3X0A","启停控制","5200.0",null,"验证通过","BOOL","基础照明A B3层全局启停控制",{"$f":"B79&VLOOKUP(A79,List!$B$3:$D$445,2,FALSE)&D79&\"_\"&VLOOKUP(E79,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB3X0A_C"},"RNILCBB3X0A_C AT%M5200.0 :BOOL; (*基础照明A B3层全局启停控制*)","RNILCBB3X0A_C           AT%M5200.0     :BOOL; (*基础照明A B3层全局启停控制*)"]
["照明控制箱","RNI","M","B2X0A","启停控制",{"$f":"IF(OR(I79=\"REAL\",I79=\"DWORD\",I79=\"DINT\"),(IF(OR(I80=\"REAL\",I80=\"DWORD\",I80=\"DINT\"),F79+4+MOD(F79,4),F79+4)),(IF(OR(I80=\"REAL\",I80=\"DWORD\",I80=\"DINT\"),F79+4+MOD(F79,4),F79+2)))&\".0\"","v":"5202.0"},null,"验证通过","BOOL","基础照明A B2层全局启停控制",{"$f":"B80&VLOOKUP(A80,List!$B$3:$D$445,2,FALSE)&D80&\"_\"&VLOOKUP(E80,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB2X0A_C"},"RNILCBB2X0A_C AT%M5202.0 :BOOL; (*基础照明A B2层全局启停控制*)","RNILCBB2X0A_C           AT%M5202.0     :BOOL; (*基础照明A B2层全局启停控制*)"]
["照明控制箱","RNI","M","B1X0A","启停控制","5204.0",null,"验证通过","BOOL","基础照明A B1层全局启停控制",{"$f":"B81&VLOOKUP(A81,List!$B$3:$D$445,2,FALSE)&D81&\"_\"&VLOOKUP(E81,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB1X0A_C"},"RNILCBB1X0A_C AT%M5204.0 :BOOL; (*基础照明A B1层全局启停控制*)","RNILCBB1X0A_C           AT%M5204.0     :BOOL; (*基础照明A B1层全局启停控制*)"]
["照明控制箱","RNI","M","01X0A","启停控制","5206.0",null,"验证通过","BOOL","基础照明A 1层全局启停控制",{"$f":"B82&VLOOKUP(A82,List!$B$3:$D$445,2,FALSE)&D82&\"_\"&VLOOKUP(E82,List!$K$2:$M$447,2,FALSE)","v":"RNILCB01X0A_C"},"RNILCB01X0A_C AT%M5206.0 :BOOL; (*基础照明A 1层全局启停控制*)","RNILCB01X0A_C           AT%M5206.0     :BOOL; (*基础照明A 1层全局启停控制*)"]
["照明控制箱","RNI","M","02X0A","启停控制","5208.0",null,"验证通过","BOOL","基础照明A 2层全局启停控制",{"$f":"B83&VLOOKUP(A83,List!$B$3:$D$445,2,FALSE)&D83&\"_\"&VLOOKUP(E83,List!$K$2:$M$447,2,FALSE)","v":"RNILCB02X0A_C"},"RNILCB02X0A_C AT%M5208.0 :BOOL; (*基础照明A 2层全局启停控制*)","RNILCB02X0A_C           AT%M5208.0     :BOOL; (*基础照明A 2层全局启停控制*)"]
["照明控制箱","RNI","M","03X0A","启停控制","5210.0",null,"验证通过","BOOL","基础照明A 3层全局启停控制",{"$f":"B84&VLOOKUP(A84,List!$B$3:$D$445,2,FALSE)&D84&\"_\"&VLOOKUP(E84,List!$K$2:$M$447,2,FALSE)","v":"RNILCB03X0A_C"},"RNILCB03X0A_C AT%M5210.0 :BOOL; (*基础照明A 3层全局启停控制*)","RNILCB03X0A_C           AT%M5210.0     :BOOL; (*基础照明A 3层全局启停控制*)"]
["照明控制箱","RNI","M","04X0A","启停控制","5212.0",null,"验证通过","BOOL","基础照明A 4层全局启停控制",{"$f":"B85&VLOOKUP(A85,List!$B$3:$D$445,2,FALSE)&D85&\"_\"&VLOOKUP(E85,List!$K$2:$M$447,2,FALSE)","v":"RNILCB04X0A_C"},"RNILCB04X0A_C AT%M5212.0 :BOOL; (*基础照明A 4层全局启停控制*)","RNILCB04X0A_C           AT%M5212.0     :BOOL; (*基础照明A 4层全局启停控制*)"]
["照明控制箱","RNI","M","05X0A","启停控制","5214.0",null,"验证通过","BOOL","基础照明A 5层全局启停控制",{"$f":"B86&VLOOKUP(A86,List!$B$3:$D$445,2,FALSE)&D86&\"_\"&VLOOKUP(E86,List!$K$2:$M$447,2,FALSE)","v":"RNILCB05X0A_C"},"RNILCB05X0A_C AT%M5214.0 :BOOL; (*基础照明A 5层全局启停控制*)","RNILCB05X0A_C           AT%M5214.0     :BOOL; (*基础照明A 5层全局启停控制*)"]
["照明控制箱","RNI","M","06X0A","启停控制","5216.0",null,"验证通过","BOOL","基础照明A 6层全局启停控制",{"$f":"B87&VLOOKUP(A87,List!$B$3:$D$445,2,FALSE)&D87&\"_\"&VLOOKUP(E87,List!$K$2:$M$447,2,FALSE)","v":"RNILCB06X0A_C"},"RNILCB06X0A_C AT%M5216.0 :BOOL; (*基础照明A 6层全局启停控制*)","RNILCB06X0A_C           AT%M5216.0     :BOOL; (*基础照明A 6层全局启停控制*)"]
["照明控制箱","RNI","M","07X0A","启停控制","5218.0",null,"验证通过","BOOL","基础照明A 7层全局启停控制",{"$f":"B88&VLOOKUP(A88,List!$B$3:$D$445,2,FALSE)&D88&\"_\"&VLOOKUP(E88,List!$K$2:$M$447,2,FALSE)","v":"RNILCB07X0A_C"},"RNILCB07X0A_C AT%M5218.0 :BOOL; (*基础照明A 7层全局启停控制*)","RNILCB07X0A_C           AT%M5218.0     :BOOL; (*基础照明A 7层全局启停控制*)"]
["照明控制箱","RNI","M","08X0A","启停控制","5220.0",null,"验证通过","BOOL","基础照明A 8层全局启停控制",{"$f":"B89&VLOOKUP(A89,List!$B$3:$D$445,2,FALSE)&D89&\"_\"&VLOOKUP(E89,List!$K$2:$M$447,2,FALSE)","v":"RNILCB08X0A_C"},"RNILCB08X0A_C AT%M5220.0 :BOOL; (*基础照明A 8层全局启停控制*)","RNILCB08X0A_C           AT%M5220.0     :BOOL; (*基础照明A 8层全局启停控制*)"]
["照明控制箱","RNI","M","B3X0B","启停控制","5222.0",null,"验证通过","BOOL","基础照明B B3层全局启停控制",{"$f":"B90&VLOOKUP(A90,List!$B$3:$D$445,2,FALSE)&D90&\"_\"&VLOOKUP(E90,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB3X0B_C"},"RNILCBB3X0B_C AT%M5222.0 :BOOL; (*基础照明B B3层全局启停控制*)","RNILCBB3X0B_C           AT%M5222.0     :BOOL; (*基础照明B B3层全局启停控制*)"]
["照明控制箱","RNI","M","B2X0B","启停控制","5224.0",null,"验证通过","BOOL","基础照明B B2层全局启停控制",{"$f":"B91&VLOOKUP(A91,List!$B$3:$D$445,2,FALSE)&D91&\"_\"&VLOOKUP(E91,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB2X0B_C"},"RNILCBB2X0B_C AT%M5224.0 :BOOL; (*基础照明B B2层全局启停控制*)","RNILCBB2X0B_C           AT%M5224.0     :BOOL; (*基础照明B B2层全局启停控制*)"]
["照明控制箱","RNI","M","B1X0B","启停控制","5226.0",null,"验证通过","BOOL","基础照明B B1层全局启停控制",{"$f":"B92&VLOOKUP(A92,List!$B$3:$D$445,2,FALSE)&D92&\"_\"&VLOOKUP(E92,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB1X0B_C"},"RNILCBB1X0B_C AT%M5226.0 :BOOL; (*基础照明B B1层全局启停控制*)","RNILCBB1X0B_C           AT%M5226.0     :BOOL; (*基础照明B B1层全局启停控制*)"]
["照明控制箱","RNI","M","01X0B","启停控制","5228.0",null,"验证通过","BOOL","基础照明B 1层全局启停控制",{"$f":"B93&VLOOKUP(A93,List!$B$3:$D$445,2,FALSE)&D93&\"_\"&VLOOKUP(E93,List!$K$2:$M$447,2,FALSE)","v":"RNILCB01X0B_C"},"RNILCB01X0B_C AT%M5228.0 :BOOL; (*基础照明B 1层全局启停控制*)","RNILCB01X0B_C           AT%M5228.0     :BOOL; (*基础照明B 1层全局启停控制*)"]
["照明控制箱","RNI","M","02X0B","启停控制","5230.0",null,"验证通过","BOOL","基础照明B 2层全局启停控制",{"$f":"B94&VLOOKUP(A94,List!$B$3:$D$445,2,FALSE)&D94&\"_\"&VLOOKUP(E94,List!$K$2:$M$447,2,FALSE)","v":"RNILCB02X0B_C"},"RNILCB02X0B_C AT%M5230.0 :BOOL; (*基础照明B 2层全局启停控制*)","RNILCB02X0B_C           AT%M5230.0     :BOOL; (*基础照明B 2层全局启停控制*)"]
["照明控制箱","RNI","M","03X0B","启停控制","5232.0",null,"验证通过","BOOL","基础照明B 3层全局启停控制",{"$f":"B95&VLOOKUP(A95,List!$B$3:$D$445,2,FALSE)&D95&\"_\"&VLOOKUP(E95,List!$K$2:$M$447,2,FALSE)","v":"RNILCB03X0B_C"},"RNILCB03X0B_C AT%M5232.0 :BOOL; (*基础照明B 3层全局启停控制*)","RNILCB03X0B_C           AT%M5232.0     :BOOL; (*基础照明B 3层全局启停控制*)"]
["照明控制箱","RNI","M","04X0B","启停控制","5234.0",null,"验证通过","BOOL","基础照明B 4层全局启停控制",{"$f":"B96&VLOOKUP(A96,List!$B$3:$D$445,2,FALSE)&D96&\"_\"&VLOOKUP(E96,List!$K$2:$M$447,2,FALSE)","v":"RNILCB04X0B_C"},"RNILCB04X0B_C AT%M5234.0 :BOOL; (*基础照明B 4层全局启停控制*)","RNILCB04X0B_C           AT%M5234.0     :BOOL; (*基础照明B 4层全局启停控制*)"]
["照明控制箱","RNI","M","05X0B","启停控制","5236.0",null,"验证通过","BOOL","基础照明B 5层全局启停控制",{"$f":"B97&VLOOKUP(A97,List!$B$3:$D$445,2,FALSE)&D97&\"_\"&VLOOKUP(E97,List!$K$2:$M$447,2,FALSE)","v":"RNILCB05X0B_C"},"RNILCB05X0B_C AT%M5236.0 :BOOL; (*基础照明B 5层全局启停控制*)","RNILCB05X0B_C           AT%M5236.0     :BOOL; (*基础照明B 5层全局启停控制*)"]
["照明控制箱","RNI","M","06X0B","启停控制","5238.0",null,"验证通过","BOOL","基础照明B 6层全局启停控制",{"$f":"B98&VLOOKUP(A98,List!$B$3:$D$445,2,FALSE)&D98&\"_\"&VLOOKUP(E98,List!$K$2:$M$447,2,FALSE)","v":"RNILCB06X0B_C"},"RNILCB06X0B_C AT%M5238.0 :BOOL; (*基础照明B 6层全局启停控制*)","RNILCB06X0B_C           AT%M5238.0     :BOOL; (*基础照明B 6层全局启停控制*)"]
["照明控制箱","RNI","M","07X0B","启停控制","5240.0",null,"验证通过","BOOL","基础照明B 7层全局启停控制",{"$f":"B99&VLOOKUP(A99,List!$B$3:$D$445,2,FALSE)&D99&\"_\"&VLOOKUP(E99,List!$K$2:$M$447,2,FALSE)","v":"RNILCB07X0B_C"},"RNILCB07X0B_C AT%M5240.0 :BOOL; (*基础照明B 7层全局启停控制*)","RNILCB07X0B_C           AT%M5240.0     :BOOL; (*基础照明B 7层全局启停控制*)"]
["照明控制箱","RNI","M","08X0B","启停控制","5242.0",null,"验证通过","BOOL","基础照明B 8层全局启停控制",{"$f":"B100&VLOOKUP(A100,List!$B$3:$D$445,2,FALSE)&D100&\"_\"&VLOOKUP(E100,List!$K$2:$M$447,2,FALSE)","v":"RNILCB08X0B_C"},"RNILCB08X0B_C AT%M5242.0 :BOOL; (*基础照明B 8层全局启停控制*)","RNILCB08X0B_C           AT%M5242.0     :BOOL; (*基础照明B 8层全局启停控制*)"]
["照明控制箱","RNI","M","B3X0C","启停控制","5244.0",null,"验证通过","BOOL","灯带 B3层全局启停控制",{"$f":"B101&VLOOKUP(A101,List!$B$3:$D$445,2,FALSE)&D101&\"_\"&VLOOKUP(E101,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB3X0C_C"},"RNILCBB3X0C_C AT%M5244.0 :BOOL; (*灯带 B3层全局启停控制*)","RNILCBB3X0C_C           AT%M5244.0     :BOOL; (*灯带 B3层全局启停控制*)"]
["照明控制箱","RNI","M","B2X0C","启停控制","5246.0",null,"验证通过","BOOL","灯带 B2层全局启停控制",{"$f":"B102&VLOOKUP(A102,List!$B$3:$D$445,2,FALSE)&D102&\"_\"&VLOOKUP(E102,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB2X0C_C"},"RNILCBB2X0C_C AT%M5246.0 :BOOL; (*灯带 B2层全局启停控制*)","RNILCBB2X0C_C           AT%M5246.0     :BOOL; (*灯带 B2层全局启停控制*)"]
["照明控制箱","RNI","M","B1X0C","启停控制","5248.0",null,"验证通过","BOOL","灯带 B1层全局启停控制",{"$f":"B103&VLOOKUP(A103,List!$B$3:$D$445,2,FALSE)&D103&\"_\"&VLOOKUP(E103,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB1X0C_C"},"RNILCBB1X0C_C AT%M5248.0 :BOOL; (*灯带 B1层全局启停控制*)","RNILCBB1X0C_C           AT%M5248.0     :BOOL; (*灯带 B1层全局启停控制*)"]
["照明控制箱","RNI","M","01X0C","启停控制","5250.0",null,"验证通过","BOOL","灯带 1层全局启停控制",{"$f":"B104&VLOOKUP(A104,List!$B$3:$D$445,2,FALSE)&D104&\"_\"&VLOOKUP(E104,List!$K$2:$M$447,2,FALSE)","v":"RNILCB01X0C_C"},"RNILCB01X0C_C AT%M5250.0 :BOOL; (*灯带 1层全局启停控制*)","RNILCB01X0C_C           AT%M5250.0     :BOOL; (*灯带 1层全局启停控制*)"]
["照明控制箱","RNI","M","02X0C","启停控制","5252.0",null,"验证通过","BOOL","灯带 2层全局启停控制",{"$f":"B105&VLOOKUP(A105,List!$B$3:$D$445,2,FALSE)&D105&\"_\"&VLOOKUP(E105,List!$K$2:$M$447,2,FALSE)","v":"RNILCB02X0C_C"},"RNILCB02X0C_C AT%M5252.0 :BOOL; (*灯带 2层全局启停控制*)","RNILCB02X0C_C           AT%M5252.0     :BOOL; (*灯带 2层全局启停控制*)"]
["照明控制箱","RNI","M","03X0C","启停控制","5254.0",null,"验证通过","BOOL","灯带 3层全局启停控制",{"$f":"B106&VLOOKUP(A106,List!$B$3:$D$445,2,FALSE)&D106&\"_\"&VLOOKUP(E106,List!$K$2:$M$447,2,FALSE)","v":"RNILCB03X0C_C"},"RNILCB03X0C_C AT%M5254.0 :BOOL; (*灯带 3层全局启停控制*)","RNILCB03X0C_C           AT%M5254.0     :BOOL; (*灯带 3层全局启停控制*)"]
["照明控制箱","RNI","M","04X0C","启停控制","5256.0",null,"验证通过","BOOL","灯带 4层全局启停控制",{"$f":"B107&VLOOKUP(A107,List!$B$3:$D$445,2,FALSE)&D107&\"_\"&VLOOKUP(E107,List!$K$2:$M$447,2,FALSE)","v":"RNILCB04X0C_C"},"RNILCB04X0C_C AT%M5256.0 :BOOL; (*灯带 4层全局启停控制*)","RNILCB04X0C_C           AT%M5256.0     :BOOL; (*灯带 4层全局启停控制*)"]
["照明控制箱","RNI","M","05X0C","启停控制","5258.0",null,"验证通过","BOOL","灯带 5层全局启停控制",{"$f":"B108&VLOOKUP(A108,List!$B$3:$D$445,2,FALSE)&D108&\"_\"&VLOOKUP(E108,List!$K$2:$M$447,2,FALSE)","v":"RNILCB05X0C_C"},"RNILCB05X0C_C AT%M5258.0 :BOOL; (*灯带 5层全局启停控制*)","RNILCB05X0C_C           AT%M5258.0     :BOOL; (*灯带 5层全局启停控制*)"]
["照明控制箱","RNI","M","06X0C","启停控制","5260.0",null,"验证通过","BOOL","灯带 6层全局启停控制",{"$f":"B109&VLOOKUP(A109,List!$B$3:$D$445,2,FALSE)&D109&\"_\"&VLOOKUP(E109,List!$K$2:$M$447,2,FALSE)","v":"RNILCB06X0C_C"},"RNILCB06X0C_C AT%M5260.0 :BOOL; (*灯带 6层全局启停控制*)","RNILCB06X0C_C           AT%M5260.0     :BOOL; (*灯带 6层全局启停控制*)"]
["照明控制箱","RNI","M","07X0C","启停控制","5262.0",null,"验证通过","BOOL","灯带 7层全局启停控制",{"$f":"B110&VLOOKUP(A110,List!$B$3:$D$445,2,FALSE)&D110&\"_\"&VLOOKUP(E110,List!$K$2:$M$447,2,FALSE)","v":"RNILCB07X0C_C"},"RNILCB07X0C_C AT%M5262.0 :BOOL; (*灯带 7层全局启停控制*)","RNILCB07X0C_C           AT%M5262.0     :BOOL; (*灯带 7层全局启停控制*)"]
["照明控制箱","RNI","M","08X0C","启停控制","5264.0",null,"验证通过","BOOL","灯带 8层全局启停控制",{"$f":"B111&VLOOKUP(A111,List!$B$3:$D$445,2,FALSE)&D111&\"_\"&VLOOKUP(E111,List!$K$2:$M$447,2,FALSE)","v":"RNILCB08X0C_C"},"RNILCB08X0C_C AT%M5264.0 :BOOL; (*灯带 8层全局启停控制*)","RNILCB08X0C_C           AT%M5264.0     :BOOL; (*灯带 8层全局启停控制*)"]
["照明控制箱","RNI","M","B3X0D","启停控制","5266.0",null,"验证通过","BOOL","广告 B3层全局启停控制",{"$f":"B112&VLOOKUP(A112,List!$B$3:$D$445,2,FALSE)&D112&\"_\"&VLOOKUP(E112,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB3X0D_C"},"RNILCBB3X0D_C AT%M5266.0 :BOOL; (*广告 B3层全局启停控制*)","RNILCBB3X0D_C           AT%M5266.0     :BOOL; (*广告 B3层全局启停控制*)"]
["照明控制箱","RNI","M","B2X0D","启停控制","5268.0",null,"验证通过","BOOL","广告 B2层全局启停控制",{"$f":"B113&VLOOKUP(A113,List!$B$3:$D$445,2,FALSE)&D113&\"_\"&VLOOKUP(E113,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB2X0D_C"},"RNILCBB2X0D_C AT%M5268.0 :BOOL; (*广告 B2层全局启停控制*)","RNILCBB2X0D_C           AT%M5268.0     :BOOL; (*广告 B2层全局启停控制*)"]
["照明控制箱","RNI","M","B1X0D","启停控制","5270.0",null,"验证通过","BOOL","广告 B1层全局启停控制",{"$f":"B114&VLOOKUP(A114,List!$B$3:$D$445,2,FALSE)&D114&\"_\"&VLOOKUP(E114,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB1X0D_C"},"RNILCBB1X0D_C AT%M5270.0 :BOOL; (*广告 B1层全局启停控制*)","RNILCBB1X0D_C           AT%M5270.0     :BOOL; (*广告 B1层全局启停控制*)"]
["照明控制箱","RNI","M","01X0D","启停控制","5272.0",null,"验证通过","BOOL","广告 1层全局启停控制",{"$f":"B115&VLOOKUP(A115,List!$B$3:$D$445,2,FALSE)&D115&\"_\"&VLOOKUP(E115,List!$K$2:$M$447,2,FALSE)","v":"RNILCB01X0D_C"},"RNILCB01X0D_C AT%M5272.0 :BOOL; (*广告 1层全局启停控制*)","RNILCB01X0D_C           AT%M5272.0     :BOOL; (*广告 1层全局启停控制*)"]
["照明控制箱","RNI","M","02X0D","启停控制","5274.0",null,"验证通过","BOOL","广告 2层全局启停控制",{"$f":"B116&VLOOKUP(A116,List!$B$3:$D$445,2,FALSE)&D116&\"_\"&VLOOKUP(E116,List!$K$2:$M$447,2,FALSE)","v":"RNILCB02X0D_C"},"RNILCB02X0D_C AT%M5274.0 :BOOL; (*广告 2层全局启停控制*)","RNILCB02X0D_C           AT%M5274.0     :BOOL; (*广告 2层全局启停控制*)"]
["照明控制箱","RNI","M","03X0D","启停控制","5276.0",null,"验证通过","BOOL","广告 3层全局启停控制",{"$f":"B117&VLOOKUP(A117,List!$B$3:$D$445,2,FALSE)&D117&\"_\"&VLOOKUP(E117,List!$K$2:$M$447,2,FALSE)","v":"RNILCB03X0D_C"},"RNILCB03X0D_C AT%M5276.0 :BOOL; (*广告 3层全局启停控制*)","RNILCB03X0D_C           AT%M5276.0     :BOOL; (*广告 3层全局启停控制*)"]
["照明控制箱","RNI","M","04X0D","启停控制","5278.0",null,"验证通过","BOOL","广告 4层全局启停控制",{"$f":"B118&VLOOKUP(A118,List!$B$3:$D$445,2,FALSE)&D118&\"_\"&VLOOKUP(E118,List!$K$2:$M$447,2,FALSE)","v":"RNILCB04X0D_C"},"RNILCB04X0D_C AT%M5278.0 :BOOL; (*广告 4层全局启停控制*)","RNILCB04X0D_C           AT%M5278.0     :BOOL; (*广告 4层全局启停控制*)"]
["照明控制箱","RNI","M","05X0D","启停控制","5280.0",null,"验证通过","BOOL","广告 5层全局启停控制",{"$f":"B119&VLOOKUP(A119,List!$B$3:$D$445,2,FALSE)&D119&\"_\"&VLOOKUP(E119,List!$K$2:$M$447,2,FALSE)","v":"RNILCB05X0D_C"},"RNILCB05X0D_C AT%M5280.0 :BOOL; (*广告 5层全局启停控制*)","RNILCB05X0D_C           AT%M5280.0     :BOOL; (*广告 5层全局启停控制*)"]
["照明控制箱","RNI","M","06X0D","启停控制","5282.0",null,"验证通过","BOOL","广告 6层全局启停控制",{"$f":"B120&VLOOKUP(A120,List!$B$3:$D$445,2,FALSE)&D120&\"_\"&VLOOKUP(E120,List!$K$2:$M$447,2,FALSE)","v":"RNILCB06X0D_C"},"RNILCB06X0D_C AT%M5282.0 :BOOL; (*广告 6层全局启停控制*)","RNILCB06X0D_C           AT%M5282.0     :BOOL; (*广告 6层全局启停控制*)"]
["照明控制箱","RNI","M","07X0D","启停控制","5284.0",null,"验证通过","BOOL","广告 7层全局启停控制",{"$f":"B121&VLOOKUP(A121,List!$B$3:$D$445,2,FALSE)&D121&\"_\"&VLOOKUP(E121,List!$K$2:$M$447,2,FALSE)","v":"RNILCB07X0D_C"},"RNILCB07X0D_C AT%M5284.0 :BOOL; (*广告 7层全局启停控制*)","RNILCB07X0D_C           AT%M5284.0     :BOOL; (*广告 7层全局启停控制*)"]
["照明控制箱","RNI","M","08X0D","启停控制","5286.0",null,"验证通过","BOOL","广告 8层全局启停控制",{"$f":"B122&VLOOKUP(A122,List!$B$3:$D$445,2,FALSE)&D122&\"_\"&VLOOKUP(E122,List!$K$2:$M$447,2,FALSE)","v":"RNILCB08X0D_C"},"RNILCB08X0D_C AT%M5286.0 :BOOL; (*广告 8层全局启停控制*)","RNILCB08X0D_C           AT%M5286.0     :BOOL; (*广告 8层全局启停控制*)"]
["照明控制箱","RNI","M","B3X0E","启停控制","5288.0",null,"验证通过","BOOL","标识 B3层全局启停控制",{"$f":"B123&VLOOKUP(A123,List!$B$3:$D$445,2,FALSE)&D123&\"_\"&VLOOKUP(E123,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB3X0E_C"},"RNILCBB3X0E_C AT%M5288.0 :BOOL; (*标识 B3层全局启停控制*)","RNILCBB3X0E_C           AT%M5288.0     :BOOL; (*标识 B3层全局启停控制*)"]
["照明控制箱","RNI","M","B2X0E","启停控制","5290.0",null,"验证通过","BOOL","标识 B2层全局启停控制",{"$f":"B124&VLOOKUP(A124,List!$B$3:$D$445,2,FALSE)&D124&\"_\"&VLOOKUP(E124,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB2X0E_C"},"RNILCBB2X0E_C AT%M5290.0 :BOOL; (*标识 B2层全局启停控制*)","RNILCBB2X0E_C           AT%M5290.0     :BOOL; (*标识 B2层全局启停控制*)"]
["照明控制箱","RNI","M","B1X0E","启停控制","5292.0",null,"验证通过","BOOL","标识 B1层全局启停控制",{"$f":"B125&VLOOKUP(A125,List!$B$3:$D$445,2,FALSE)&D125&\"_\"&VLOOKUP(E125,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB1X0E_C"},"RNILCBB1X0E_C AT%M5292.0 :BOOL; (*标识 B1层全局启停控制*)","RNILCBB1X0E_C           AT%M5292.0     :BOOL; (*标识 B1层全局启停控制*)"]
["照明控制箱","RNI","M","01X0E","启停控制","5294.0",null,"验证通过","BOOL","标识 1层全局启停控制",{"$f":"B126&VLOOKUP(A126,List!$B$3:$D$445,2,FALSE)&D126&\"_\"&VLOOKUP(E126,List!$K$2:$M$447,2,FALSE)","v":"RNILCB01X0E_C"},"RNILCB01X0E_C AT%M5294.0 :BOOL; (*标识 1层全局启停控制*)","RNILCB01X0E_C           AT%M5294.0     :BOOL; (*标识 1层全局启停控制*)"]
["照明控制箱","RNI","M","02X0E","启停控制","5296.0",null,"验证通过","BOOL","标识 2层全局启停控制",{"$f":"B127&VLOOKUP(A127,List!$B$3:$D$445,2,FALSE)&D127&\"_\"&VLOOKUP(E127,List!$K$2:$M$447,2,FALSE)","v":"RNILCB02X0E_C"},"RNILCB02X0E_C AT%M5296.0 :BOOL; (*标识 2层全局启停控制*)","RNILCB02X0E_C           AT%M5296.0     :BOOL; (*标识 2层全局启停控制*)"]
["照明控制箱","RNI","M","03X0E","启停控制","5298.0",null,{"$f":"IF((IF(OR(I128=\"INT\",I128=\"WORD\",I128=\"BOOL\"),MOD(F128,2),MOD(F128,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","标识 3层全局启停控制",{"$f":"B128&VLOOKUP(A128,List!$B$3:$D$445,2,FALSE)&D128&\"_\"&VLOOKUP(E128,List!$K$2:$M$447,2,FALSE)","v":"RNILCB03X0E_C"},"RNILCB03X0E_C AT%M5298.0 :BOOL; (*标识 3层全局启停控制*)","RNILCB03X0E_C           AT%M5298.0     :BOOL; (*标识 3层全局启停控制*)"]
["照明控制箱","RNI","M","04X0E","启停控制","5300.0",null,"验证通过","BOOL","标识 4层全局启停控制",{"$f":"B129&VLOOKUP(A129,List!$B$3:$D$445,2,FALSE)&D129&\"_\"&VLOOKUP(E129,List!$K$2:$M$447,2,FALSE)","v":"RNILCB04X0E_C"},"RNILCB04X0E_C AT%M5300.0 :BOOL; (*标识 4层全局启停控制*)","RNILCB04X0E_C           AT%M5300.0     :BOOL; (*标识 4层全局启停控制*)"]
["照明控制箱","RNI","M","05X0E","启停控制","5302.0",null,"验证通过","BOOL","标识 5层全局启停控制",{"$f":"B130&VLOOKUP(A130,List!$B$3:$D$445,2,FALSE)&D130&\"_\"&VLOOKUP(E130,List!$K$2:$M$447,2,FALSE)","v":"RNILCB05X0E_C"},"RNILCB05X0E_C AT%M5302.0 :BOOL; (*标识 5层全局启停控制*)","RNILCB05X0E_C           AT%M5302.0     :BOOL; (*标识 5层全局启停控制*)"]
["照明控制箱","RNI","M","06X0E","启停控制","5304.0",null,"验证通过","BOOL","标识 6层全局启停控制",{"$f":"B131&VLOOKUP(A131,List!$B$3:$D$445,2,FALSE)&D131&\"_\"&VLOOKUP(E131,List!$K$2:$M$447,2,FALSE)","v":"RNILCB06X0E_C"},"RNILCB06X0E_C AT%M5304.0 :BOOL; (*标识 6层全局启停控制*)","RNILCB06X0E_C           AT%M5304.0     :BOOL; (*标识 6层全局启停控制*)"]
["照明控制箱","RNI","M","07X0E","启停控制","5306.0",null,"验证通过","BOOL","标识 7层全局启停控制",{"$f":"B132&VLOOKUP(A132,List!$B$3:$D$445,2,FALSE)&D132&\"_\"&VLOOKUP(E132,List!$K$2:$M$447,2,FALSE)","v":"RNILCB07X0E_C"},"RNILCB07X0E_C AT%M5306.0 :BOOL; (*标识 7层全局启停控制*)","RNILCB07X0E_C           AT%M5306.0     :BOOL; (*标识 7层全局启停控制*)"]
["照明控制箱","RNI","M","08X0E","启停控制","5308.0",null,"验证通过","BOOL","标识 8层全局启停控制",{"$f":"B133&VLOOKUP(A133,List!$B$3:$D$445,2,FALSE)&D133&\"_\"&VLOOKUP(E133,List!$K$2:$M$447,2,FALSE)","v":"RNILCB08X0E_C"},"RNILCB08X0E_C AT%M5308.0 :BOOL; (*标识 8层全局启停控制*)","RNILCB08X0E_C           AT%M5308.0     :BOOL; (*标识 8层全局启停控制*)"]
["照明控制箱","RNI","M","B3X0F","启停控制","5310.0",null,"验证通过","BOOL","备用 B3层全局启停控制",{"$f":"B134&VLOOKUP(A134,List!$B$3:$D$445,2,FALSE)&D134&\"_\"&VLOOKUP(E134,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB3X0F_C"},"RNILCBB3X0F_C AT%M5310.0 :BOOL; (*备用 B3层全局启停控制*)","RNILCBB3X0F_C           AT%M5310.0     :BOOL; (*备用 B3层全局启停控制*)"]
["照明控制箱","RNI","M","B2X0F","启停控制","5312.0",null,"验证通过","BOOL","备用 B2层全局启停控制",{"$f":"B135&VLOOKUP(A135,List!$B$3:$D$445,2,FALSE)&D135&\"_\"&VLOOKUP(E135,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB2X0F_C"},"RNILCBB2X0F_C AT%M5312.0 :BOOL; (*备用 B2层全局启停控制*)","RNILCBB2X0F_C           AT%M5312.0     :BOOL; (*备用 B2层全局启停控制*)"]
["照明控制箱","RNI","M","B1X0F","启停控制","5314.0",null,"验证通过","BOOL","备用 B1层全局启停控制",{"$f":"B136&VLOOKUP(A136,List!$B$3:$D$445,2,FALSE)&D136&\"_\"&VLOOKUP(E136,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB1X0F_C"},"RNILCBB1X0F_C AT%M5314.0 :BOOL; (*备用 B1层全局启停控制*)","RNILCBB1X0F_C           AT%M5314.0     :BOOL; (*备用 B1层全局启停控制*)"]
["照明控制箱","RNI","M","01X0F","启停控制","5316.0",null,"验证通过","BOOL","备用 1层全局启停控制",{"$f":"B137&VLOOKUP(A137,List!$B$3:$D$445,2,FALSE)&D137&\"_\"&VLOOKUP(E137,List!$K$2:$M$447,2,FALSE)","v":"RNILCB01X0F_C"},"RNILCB01X0F_C AT%M5316.0 :BOOL; (*备用 1层全局启停控制*)","RNILCB01X0F_C           AT%M5316.0     :BOOL; (*备用 1层全局启停控制*)"]
["照明控制箱","RNI","M","02X0F","启停控制","5318.0",null,"验证通过","BOOL","备用 2层全局启停控制",{"$f":"B138&VLOOKUP(A138,List!$B$3:$D$445,2,FALSE)&D138&\"_\"&VLOOKUP(E138,List!$K$2:$M$447,2,FALSE)","v":"RNILCB02X0F_C"},"RNILCB02X0F_C AT%M5318.0 :BOOL; (*备用 2层全局启停控制*)","RNILCB02X0F_C           AT%M5318.0     :BOOL; (*备用 2层全局启停控制*)"]
["照明控制箱","RNI","M","03X0F","启停控制","5320.0",null,"验证通过","BOOL","备用 3层全局启停控制",{"$f":"B139&VLOOKUP(A139,List!$B$3:$D$445,2,FALSE)&D139&\"_\"&VLOOKUP(E139,List!$K$2:$M$447,2,FALSE)","v":"RNILCB03X0F_C"},"RNILCB03X0F_C AT%M5320.0 :BOOL; (*备用 3层全局启停控制*)","RNILCB03X0F_C           AT%M5320.0     :BOOL; (*备用 3层全局启停控制*)"]
["照明控制箱","RNI","M","04X0F","启停控制","5322.0",null,"验证通过","BOOL","备用 4层全局启停控制",{"$f":"B140&VLOOKUP(A140,List!$B$3:$D$445,2,FALSE)&D140&\"_\"&VLOOKUP(E140,List!$K$2:$M$447,2,FALSE)","v":"RNILCB04X0F_C"},"RNILCB04X0F_C AT%M5322.0 :BOOL; (*备用 4层全局启停控制*)","RNILCB04X0F_C           AT%M5322.0     :BOOL; (*备用 4层全局启停控制*)"]
["照明控制箱","RNI","M","05X0F","启停控制","5324.0",null,"验证通过","BOOL","备用 5层全局启停控制",{"$f":"B141&VLOOKUP(A141,List!$B$3:$D$445,2,FALSE)&D141&\"_\"&VLOOKUP(E141,List!$K$2:$M$447,2,FALSE)","v":"RNILCB05X0F_C"},{"$f":"K141&\" \"&\"AT%\"&C141&F141&\" \"&\":\"&I141&\";\"&\" \"&\"(*\"&J141&\"*)\"","v":"RNILCB05X0F_C AT%M5324.0 :BOOL; (*备用 5层全局启停控制*)"},{"$f":"REPLACE(REPLACE(L141,SEARCH(\"AT%\",L141),,REPT(\" \",25-SEARCH(\"AT%\",L141))),SEARCH(\":\",REPLACE(L141,SEARCH(\"AT%\",L141),,REPT(\" \",25-SEARCH(\"AT%\",L141)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L141,SEARCH(\"AT%\",L141),,REPT(\" \",25-SEARCH(\"AT%\",L141))))))","v":"RNILCB05X0F_C           AT%M5324.0     :BOOL; (*备用 5层全局启停控制*)"}]
["照明控制箱","RNI","M","06X0F","启停控制","5326.0",null,"验证通过","BOOL","备用 6层全局启停控制",{"$f":"B142&VLOOKUP(A142,List!$B$3:$D$445,2,FALSE)&D142&\"_\"&VLOOKUP(E142,List!$K$2:$M$447,2,FALSE)","v":"RNILCB06X0F_C"},"RNILCB06X0F_C AT%M5326.0 :BOOL; (*备用 6层全局启停控制*)","RNILCB06X0F_C           AT%M5326.0     :BOOL; (*备用 6层全局启停控制*)"]
["照明控制箱","RNI","M","07X0F","启停控制","5328.0",null,"验证通过","BOOL","备用 7层全局启停控制",{"$f":"B143&VLOOKUP(A143,List!$B$3:$D$445,2,FALSE)&D143&\"_\"&VLOOKUP(E143,List!$K$2:$M$447,2,FALSE)","v":"RNILCB07X0F_C"},"RNILCB07X0F_C AT%M5328.0 :BOOL; (*备用 7层全局启停控制*)","RNILCB07X0F_C           AT%M5328.0     :BOOL; (*备用 7层全局启停控制*)"]
["照明控制箱","RNI","M","08X0F","启停控制",{"$f":"IF(OR(I143=\"REAL\",I143=\"DWORD\",I143=\"DINT\"),(IF(OR(I144=\"REAL\",I144=\"DWORD\",I144=\"DINT\"),F143+4+MOD(F143,4),F143+4)),(IF(OR(I144=\"REAL\",I144=\"DWORD\",I144=\"DINT\"),F143+4+MOD(F143,4),F143+2)))&\".0\"","v":"5330.0"},null,"验证通过","BOOL","备用 8层全局启停控制",{"$f":"B144&VLOOKUP(A144,List!$B$3:$D$445,2,FALSE)&D144&\"_\"&VLOOKUP(E144,List!$K$2:$M$447,2,FALSE)","v":"RNILCB08X0F_C"},"RNILCB08X0F_C AT%M5330.0 :BOOL; (*备用 8层全局启停控制*)","RNILCB08X0F_C           AT%M5330.0     :BOOL; (*备用 8层全局启停控制*)"]
["照明控制箱","RNI","M","B3X0G","启停控制","5332.0",null,"验证通过","BOOL","备用 B3层全局启停控制",{"$f":"B145&VLOOKUP(A145,List!$B$3:$D$445,2,FALSE)&D145&\"_\"&VLOOKUP(E145,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB3X0G_C"},"RNILCBB3X0G_C AT%M5332.0 :BOOL; (*备用 B3层全局启停控制*)","RNILCBB3X0G_C           AT%M5332.0     :BOOL; (*备用 B3层全局启停控制*)"]
["照明控制箱","RNI","M","B2X0G","启停控制","5334.0",null,"验证通过","BOOL","备用 B2层全局启停控制",{"$f":"B146&VLOOKUP(A146,List!$B$3:$D$445,2,FALSE)&D146&\"_\"&VLOOKUP(E146,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB2X0G_C"},"RNILCBB2X0G_C AT%M5334.0 :BOOL; (*备用 B2层全局启停控制*)","RNILCBB2X0G_C           AT%M5334.0     :BOOL; (*备用 B2层全局启停控制*)"]
["照明控制箱","RNI","M","B1X0G","启停控制","5336.0",null,"验证通过","BOOL","备用 B1层全局启停控制",{"$f":"B147&VLOOKUP(A147,List!$B$3:$D$445,2,FALSE)&D147&\"_\"&VLOOKUP(E147,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB1X0G_C"},"RNILCBB1X0G_C AT%M5336.0 :BOOL; (*备用 B1层全局启停控制*)","RNILCBB1X0G_C           AT%M5336.0     :BOOL; (*备用 B1层全局启停控制*)"]
["照明控制箱","RNI","M","01X0G","启停控制","5338.0",null,"验证通过","BOOL","备用 1层全局启停控制",{"$f":"B148&VLOOKUP(A148,List!$B$3:$D$445,2,FALSE)&D148&\"_\"&VLOOKUP(E148,List!$K$2:$M$447,2,FALSE)","v":"RNILCB01X0G_C"},"RNILCB01X0G_C AT%M5338.0 :BOOL; (*备用 1层全局启停控制*)","RNILCB01X0G_C           AT%M5338.0     :BOOL; (*备用 1层全局启停控制*)"]
["照明控制箱","RNI","M","02X0G","启停控制","5340.0",null,"验证通过","BOOL","备用 2层全局启停控制",{"$f":"B149&VLOOKUP(A149,List!$B$3:$D$445,2,FALSE)&D149&\"_\"&VLOOKUP(E149,List!$K$2:$M$447,2,FALSE)","v":"RNILCB02X0G_C"},"RNILCB02X0G_C AT%M5340.0 :BOOL; (*备用 2层全局启停控制*)","RNILCB02X0G_C           AT%M5340.0     :BOOL; (*备用 2层全局启停控制*)"]
["照明控制箱","RNI","M","03X0G","启停控制","5342.0",null,"验证通过","BOOL","备用 3层全局启停控制",{"$f":"B150&VLOOKUP(A150,List!$B$3:$D$445,2,FALSE)&D150&\"_\"&VLOOKUP(E150,List!$K$2:$M$447,2,FALSE)","v":"RNILCB03X0G_C"},"RNILCB03X0G_C AT%M5342.0 :BOOL; (*备用 3层全局启停控制*)","RNILCB03X0G_C           AT%M5342.0     :BOOL; (*备用 3层全局启停控制*)"]
["照明控制箱","RNI","M","04X0G","启停控制","5344.0",null,"验证通过","BOOL","备用 4层全局启停控制",{"$f":"B151&VLOOKUP(A151,List!$B$3:$D$445,2,FALSE)&D151&\"_\"&VLOOKUP(E151,List!$K$2:$M$447,2,FALSE)","v":"RNILCB04X0G_C"},"RNILCB04X0G_C AT%M5344.0 :BOOL; (*备用 4层全局启停控制*)","RNILCB04X0G_C           AT%M5344.0     :BOOL; (*备用 4层全局启停控制*)"]
["照明控制箱","RNI","M","05X0G","启停控制","5346.0",null,"验证通过","BOOL","备用 5层全局启停控制",{"$f":"B152&VLOOKUP(A152,List!$B$3:$D$445,2,FALSE)&D152&\"_\"&VLOOKUP(E152,List!$K$2:$M$447,2,FALSE)","v":"RNILCB05X0G_C"},"RNILCB05X0G_C AT%M5346.0 :BOOL; (*备用 5层全局启停控制*)","RNILCB05X0G_C           AT%M5346.0     :BOOL; (*备用 5层全局启停控制*)"]
["照明控制箱","RNI","M","06X0G","启停控制","5348.0",null,"验证通过","BOOL","备用 6层全局启停控制",{"$f":"B153&VLOOKUP(A153,List!$B$3:$D$445,2,FALSE)&D153&\"_\"&VLOOKUP(E153,List!$K$2:$M$447,2,FALSE)","v":"RNILCB06X0G_C"},"RNILCB06X0G_C AT%M5348.0 :BOOL; (*备用 6层全局启停控制*)","RNILCB06X0G_C           AT%M5348.0     :BOOL; (*备用 6层全局启停控制*)"]
["照明控制箱","RNI","M","07X0G","启停控制","5350.0",null,"验证通过","BOOL","备用 7层全局启停控制",{"$f":"B154&VLOOKUP(A154,List!$B$3:$D$445,2,FALSE)&D154&\"_\"&VLOOKUP(E154,List!$K$2:$M$447,2,FALSE)","v":"RNILCB07X0G_C"},"RNILCB07X0G_C AT%M5350.0 :BOOL; (*备用 7层全局启停控制*)","RNILCB07X0G_C           AT%M5350.0     :BOOL; (*备用 7层全局启停控制*)"]
["照明控制箱","RNI","M","08X0G","启停控制","5352.0",null,"验证通过","BOOL","备用 8层全局启停控制",{"$f":"B155&VLOOKUP(A155,List!$B$3:$D$445,2,FALSE)&D155&\"_\"&VLOOKUP(E155,List!$K$2:$M$447,2,FALSE)","v":"RNILCB08X0G_C"},"RNILCB08X0G_C AT%M5352.0 :BOOL; (*备用 8层全局启停控制*)","RNILCB08X0G_C           AT%M5352.0     :BOOL; (*备用 8层全局启停控制*)"]
["照明控制箱","RNI","M","B3X0H","启停控制","5354.0",null,"验证通过","BOOL","备用 B3层全局启停控制",{"$f":"B156&VLOOKUP(A156,List!$B$3:$D$445,2,FALSE)&D156&\"_\"&VLOOKUP(E156,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB3X0H_C"},"RNILCBB3X0H_C AT%M5354.0 :BOOL; (*备用 B3层全局启停控制*)","RNILCBB3X0H_C           AT%M5354.0     :BOOL; (*备用 B3层全局启停控制*)"]
["照明控制箱","RNI","M","B2X0H","启停控制","5356.0",null,"验证通过","BOOL","备用 B2层全局启停控制",{"$f":"B157&VLOOKUP(A157,List!$B$3:$D$445,2,FALSE)&D157&\"_\"&VLOOKUP(E157,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB2X0H_C"},"RNILCBB2X0H_C AT%M5356.0 :BOOL; (*备用 B2层全局启停控制*)","RNILCBB2X0H_C           AT%M5356.0     :BOOL; (*备用 B2层全局启停控制*)"]
["照明控制箱","RNI","M","B1X0H","启停控制","5358.0",null,"验证通过","BOOL","备用 B1层全局启停控制",{"$f":"B158&VLOOKUP(A158,List!$B$3:$D$445,2,FALSE)&D158&\"_\"&VLOOKUP(E158,List!$K$2:$M$447,2,FALSE)","v":"RNILCBB1X0H_C"},"RNILCBB1X0H_C AT%M5358.0 :BOOL; (*备用 B1层全局启停控制*)","RNILCBB1X0H_C           AT%M5358.0     :BOOL; (*备用 B1层全局启停控制*)"]
["照明控制箱","RNI","M","01X0H","启停控制","5360.0",null,"验证通过","BOOL","备用 1层全局启停控制",{"$f":"B159&VLOOKUP(A159,List!$B$3:$D$445,2,FALSE)&D159&\"_\"&VLOOKUP(E159,List!$K$2:$M$447,2,FALSE)","v":"RNILCB01X0H_C"},"RNILCB01X0H_C AT%M5360.0 :BOOL; (*备用 1层全局启停控制*)","RNILCB01X0H_C           AT%M5360.0     :BOOL; (*备用 1层全局启停控制*)"]
["照明控制箱","RNI","M","02X0H","启停控制","5362.0",null,"验证通过","BOOL","备用 2层全局启停控制",{"$f":"B160&VLOOKUP(A160,List!$B$3:$D$445,2,FALSE)&D160&\"_\"&VLOOKUP(E160,List!$K$2:$M$447,2,FALSE)","v":"RNILCB02X0H_C"},"RNILCB02X0H_C AT%M5362.0 :BOOL; (*备用 2层全局启停控制*)","RNILCB02X0H_C           AT%M5362.0     :BOOL; (*备用 2层全局启停控制*)"]
["照明控制箱","RNI","M","03X0H","启停控制","5364.0",null,"验证通过","BOOL","备用 3层全局启停控制",{"$f":"B161&VLOOKUP(A161,List!$B$3:$D$445,2,FALSE)&D161&\"_\"&VLOOKUP(E161,List!$K$2:$M$447,2,FALSE)","v":"RNILCB03X0H_C"},"RNILCB03X0H_C AT%M5364.0 :BOOL; (*备用 3层全局启停控制*)","RNILCB03X0H_C           AT%M5364.0     :BOOL; (*备用 3层全局启停控制*)"]
["照明控制箱","RNI","M","04X0H","启停控制","5366.0",null,"验证通过","BOOL","备用 4层全局启停控制",{"$f":"B162&VLOOKUP(A162,List!$B$3:$D$445,2,FALSE)&D162&\"_\"&VLOOKUP(E162,List!$K$2:$M$447,2,FALSE)","v":"RNILCB04X0H_C"},"RNILCB04X0H_C AT%M5366.0 :BOOL; (*备用 4层全局启停控制*)","RNILCB04X0H_C           AT%M5366.0     :BOOL; (*备用 4层全局启停控制*)"]
["照明控制箱","RNI","M","05X0H","启停控制","5368.0",null,"验证通过","BOOL","备用 5层全局启停控制",{"$f":"B163&VLOOKUP(A163,List!$B$3:$D$445,2,FALSE)&D163&\"_\"&VLOOKUP(E163,List!$K$2:$M$447,2,FALSE)","v":"RNILCB05X0H_C"},"RNILCB05X0H_C AT%M5368.0 :BOOL; (*备用 5层全局启停控制*)","RNILCB05X0H_C           AT%M5368.0     :BOOL; (*备用 5层全局启停控制*)"]
["照明控制箱","RNI","M","06X0H","启停控制","5370.0",null,"验证通过","BOOL","备用 6层全局启停控制",{"$f":"B164&VLOOKUP(A164,List!$B$3:$D$445,2,FALSE)&D164&\"_\"&VLOOKUP(E164,List!$K$2:$M$447,2,FALSE)","v":"RNILCB06X0H_C"},"RNILCB06X0H_C AT%M5370.0 :BOOL; (*备用 6层全局启停控制*)","RNILCB06X0H_C           AT%M5370.0     :BOOL; (*备用 6层全局启停控制*)"]
["照明控制箱","RNI","M","07X0H","启停控制","5372.0",null,"验证通过","BOOL","备用 7层全局启停控制",{"$f":"B165&VLOOKUP(A165,List!$B$3:$D$445,2,FALSE)&D165&\"_\"&VLOOKUP(E165,List!$K$2:$M$447,2,FALSE)","v":"RNILCB07X0H_C"},"RNILCB07X0H_C AT%M5372.0 :BOOL; (*备用 7层全局启停控制*)","RNILCB07X0H_C           AT%M5372.0     :BOOL; (*备用 7层全局启停控制*)"]
["照明控制箱","RNI","M","08X0H","启停控制","5374.0",null,"验证通过","BOOL","备用 8层全局启停控制",{"$f":"B166&VLOOKUP(A166,List!$B$3:$D$445,2,FALSE)&D166&\"_\"&VLOOKUP(E166,List!$K$2:$M$447,2,FALSE)","v":"RNILCB08X0H_C"},"RNILCB08X0H_C AT%M5374.0 :BOOL; (*备用 8层全局启停控制*)","RNILCB08X0H_C           AT%M5374.0     :BOOL; (*备用 8层全局启停控制*)"]
["P新风机组","RNI","M","05X00","设定温度值","5380.0",null,"验证通过","REAL","新风机组5层温度全局设定",{"$f":"B167&VLOOKUP(A167,List!$B$3:$D$445,2,FALSE)&D167&\"_\"&VLOOKUP(E167,List!$K$2:$M$447,2,FALSE)","v":"RNIPAU05X00_TSET"},"RNIPAU05X00_TSET AT%M5380.0 :REAL; (*新风机组5层温度全局设定*)","RNIPAU05X00_TSET        AT%M5380.0     :REAL; (*新风机组5层温度全局设定*)"]
["P新风机组","RNI","M","06X00","设定温度值","5384.0",null,"验证通过","REAL","新风机组6层温度全局设定",{"$f":"B168&VLOOKUP(A168,List!$B$3:$D$445,2,FALSE)&D168&\"_\"&VLOOKUP(E168,List!$K$2:$M$447,2,FALSE)","v":"RNIPAU06X00_TSET"},"RNIPAU06X00_TSET AT%M5384.0 :REAL; (*新风机组6层温度全局设定*)","RNIPAU06X00_TSET        AT%M5384.0     :REAL; (*新风机组6层温度全局设定*)"]
["P新风机组","RNI","M","07X00","设定温度值","5388.0",null,"验证通过","REAL","新风机组7层温度全局设定",{"$f":"B169&VLOOKUP(A169,List!$B$3:$D$445,2,FALSE)&D169&\"_\"&VLOOKUP(E169,List!$K$2:$M$447,2,FALSE)","v":"RNIPAU07X00_TSET"},"RNIPAU07X00_TSET AT%M5388.0 :REAL; (*新风机组7层温度全局设定*)","RNIPAU07X00_TSET        AT%M5388.0     :REAL; (*新风机组7层温度全局设定*)"]
["P新风机组","RNI","M","08X00","设定温度值","5392.0",null,"验证通过","REAL","新风机组8层温度全局设定",{"$f":"B170&VLOOKUP(A170,List!$B$3:$D$445,2,FALSE)&D170&\"_\"&VLOOKUP(E170,List!$K$2:$M$447,2,FALSE)","v":"RNIPAU08X00_TSET"},"RNIPAU08X00_TSET AT%M5392.0 :REAL; (*新风机组8层温度全局设定*)","RNIPAU08X00_TSET        AT%M5392.0     :REAL; (*新风机组8层温度全局设定*)"]
["P新风机组","RNI","M","09X00","设定温度值","5396.0",null,"验证通过","REAL","新风机组9层温度全局设定",{"$f":"B171&VLOOKUP(A171,List!$B$3:$D$445,2,FALSE)&D171&\"_\"&VLOOKUP(E171,List!$K$2:$M$447,2,FALSE)","v":"RNIPAU09X00_TSET"},"RNIPAU09X00_TSET AT%M5396.0 :REAL; (*新风机组9层温度全局设定*)","RNIPAU09X00_TSET        AT%M5396.0     :REAL; (*新风机组9层温度全局设定*)"]
["P新风机组","RNI","M","05X00","季节模式","5400.0",null,"验证通过","INT","新风机组5层季节模式全局设定",{"$f":"B172&VLOOKUP(A172,List!$B$3:$D$445,2,FALSE)&D172&\"_\"&VLOOKUP(E172,List!$K$2:$M$447,2,FALSE)","v":"RNIPAU05X00_SM"},"RNIPAU05X00_SM AT%M5400.0 :INT; (*新风机组5层季节模式全局设定*)","RNIPAU05X00_SM          AT%M5400.0     :INT; (*新风机组5层季节模式全局设定*)"]
["P新风机组","RNI","M","06X00","季节模式","5402.0",null,"验证通过","INT","新风机组6层季节模式全局设定",{"$f":"B173&VLOOKUP(A173,List!$B$3:$D$445,2,FALSE)&D173&\"_\"&VLOOKUP(E173,List!$K$2:$M$447,2,FALSE)","v":"RNIPAU06X00_SM"},"RNIPAU06X00_SM AT%M5402.0 :INT; (*新风机组6层季节模式全局设定*)","RNIPAU06X00_SM          AT%M5402.0     :INT; (*新风机组6层季节模式全局设定*)"]
["P新风机组","RNI","M","07X00","季节模式","5404.0",null,"验证通过","INT","新风机组7层季节模式全局设定",{"$f":"B174&VLOOKUP(A174,List!$B$3:$D$445,2,FALSE)&D174&\"_\"&VLOOKUP(E174,List!$K$2:$M$447,2,FALSE)","v":"RNIPAU07X00_SM"},"RNIPAU07X00_SM AT%M5404.0 :INT; (*新风机组7层季节模式全局设定*)","RNIPAU07X00_SM          AT%M5404.0     :INT; (*新风机组7层季节模式全局设定*)"]
["P新风机组","RNI","M","08X00","季节模式","5406.0",null,"验证通过","INT","新风机组8层季节模式全局设定",{"$f":"B175&VLOOKUP(A175,List!$B$3:$D$445,2,FALSE)&D175&\"_\"&VLOOKUP(E175,List!$K$2:$M$447,2,FALSE)","v":"RNIPAU08X00_SM"},"RNIPAU08X00_SM AT%M5406.0 :INT; (*新风机组8层季节模式全局设定*)","RNIPAU08X00_SM          AT%M5406.0     :INT; (*新风机组8层季节模式全局设定*)"]
["P新风机组","RNI","M","09X00","季节模式","5408.0",null,"验证通过","INT","新风机组9层季节模式全局设定",{"$f":"B176&VLOOKUP(A176,List!$B$3:$D$445,2,FALSE)&D176&\"_\"&VLOOKUP(E176,List!$K$2:$M$447,2,FALSE)","v":"RNIPAU09X00_SM"},"RNIPAU09X00_SM AT%M5408.0 :INT; (*新风机组9层季节模式全局设定*)","RNIPAU09X00_SM          AT%M5408.0     :INT; (*新风机组9层季节模式全局设定*)"]
["P新风机组","RNI","M","05X00","程序控制","5410.0",null,"验证通过","BOOL","新风机组5层启停控制",{"$f":"B177&VLOOKUP(A177,List!$B$3:$D$445,2,FALSE)&D177&\"_\"&VLOOKUP(E177,List!$K$2:$M$447,2,FALSE)","v":"RNIPAU05X00_PC"},"RNIPAU05X00_PC AT%M5410.0 :BOOL; (*新风机组5层启停控制*)","RNIPAU05X00_PC          AT%M5410.0     :BOOL; (*新风机组5层启停控制*)"]
["P新风机组","RNI","M","06X00","程序控制","5412.0",null,"验证通过","BOOL","新风机组6层启停控制",{"$f":"B178&VLOOKUP(A178,List!$B$3:$D$445,2,FALSE)&D178&\"_\"&VLOOKUP(E178,List!$K$2:$M$447,2,FALSE)","v":"RNIPAU06X00_PC"},"RNIPAU06X00_PC AT%M5412.0 :BOOL; (*新风机组6层启停控制*)","RNIPAU06X00_PC          AT%M5412.0     :BOOL; (*新风机组6层启停控制*)"]
["P新风机组","RNI","M","07X00","程序控制","5414.0",null,"验证通过","BOOL","新风机组7层启停控制",{"$f":"B179&VLOOKUP(A179,List!$B$3:$D$445,2,FALSE)&D179&\"_\"&VLOOKUP(E179,List!$K$2:$M$447,2,FALSE)","v":"RNIPAU07X00_PC"},"RNIPAU07X00_PC AT%M5414.0 :BOOL; (*新风机组7层启停控制*)","RNIPAU07X00_PC          AT%M5414.0     :BOOL; (*新风机组7层启停控制*)"]
["P新风机组","RNI","M","08X00","程序控制","5416.0",null,"验证通过","BOOL","新风机组8层启停控制",{"$f":"B180&VLOOKUP(A180,List!$B$3:$D$445,2,FALSE)&D180&\"_\"&VLOOKUP(E180,List!$K$2:$M$447,2,FALSE)","v":"RNIPAU08X00_PC"},"RNIPAU08X00_PC AT%M5416.0 :BOOL; (*新风机组8层启停控制*)","RNIPAU08X00_PC          AT%M5416.0     :BOOL; (*新风机组8层启停控制*)"]
["P新风机组","RNI","M","09X00","程序控制","5418.0",null,"验证通过","BOOL","新风机组9层启停控制",{"$f":"B181&VLOOKUP(A181,List!$B$3:$D$445,2,FALSE)&D181&\"_\"&VLOOKUP(E181,List!$K$2:$M$447,2,FALSE)","v":"RNIPAU09X00_PC"},"RNIPAU09X00_PC AT%M5418.0 :BOOL; (*新风机组9层启停控制*)","RNIPAU09X00_PC          AT%M5418.0     :BOOL; (*新风机组9层启停控制*)"]
["送风机","RNI","M","B3X00","程序控制","5420.0",null,"验证通过","BOOL","送风机B3层启停控制",{"$f":"B182&VLOOKUP(A182,List!$B$3:$D$445,2,FALSE)&D182&\"_\"&VLOOKUP(E182,List!$K$2:$M$447,2,FALSE)","v":"RNISAFB3X00_PC"},"RNISAFB3X00_PC AT%M5420.0 :BOOL; (*送风机B3层启停控制*)","RNISAFB3X00_PC          AT%M5420.0     :BOOL; (*送风机B3层启停控制*)"]
["送风机","RNI","M","B2X00","程序控制","5422.0",null,"验证通过","BOOL","送风机B2层启停控制",{"$f":"B183&VLOOKUP(A183,List!$B$3:$D$445,2,FALSE)&D183&\"_\"&VLOOKUP(E183,List!$K$2:$M$447,2,FALSE)","v":"RNISAFB2X00_PC"},"RNISAFB2X00_PC AT%M5422.0 :BOOL; (*送风机B2层启停控制*)","RNISAFB2X00_PC          AT%M5422.0     :BOOL; (*送风机B2层启停控制*)"]
["送风机","RNI","M","B1X00","程序控制","5424.0",null,"验证通过","BOOL","送风机B1层启停控制",{"$f":"B184&VLOOKUP(A184,List!$B$3:$D$445,2,FALSE)&D184&\"_\"&VLOOKUP(E184,List!$K$2:$M$447,2,FALSE)","v":"RNISAFB1X00_PC"},"RNISAFB1X00_PC AT%M5424.0 :BOOL; (*送风机B1层启停控制*)","RNISAFB1X00_PC          AT%M5424.0     :BOOL; (*送风机B1层启停控制*)"]
["送风机","RNI","M","05X00","程序控制","5426.0",null,"验证通过","BOOL","送风机5层启停控制",{"$f":"B185&VLOOKUP(A185,List!$B$3:$D$445,2,FALSE)&D185&\"_\"&VLOOKUP(E185,List!$K$2:$M$447,2,FALSE)","v":"RNISAF05X00_PC"},"RNISAF05X00_PC AT%M5426.0 :BOOL; (*送风机5层启停控制*)","RNISAF05X00_PC          AT%M5426.0     :BOOL; (*送风机5层启停控制*)"]
["送风机","RNI","M","06X00","程序控制","5428.0",null,"验证通过","BOOL","送风机6层启停控制",{"$f":"B186&VLOOKUP(A186,List!$B$3:$D$445,2,FALSE)&D186&\"_\"&VLOOKUP(E186,List!$K$2:$M$447,2,FALSE)","v":"RNISAF06X00_PC"},"RNISAF06X00_PC AT%M5428.0 :BOOL; (*送风机6层启停控制*)","RNISAF06X00_PC          AT%M5428.0     :BOOL; (*送风机6层启停控制*)"]
["送风机","RNI","M","07X00","程序控制","5430.0",null,"验证通过","BOOL","送风机7层启停控制",{"$f":"B187&VLOOKUP(A187,List!$B$3:$D$445,2,FALSE)&D187&\"_\"&VLOOKUP(E187,List!$K$2:$M$447,2,FALSE)","v":"RNISAF07X00_PC"},"RNISAF07X00_PC AT%M5430.0 :BOOL; (*送风机7层启停控制*)","RNISAF07X00_PC          AT%M5430.0     :BOOL; (*送风机7层启停控制*)"]
["送风机","RNI","M","08X00","程序控制","5432.0",null,"验证通过","BOOL","送风机8层启停控制",{"$f":"B188&VLOOKUP(A188,List!$B$3:$D$445,2,FALSE)&D188&\"_\"&VLOOKUP(E188,List!$K$2:$M$447,2,FALSE)","v":"RNISAF08X00_PC"},"RNISAF08X00_PC AT%M5432.0 :BOOL; (*送风机8层启停控制*)","RNISAF08X00_PC          AT%M5432.0     :BOOL; (*送风机8层启停控制*)"]
["送风机","RNI","M","09X00","程序控制","5434.0",null,"验证通过","BOOL","送风机9层启停控制",{"$f":"B189&VLOOKUP(A189,List!$B$3:$D$445,2,FALSE)&D189&\"_\"&VLOOKUP(E189,List!$K$2:$M$447,2,FALSE)","v":"RNISAF09X00_PC"},"RNISAF09X00_PC AT%M5434.0 :BOOL; (*送风机9层启停控制*)","RNISAF09X00_PC          AT%M5434.0     :BOOL; (*送风机9层启停控制*)"]
["排风机","RNI","M","B3X00","程序控制","5436.0",null,"验证通过","BOOL","排风机B3层启停控制",{"$f":"B190&VLOOKUP(A190,List!$B$3:$D$445,2,FALSE)&D190&\"_\"&VLOOKUP(E190,List!$K$2:$M$447,2,FALSE)","v":"RNIEAFB3X00_PC"},"RNIEAFB3X00_PC AT%M5436.0 :BOOL; (*排风机B3层启停控制*)","RNIEAFB3X00_PC          AT%M5436.0     :BOOL; (*排风机B3层启停控制*)"]
["排风机","RNI","M","B2X00","程序控制","5438.0",null,"验证通过","BOOL","排风机B2层启停控制",{"$f":"B191&VLOOKUP(A191,List!$B$3:$D$445,2,FALSE)&D191&\"_\"&VLOOKUP(E191,List!$K$2:$M$447,2,FALSE)","v":"RNIEAFB2X00_PC"},"RNIEAFB2X00_PC AT%M5438.0 :BOOL; (*排风机B2层启停控制*)","RNIEAFB2X00_PC          AT%M5438.0     :BOOL; (*排风机B2层启停控制*)"]
["排风机","RNI","M","B1X00","程序控制","5440.0",null,{"$f":"IF((IF(OR(I192=\"INT\",I192=\"WORD\",I192=\"BOOL\"),MOD(F192,2),MOD(F192,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"BOOL","排风机B1层启停控制",{"$f":"B192&VLOOKUP(A192,List!$B$3:$D$445,2,FALSE)&D192&\"_\"&VLOOKUP(E192,List!$K$2:$M$447,2,FALSE)","v":"RNIEAFB1X00_PC"},"RNIEAFB1X00_PC AT%M5440.0 :BOOL; (*排风机B1层启停控制*)","RNIEAFB1X00_PC          AT%M5440.0     :BOOL; (*排风机B1层启停控制*)"]
["排风机","RNI","M","05X00","程序控制","5442.0",null,"验证通过","BOOL","排风机5层启停控制",{"$f":"B193&VLOOKUP(A193,List!$B$3:$D$445,2,FALSE)&D193&\"_\"&VLOOKUP(E193,List!$K$2:$M$447,2,FALSE)","v":"RNIEAF05X00_PC"},"RNIEAF05X00_PC AT%M5442.0 :BOOL; (*排风机5层启停控制*)","RNIEAF05X00_PC          AT%M5442.0     :BOOL; (*排风机5层启停控制*)"]
["排风机","RNI","M","06X00","程序控制","5444.0",null,"验证通过","BOOL","排风机6层启停控制",{"$f":"B194&VLOOKUP(A194,List!$B$3:$D$445,2,FALSE)&D194&\"_\"&VLOOKUP(E194,List!$K$2:$M$447,2,FALSE)","v":"RNIEAF06X00_PC"},"RNIEAF06X00_PC AT%M5444.0 :BOOL; (*排风机6层启停控制*)","RNIEAF06X00_PC          AT%M5444.0     :BOOL; (*排风机6层启停控制*)"]
["排风机","RNI","M","07X00","程序控制","5446.0",null,"验证通过","BOOL","排风机7层启停控制",{"$f":"B195&VLOOKUP(A195,List!$B$3:$D$445,2,FALSE)&D195&\"_\"&VLOOKUP(E195,List!$K$2:$M$447,2,FALSE)","v":"RNIEAF07X00_PC"},"RNIEAF07X00_PC AT%M5446.0 :BOOL; (*排风机7层启停控制*)","RNIEAF07X00_PC          AT%M5446.0     :BOOL; (*排风机7层启停控制*)"]
["排风机","RNI","M","08X00","程序控制","5448.0",null,"验证通过","BOOL","排风机8层启停控制",{"$f":"B196&VLOOKUP(A196,List!$B$3:$D$445,2,FALSE)&D196&\"_\"&VLOOKUP(E196,List!$K$2:$M$447,2,FALSE)","v":"RNIEAF08X00_PC"},"RNIEAF08X00_PC AT%M5448.0 :BOOL; (*排风机8层启停控制*)","RNIEAF08X00_PC          AT%M5448.0     :BOOL; (*排风机8层启停控制*)"]
["排风机","RNI","M","09X00","程序控制","5450.0",null,"验证通过","BOOL","排风机9层启停控制",{"$f":"B197&VLOOKUP(A197,List!$B$3:$D$445,2,FALSE)&D197&\"_\"&VLOOKUP(E197,List!$K$2:$M$447,2,FALSE)","v":"RNIEAF09X00_PC"},"RNIEAF09X00_PC AT%M5450.0 :BOOL; (*排风机9层启停控制*)","RNIEAF09X00_PC          AT%M5450.0     :BOOL; (*排风机9层启停控制*)"]
["风幕机","RNI","M","B3X00","程序控制","5452.0",null,"验证通过","BOOL","风幕机B3层启停控制",{"$f":"B198&VLOOKUP(A198,List!$B$3:$D$445,2,FALSE)&D198&\"_\"&VLOOKUP(E198,List!$K$2:$M$447,2,FALSE)","v":"RNIACB3X00_PC"},"RNIACB3X00_PC AT%M5452.0 :BOOL; (*风幕机B3层启停控制*)","RNIACB3X00_PC           AT%M5452.0     :BOOL; (*风幕机B3层启停控制*)"]
["风幕机","RNI","M","B2X00","程序控制","5454.0",null,"验证通过","BOOL","风幕机B2层启停控制",{"$f":"B199&VLOOKUP(A199,List!$B$3:$D$445,2,FALSE)&D199&\"_\"&VLOOKUP(E199,List!$K$2:$M$447,2,FALSE)","v":"RNIACB2X00_PC"},"RNIACB2X00_PC AT%M5454.0 :BOOL; (*风幕机B2层启停控制*)","RNIACB2X00_PC           AT%M5454.0     :BOOL; (*风幕机B2层启停控制*)"]
["风幕机","RNI","M","B1X00","程序控制","5456.0",null,"验证通过","BOOL","风幕机B1层启停控制",{"$f":"B200&VLOOKUP(A200,List!$B$3:$D$445,2,FALSE)&D200&\"_\"&VLOOKUP(E200,List!$K$2:$M$447,2,FALSE)","v":"RNIACB1X00_PC"},"RNIACB1X00_PC AT%M5456.0 :BOOL; (*风幕机B1层启停控制*)","RNIACB1X00_PC           AT%M5456.0     :BOOL; (*风幕机B1层启停控制*)"]
["风幕机","RNI","M","01X00","程序控制","5458.0",null,"验证通过","BOOL","风幕机1层启停控制",{"$f":"B201&VLOOKUP(A201,List!$B$3:$D$445,2,FALSE)&D201&\"_\"&VLOOKUP(E201,List!$K$2:$M$447,2,FALSE)","v":"RNIAC01X00_PC"},"RNIAC01X00_PC AT%M5458.0 :BOOL; (*风幕机1层启停控制*)","RNIAC01X00_PC           AT%M5458.0     :BOOL; (*风幕机1层启停控制*)"]
["风幕机","RNI","M","02X00","程序控制","5460.0",null,"验证通过","BOOL","风幕机2层启停控制",{"$f":"B202&VLOOKUP(A202,List!$B$3:$D$445,2,FALSE)&D202&\"_\"&VLOOKUP(E202,List!$K$2:$M$447,2,FALSE)","v":"RNIAC02X00_PC"},"RNIAC02X00_PC AT%M5460.0 :BOOL; (*风幕机2层启停控制*)","RNIAC02X00_PC           AT%M5460.0     :BOOL; (*风幕机2层启停控制*)"]
["风幕机","RNI","M","03X00","程序控制","5462.0",null,"验证通过","BOOL","风幕机3层启停控制",{"$f":"B203&VLOOKUP(A203,List!$B$3:$D$445,2,FALSE)&D203&\"_\"&VLOOKUP(E203,List!$K$2:$M$447,2,FALSE)","v":"RNIAC03X00_PC"},"RNIAC03X00_PC AT%M5462.0 :BOOL; (*风幕机3层启停控制*)","RNIAC03X00_PC           AT%M5462.0     :BOOL; (*风幕机3层启停控制*)"]
["风幕机","RNI","M","04X00","程序控制","5464.0",null,"验证通过","BOOL","风幕机4层启停控制",{"$f":"B204&VLOOKUP(A204,List!$B$3:$D$445,2,FALSE)&D204&\"_\"&VLOOKUP(E204,List!$K$2:$M$447,2,FALSE)","v":"RNIAC04X00_PC"},"RNIAC04X00_PC AT%M5464.0 :BOOL; (*风幕机4层启停控制*)","RNIAC04X00_PC           AT%M5464.0     :BOOL; (*风幕机4层启停控制*)"]
["风幕机","RNI","M","05X00","程序控制","5466.0",null,"验证通过","BOOL","风幕机5层启停控制",{"$f":"B205&VLOOKUP(A205,List!$B$3:$D$445,2,FALSE)&D205&\"_\"&VLOOKUP(E205,List!$K$2:$M$447,2,FALSE)","v":"RNIAC05X00_PC"},{"$f":"K205&\" \"&\"AT%\"&C205&F205&\" \"&\":\"&I205&\";\"&\" \"&\"(*\"&J205&\"*)\"","v":"RNIAC05X00_PC AT%M5466.0 :BOOL; (*风幕机5层启停控制*)"},{"$f":"REPLACE(REPLACE(L205,SEARCH(\"AT%\",L205),,REPT(\" \",25-SEARCH(\"AT%\",L205))),SEARCH(\":\",REPLACE(L205,SEARCH(\"AT%\",L205),,REPT(\" \",25-SEARCH(\"AT%\",L205)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L205,SEARCH(\"AT%\",L205),,REPT(\" \",25-SEARCH(\"AT%\",L205))))))","v":"RNIAC05X00_PC           AT%M5466.0     :BOOL; (*风幕机5层启停控制*)"}]
["风幕机","RNI","M","06X00","程序控制","5468.0",null,"验证通过","BOOL","风幕机6层启停控制",{"$f":"B206&VLOOKUP(A206,List!$B$3:$D$445,2,FALSE)&D206&\"_\"&VLOOKUP(E206,List!$K$2:$M$447,2,FALSE)","v":"RNIAC06X00_PC"},"RNIAC06X00_PC AT%M5468.0 :BOOL; (*风幕机6层启停控制*)","RNIAC06X00_PC           AT%M5468.0     :BOOL; (*风幕机6层启停控制*)"]
["风幕机","RNI","M","07X00","程序控制","5470.0",null,"验证通过","BOOL","风幕机7层启停控制",{"$f":"B207&VLOOKUP(A207,List!$B$3:$D$445,2,FALSE)&D207&\"_\"&VLOOKUP(E207,List!$K$2:$M$447,2,FALSE)","v":"RNIAC07X00_PC"},"RNIAC07X00_PC AT%M5470.0 :BOOL; (*风幕机7层启停控制*)","RNIAC07X00_PC           AT%M5470.0     :BOOL; (*风幕机7层启停控制*)"]
["风幕机","RNI","M","08X00","程序控制",{"$f":"IF(OR(I207=\"REAL\",I207=\"DWORD\",I207=\"DINT\"),(IF(OR(I208=\"REAL\",I208=\"DWORD\",I208=\"DINT\"),F207+4+MOD(F207,4),F207+4)),(IF(OR(I208=\"REAL\",I208=\"DWORD\",I208=\"DINT\"),F207+4+MOD(F207,4),F207+2)))&\".0\"","v":"5472.0"},null,"验证通过","BOOL","风幕机8层启停控制",{"$f":"B208&VLOOKUP(A208,List!$B$3:$D$445,2,FALSE)&D208&\"_\"&VLOOKUP(E208,List!$K$2:$M$447,2,FALSE)","v":"RNIAC08X00_PC"},"RNIAC08X00_PC AT%M5472.0 :BOOL; (*风幕机8层启停控制*)","RNIAC08X00_PC           AT%M5472.0     :BOOL; (*风幕机8层启停控制*)"]
["水幕机","RNI","M","B3X00","程序控制","5474.0",null,"验证通过","BOOL","水幕机B3层启停控制",{"$f":"B209&VLOOKUP(A209,List!$B$3:$D$445,2,FALSE)&D209&\"_\"&VLOOKUP(E209,List!$K$2:$M$447,2,FALSE)","v":"RNIWACB3X00_PC"},"RNIWACB3X00_PC AT%M5474.0 :BOOL; (*水幕机B3层启停控制*)","RNIWACB3X00_PC          AT%M5474.0     :BOOL; (*水幕机B3层启停控制*)"]
["水幕机","RNI","M","B2X00","程序控制","5476.0",null,"验证通过","BOOL","水幕机B2层启停控制",{"$f":"B210&VLOOKUP(A210,List!$B$3:$D$445,2,FALSE)&D210&\"_\"&VLOOKUP(E210,List!$K$2:$M$447,2,FALSE)","v":"RNIWACB2X00_PC"},"RNIWACB2X00_PC AT%M5476.0 :BOOL; (*水幕机B2层启停控制*)","RNIWACB2X00_PC          AT%M5476.0     :BOOL; (*水幕机B2层启停控制*)"]
["水幕机","RNI","M","B1X00","程序控制","5478.0",null,"验证通过","BOOL","水幕机B1层启停控制",{"$f":"B211&VLOOKUP(A211,List!$B$3:$D$445,2,FALSE)&D211&\"_\"&VLOOKUP(E211,List!$K$2:$M$447,2,FALSE)","v":"RNIWACB1X00_PC"},"RNIWACB1X00_PC AT%M5478.0 :BOOL; (*水幕机B1层启停控制*)","RNIWACB1X00_PC          AT%M5478.0     :BOOL; (*水幕机B1层启停控制*)"]
["水幕机","RNI","M","01X00","程序控制","5480.0",null,"验证通过","BOOL","水幕机1层启停控制",{"$f":"B212&VLOOKUP(A212,List!$B$3:$D$445,2,FALSE)&D212&\"_\"&VLOOKUP(E212,List!$K$2:$M$447,2,FALSE)","v":"RNIWAC01X00_PC"},"RNIWAC01X00_PC AT%M5480.0 :BOOL; (*水幕机1层启停控制*)","RNIWAC01X00_PC          AT%M5480.0     :BOOL; (*水幕机1层启停控制*)"]
["水幕机","RNI","M","02X00","程序控制","5482.0",null,"验证通过","BOOL","水幕机2层启停控制",{"$f":"B213&VLOOKUP(A213,List!$B$3:$D$445,2,FALSE)&D213&\"_\"&VLOOKUP(E213,List!$K$2:$M$447,2,FALSE)","v":"RNIWAC02X00_PC"},"RNIWAC02X00_PC AT%M5482.0 :BOOL; (*水幕机2层启停控制*)","RNIWAC02X00_PC          AT%M5482.0     :BOOL; (*水幕机2层启停控制*)"]
["水幕机","RNI","M","03X00","程序控制","5484.0",null,"验证通过","BOOL","水幕机3层启停控制",{"$f":"B214&VLOOKUP(A214,List!$B$3:$D$445,2,FALSE)&D214&\"_\"&VLOOKUP(E214,List!$K$2:$M$447,2,FALSE)","v":"RNIWAC03X00_PC"},"RNIWAC03X00_PC AT%M5484.0 :BOOL; (*水幕机3层启停控制*)","RNIWAC03X00_PC          AT%M5484.0     :BOOL; (*水幕机3层启停控制*)"]
["水幕机","RNI","M","04X00","程序控制","5486.0",null,"验证通过","BOOL","水幕机4层启停控制",{"$f":"B215&VLOOKUP(A215,List!$B$3:$D$445,2,FALSE)&D215&\"_\"&VLOOKUP(E215,List!$K$2:$M$447,2,FALSE)","v":"RNIWAC04X00_PC"},"RNIWAC04X00_PC AT%M5486.0 :BOOL; (*水幕机4层启停控制*)","RNIWAC04X00_PC          AT%M5486.0     :BOOL; (*水幕机4层启停控制*)"]
["水幕机","RNI","M","05X00","程序控制","5488.0",null,"验证通过","BOOL","水幕机5层启停控制",{"$f":"B216&VLOOKUP(A216,List!$B$3:$D$445,2,FALSE)&D216&\"_\"&VLOOKUP(E216,List!$K$2:$M$447,2,FALSE)","v":"RNIWAC05X00_PC"},"RNIWAC05X00_PC AT%M5488.0 :BOOL; (*水幕机5层启停控制*)","RNIWAC05X00_PC          AT%M5488.0     :BOOL; (*水幕机5层启停控制*)"]
["水幕机","RNI","M","06X00","程序控制","5490.0",null,"验证通过","BOOL","水幕机6层启停控制",{"$f":"B217&VLOOKUP(A217,List!$B$3:$D$445,2,FALSE)&D217&\"_\"&VLOOKUP(E217,List!$K$2:$M$447,2,FALSE)","v":"RNIWAC06X00_PC"},"RNIWAC06X00_PC AT%M5490.0 :BOOL; (*水幕机6层启停控制*)","RNIWAC06X00_PC          AT%M5490.0     :BOOL; (*水幕机6层启停控制*)"]
["水幕机","RNI","M","07X00","程序控制","5492.0",null,"验证通过","BOOL","水幕机7层启停控制",{"$f":"B218&VLOOKUP(A218,List!$B$3:$D$445,2,FALSE)&D218&\"_\"&VLOOKUP(E218,List!$K$2:$M$447,2,FALSE)","v":"RNIWAC07X00_PC"},"RNIWAC07X00_PC AT%M5492.0 :BOOL; (*水幕机7层启停控制*)","RNIWAC07X00_PC          AT%M5492.0     :BOOL; (*水幕机7层启停控制*)"]
["水幕机","RNI","M","08X00","程序控制","5494.0",null,"验证通过","BOOL","水幕机8层启停控制",{"$f":"B219&VLOOKUP(A219,List!$B$3:$D$445,2,FALSE)&D219&\"_\"&VLOOKUP(E219,List!$K$2:$M$447,2,FALSE)","v":"RNIWAC08X00_PC"},"RNIWAC08X00_PC AT%M5494.0 :BOOL; (*水幕机8层启停控制*)","RNIWAC08X00_PC          AT%M5494.0     :BOOL; (*水幕机8层启停控制*)"]
{"$rows_empty":12}
["从CPU-->主控CPU",{"$nulls":5},"接收地址.auto"]
["命令","RNQ","M","00000","心跳值","6000.0",{"$f":"F233-1024&\".0\"","v":"4976.0"},{"$f":"IF((IF(OR(I233=\"INT\",I233=\"WORD\",I233=\"BOOL\"),MOD(F233,2),MOD(F233,4)))=0,\"验证通过\",\"验证失败\")","v":"验证通过"},"INT","心跳值",{"$f":"B233&VLOOKUP(A233,List!$B$3:$D$445,2,FALSE)&D233&\"_\"&VLOOKUP(E233,List!$K$2:$M$447,2,FALSE)","v":"RNQCMD00000_DHV"},{"$f":"K233&\" \"&\"AT%\"&C233&F233&\" \"&\":\"&I233&\";\"&\" \"&\"(*\"&J233&\"*)\"","v":"RNQCMD00000_DHV AT%M6000.0 :INT; (*心跳值*)"},{"$f":"REPLACE(REPLACE(L233,SEARCH(\"AT%\",L233),,REPT(\" \",25-SEARCH(\"AT%\",L233))),SEARCH(\":\",REPLACE(L233,SEARCH(\"AT%\",L233),,REPT(\" \",25-SEARCH(\"AT%\",L233)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L233,SEARCH(\"AT%\",L233),,REPT(\" \",25-SEARCH(\"AT%\",L233))))))","v":"RNQCMD00000_DHV         AT%M6000.0     :INT; (*心跳值*)"}]
[{"$nulls":10},{"$f":"B234&VLOOKUP(A234,List!$B$3:$D$445,2,FALSE)&D234&\"_\"&VLOOKUP(E234,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"K234&\" \"&\"AT%\"&C234&F234&\" \"&\":\"&I234&\";\"&\" \"&\"(*\"&J234&\"*)\"","v":{"$error":"#N/A"}},{"$f":"REPLACE(REPLACE(L234,SEARCH(\"AT%\",L234),,REPT(\" \",25-SEARCH(\"AT%\",L234))),SEARCH(\":\",REPLACE(L234,SEARCH(\"AT%\",L234),,REPT(\" \",25-SEARCH(\"AT%\",L234)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L234,SEARCH(\"AT%\",L234),,REPT(\" \",25-SEARCH(\"AT%\",L234))))))","v":{"$error":"#N/A"}}]
[{"$nulls":10},{"$f":"B235&VLOOKUP(A235,List!$B$3:$D$445,2,FALSE)&D235&\"_\"&VLOOKUP(E235,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B236&VLOOKUP(A236,List!$B$3:$D$445,2,FALSE)&D236&\"_\"&VLOOKUP(E236,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B237&VLOOKUP(A237,List!$B$3:$D$445,2,FALSE)&D237&\"_\"&VLOOKUP(E237,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B238&VLOOKUP(A238,List!$B$3:$D$445,2,FALSE)&D238&\"_\"&VLOOKUP(E238,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B239&VLOOKUP(A239,List!$B$3:$D$445,2,FALSE)&D239&\"_\"&VLOOKUP(E239,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B240&VLOOKUP(A240,List!$B$3:$D$445,2,FALSE)&D240&\"_\"&VLOOKUP(E240,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B241&VLOOKUP(A241,List!$B$3:$D$445,2,FALSE)&D241&\"_\"&VLOOKUP(E241,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B242&VLOOKUP(A242,List!$B$3:$D$445,2,FALSE)&D242&\"_\"&VLOOKUP(E242,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B243&VLOOKUP(A243,List!$B$3:$D$445,2,FALSE)&D243&\"_\"&VLOOKUP(E243,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B244&VLOOKUP(A244,List!$B$3:$D$445,2,FALSE)&D244&\"_\"&VLOOKUP(E244,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B245&VLOOKUP(A245,List!$B$3:$D$445,2,FALSE)&D245&\"_\"&VLOOKUP(E245,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B246&VLOOKUP(A246,List!$B$3:$D$445,2,FALSE)&D246&\"_\"&VLOOKUP(E246,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B247&VLOOKUP(A247,List!$B$3:$D$445,2,FALSE)&D247&\"_\"&VLOOKUP(E247,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B248&VLOOKUP(A248,List!$B$3:$D$445,2,FALSE)&D248&\"_\"&VLOOKUP(E248,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B249&VLOOKUP(A249,List!$B$3:$D$445,2,FALSE)&D249&\"_\"&VLOOKUP(E249,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B250&VLOOKUP(A250,List!$B$3:$D$445,2,FALSE)&D250&\"_\"&VLOOKUP(E250,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B251&VLOOKUP(A251,List!$B$3:$D$445,2,FALSE)&D251&\"_\"&VLOOKUP(E251,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B252&VLOOKUP(A252,List!$B$3:$D$445,2,FALSE)&D252&\"_\"&VLOOKUP(E252,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B253&VLOOKUP(A253,List!$B$3:$D$445,2,FALSE)&D253&\"_\"&VLOOKUP(E253,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B254&VLOOKUP(A254,List!$B$3:$D$445,2,FALSE)&D254&\"_\"&VLOOKUP(E254,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B255&VLOOKUP(A255,List!$B$3:$D$445,2,FALSE)&D255&\"_\"&VLOOKUP(E255,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B256&VLOOKUP(A256,List!$B$3:$D$445,2,FALSE)&D256&\"_\"&VLOOKUP(E256,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"K256&\" \"&\"AT%\"&C256&F256&\" \"&\":\"&I256&\";\"&\" \"&\"(*\"&J256&\"*)\"","v":{"$error":"#N/A"}},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B257&VLOOKUP(A257,List!$B$3:$D$445,2,FALSE)&D257&\"_\"&VLOOKUP(E257,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B258&VLOOKUP(A258,List!$B$3:$D$445,2,FALSE)&D258&\"_\"&VLOOKUP(E258,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B259&VLOOKUP(A259,List!$B$3:$D$445,2,FALSE)&D259&\"_\"&VLOOKUP(E259,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B260&VLOOKUP(A260,List!$B$3:$D$445,2,FALSE)&D260&\"_\"&VLOOKUP(E260,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B261&VLOOKUP(A261,List!$B$3:$D$445,2,FALSE)&D261&\"_\"&VLOOKUP(E261,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B262&VLOOKUP(A262,List!$B$3:$D$445,2,FALSE)&D262&\"_\"&VLOOKUP(E262,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B263&VLOOKUP(A263,List!$B$3:$D$445,2,FALSE)&D263&\"_\"&VLOOKUP(E263,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B264&VLOOKUP(A264,List!$B$3:$D$445,2,FALSE)&D264&\"_\"&VLOOKUP(E264,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B265&VLOOKUP(A265,List!$B$3:$D$445,2,FALSE)&D265&\"_\"&VLOOKUP(E265,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B266&VLOOKUP(A266,List!$B$3:$D$445,2,FALSE)&D266&\"_\"&VLOOKUP(E266,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B267&VLOOKUP(A267,List!$B$3:$D$445,2,FALSE)&D267&\"_\"&VLOOKUP(E267,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B268&VLOOKUP(A268,List!$B$3:$D$445,2,FALSE)&D268&\"_\"&VLOOKUP(E268,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B269&VLOOKUP(A269,List!$B$3:$D$445,2,FALSE)&D269&\"_\"&VLOOKUP(E269,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B270&VLOOKUP(A270,List!$B$3:$D$445,2,FALSE)&D270&\"_\"&VLOOKUP(E270,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B271&VLOOKUP(A271,List!$B$3:$D$445,2,FALSE)&D271&\"_\"&VLOOKUP(E271,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B272&VLOOKUP(A272,List!$B$3:$D$445,2,FALSE)&D272&\"_\"&VLOOKUP(E272,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B273&VLOOKUP(A273,List!$B$3:$D$445,2,FALSE)&D273&\"_\"&VLOOKUP(E273,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B274&VLOOKUP(A274,List!$B$3:$D$445,2,FALSE)&D274&\"_\"&VLOOKUP(E274,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B275&VLOOKUP(A275,List!$B$3:$D$445,2,FALSE)&D275&\"_\"&VLOOKUP(E275,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B276&VLOOKUP(A276,List!$B$3:$D$445,2,FALSE)&D276&\"_\"&VLOOKUP(E276,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B277&VLOOKUP(A277,List!$B$3:$D$445,2,FALSE)&D277&\"_\"&VLOOKUP(E277,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B278&VLOOKUP(A278,List!$B$3:$D$445,2,FALSE)&D278&\"_\"&VLOOKUP(E278,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B279&VLOOKUP(A279,List!$B$3:$D$445,2,FALSE)&D279&\"_\"&VLOOKUP(E279,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B280&VLOOKUP(A280,List!$B$3:$D$445,2,FALSE)&D280&\"_\"&VLOOKUP(E280,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B281&VLOOKUP(A281,List!$B$3:$D$445,2,FALSE)&D281&\"_\"&VLOOKUP(E281,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B282&VLOOKUP(A282,List!$B$3:$D$445,2,FALSE)&D282&\"_\"&VLOOKUP(E282,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B283&VLOOKUP(A283,List!$B$3:$D$445,2,FALSE)&D283&\"_\"&VLOOKUP(E283,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B284&VLOOKUP(A284,List!$B$3:$D$445,2,FALSE)&D284&\"_\"&VLOOKUP(E284,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B285&VLOOKUP(A285,List!$B$3:$D$445,2,FALSE)&D285&\"_\"&VLOOKUP(E285,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B286&VLOOKUP(A286,List!$B$3:$D$445,2,FALSE)&D286&\"_\"&VLOOKUP(E286,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B287&VLOOKUP(A287,List!$B$3:$D$445,2,FALSE)&D287&\"_\"&VLOOKUP(E287,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B288&VLOOKUP(A288,List!$B$3:$D$445,2,FALSE)&D288&\"_\"&VLOOKUP(E288,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B289&VLOOKUP(A289,List!$B$3:$D$445,2,FALSE)&D289&\"_\"&VLOOKUP(E289,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B290&VLOOKUP(A290,List!$B$3:$D$445,2,FALSE)&D290&\"_\"&VLOOKUP(E290,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B291&VLOOKUP(A291,List!$B$3:$D$445,2,FALSE)&D291&\"_\"&VLOOKUP(E291,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B292&VLOOKUP(A292,List!$B$3:$D$445,2,FALSE)&D292&\"_\"&VLOOKUP(E292,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B293&VLOOKUP(A293,List!$B$3:$D$445,2,FALSE)&D293&\"_\"&VLOOKUP(E293,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B294&VLOOKUP(A294,List!$B$3:$D$445,2,FALSE)&D294&\"_\"&VLOOKUP(E294,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B295&VLOOKUP(A295,List!$B$3:$D$445,2,FALSE)&D295&\"_\"&VLOOKUP(E295,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B296&VLOOKUP(A296,List!$B$3:$D$445,2,FALSE)&D296&\"_\"&VLOOKUP(E296,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B297&VLOOKUP(A297,List!$B$3:$D$445,2,FALSE)&D297&\"_\"&VLOOKUP(E297,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B298&VLOOKUP(A298,List!$B$3:$D$445,2,FALSE)&D298&\"_\"&VLOOKUP(E298,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$f":"REPLACE(REPLACE(L298,SEARCH(\"AT%\",L298),,REPT(\" \",25-SEARCH(\"AT%\",L298))),SEARCH(\":\",REPLACE(L298,SEARCH(\"AT%\",L298),,REPT(\" \",25-SEARCH(\"AT%\",L298)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L298,SEARCH(\"AT%\",L298),,REPT(\" \",25-SEARCH(\"AT%\",L298))))))","v":{"$error":"#N/A"}}]
[{"$nulls":10},{"$f":"B299&VLOOKUP(A299,List!$B$3:$D$445,2,FALSE)&D299&\"_\"&VLOOKUP(E299,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B300&VLOOKUP(A300,List!$B$3:$D$445,2,FALSE)&D300&\"_\"&VLOOKUP(E300,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B301&VLOOKUP(A301,List!$B$3:$D$445,2,FALSE)&D301&\"_\"&VLOOKUP(E301,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B302&VLOOKUP(A302,List!$B$3:$D$445,2,FALSE)&D302&\"_\"&VLOOKUP(E302,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B303&VLOOKUP(A303,List!$B$3:$D$445,2,FALSE)&D303&\"_\"&VLOOKUP(E303,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B304&VLOOKUP(A304,List!$B$3:$D$445,2,FALSE)&D304&\"_\"&VLOOKUP(E304,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B305&VLOOKUP(A305,List!$B$3:$D$445,2,FALSE)&D305&\"_\"&VLOOKUP(E305,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B306&VLOOKUP(A306,List!$B$3:$D$445,2,FALSE)&D306&\"_\"&VLOOKUP(E306,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B307&VLOOKUP(A307,List!$B$3:$D$445,2,FALSE)&D307&\"_\"&VLOOKUP(E307,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B308&VLOOKUP(A308,List!$B$3:$D$445,2,FALSE)&D308&\"_\"&VLOOKUP(E308,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B309&VLOOKUP(A309,List!$B$3:$D$445,2,FALSE)&D309&\"_\"&VLOOKUP(E309,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B310&VLOOKUP(A310,List!$B$3:$D$445,2,FALSE)&D310&\"_\"&VLOOKUP(E310,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B311&VLOOKUP(A311,List!$B$3:$D$445,2,FALSE)&D311&\"_\"&VLOOKUP(E311,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B312&VLOOKUP(A312,List!$B$3:$D$445,2,FALSE)&D312&\"_\"&VLOOKUP(E312,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B313&VLOOKUP(A313,List!$B$3:$D$445,2,FALSE)&D313&\"_\"&VLOOKUP(E313,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B314&VLOOKUP(A314,List!$B$3:$D$445,2,FALSE)&D314&\"_\"&VLOOKUP(E314,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B315&VLOOKUP(A315,List!$B$3:$D$445,2,FALSE)&D315&\"_\"&VLOOKUP(E315,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B316&VLOOKUP(A316,List!$B$3:$D$445,2,FALSE)&D316&\"_\"&VLOOKUP(E316,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B317&VLOOKUP(A317,List!$B$3:$D$445,2,FALSE)&D317&\"_\"&VLOOKUP(E317,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B318&VLOOKUP(A318,List!$B$3:$D$445,2,FALSE)&D318&\"_\"&VLOOKUP(E318,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B319&VLOOKUP(A319,List!$B$3:$D$445,2,FALSE)&D319&\"_\"&VLOOKUP(E319,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B320&VLOOKUP(A320,List!$B$3:$D$445,2,FALSE)&D320&\"_\"&VLOOKUP(E320,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"K320&\" \"&\"AT%\"&C320&F320&\" \"&\":\"&I320&\";\"&\" \"&\"(*\"&J320&\"*)\"","v":{"$error":"#N/A"}},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B321&VLOOKUP(A321,List!$B$3:$D$445,2,FALSE)&D321&\"_\"&VLOOKUP(E321,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B322&VLOOKUP(A322,List!$B$3:$D$445,2,FALSE)&D322&\"_\"&VLOOKUP(E322,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B323&VLOOKUP(A323,List!$B$3:$D$445,2,FALSE)&D323&\"_\"&VLOOKUP(E323,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B324&VLOOKUP(A324,List!$B$3:$D$445,2,FALSE)&D324&\"_\"&VLOOKUP(E324,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B325&VLOOKUP(A325,List!$B$3:$D$445,2,FALSE)&D325&\"_\"&VLOOKUP(E325,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B326&VLOOKUP(A326,List!$B$3:$D$445,2,FALSE)&D326&\"_\"&VLOOKUP(E326,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B327&VLOOKUP(A327,List!$B$3:$D$445,2,FALSE)&D327&\"_\"&VLOOKUP(E327,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B328&VLOOKUP(A328,List!$B$3:$D$445,2,FALSE)&D328&\"_\"&VLOOKUP(E328,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B329&VLOOKUP(A329,List!$B$3:$D$445,2,FALSE)&D329&\"_\"&VLOOKUP(E329,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B330&VLOOKUP(A330,List!$B$3:$D$445,2,FALSE)&D330&\"_\"&VLOOKUP(E330,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B331&VLOOKUP(A331,List!$B$3:$D$445,2,FALSE)&D331&\"_\"&VLOOKUP(E331,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B332&VLOOKUP(A332,List!$B$3:$D$445,2,FALSE)&D332&\"_\"&VLOOKUP(E332,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B333&VLOOKUP(A333,List!$B$3:$D$445,2,FALSE)&D333&\"_\"&VLOOKUP(E333,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B334&VLOOKUP(A334,List!$B$3:$D$445,2,FALSE)&D334&\"_\"&VLOOKUP(E334,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B335&VLOOKUP(A335,List!$B$3:$D$445,2,FALSE)&D335&\"_\"&VLOOKUP(E335,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B336&VLOOKUP(A336,List!$B$3:$D$445,2,FALSE)&D336&\"_\"&VLOOKUP(E336,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B337&VLOOKUP(A337,List!$B$3:$D$445,2,FALSE)&D337&\"_\"&VLOOKUP(E337,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B338&VLOOKUP(A338,List!$B$3:$D$445,2,FALSE)&D338&\"_\"&VLOOKUP(E338,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B339&VLOOKUP(A339,List!$B$3:$D$445,2,FALSE)&D339&\"_\"&VLOOKUP(E339,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B340&VLOOKUP(A340,List!$B$3:$D$445,2,FALSE)&D340&\"_\"&VLOOKUP(E340,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B341&VLOOKUP(A341,List!$B$3:$D$445,2,FALSE)&D341&\"_\"&VLOOKUP(E341,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B342&VLOOKUP(A342,List!$B$3:$D$445,2,FALSE)&D342&\"_\"&VLOOKUP(E342,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B343&VLOOKUP(A343,List!$B$3:$D$445,2,FALSE)&D343&\"_\"&VLOOKUP(E343,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B344&VLOOKUP(A344,List!$B$3:$D$445,2,FALSE)&D344&\"_\"&VLOOKUP(E344,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B345&VLOOKUP(A345,List!$B$3:$D$445,2,FALSE)&D345&\"_\"&VLOOKUP(E345,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B346&VLOOKUP(A346,List!$B$3:$D$445,2,FALSE)&D346&\"_\"&VLOOKUP(E346,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B347&VLOOKUP(A347,List!$B$3:$D$445,2,FALSE)&D347&\"_\"&VLOOKUP(E347,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B348&VLOOKUP(A348,List!$B$3:$D$445,2,FALSE)&D348&\"_\"&VLOOKUP(E348,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B349&VLOOKUP(A349,List!$B$3:$D$445,2,FALSE)&D349&\"_\"&VLOOKUP(E349,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B350&VLOOKUP(A350,List!$B$3:$D$445,2,FALSE)&D350&\"_\"&VLOOKUP(E350,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B351&VLOOKUP(A351,List!$B$3:$D$445,2,FALSE)&D351&\"_\"&VLOOKUP(E351,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B352&VLOOKUP(A352,List!$B$3:$D$445,2,FALSE)&D352&\"_\"&VLOOKUP(E352,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B353&VLOOKUP(A353,List!$B$3:$D$445,2,FALSE)&D353&\"_\"&VLOOKUP(E353,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B354&VLOOKUP(A354,List!$B$3:$D$445,2,FALSE)&D354&\"_\"&VLOOKUP(E354,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B355&VLOOKUP(A355,List!$B$3:$D$445,2,FALSE)&D355&\"_\"&VLOOKUP(E355,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B356&VLOOKUP(A356,List!$B$3:$D$445,2,FALSE)&D356&\"_\"&VLOOKUP(E356,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B357&VLOOKUP(A357,List!$B$3:$D$445,2,FALSE)&D357&\"_\"&VLOOKUP(E357,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B358&VLOOKUP(A358,List!$B$3:$D$445,2,FALSE)&D358&\"_\"&VLOOKUP(E358,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B359&VLOOKUP(A359,List!$B$3:$D$445,2,FALSE)&D359&\"_\"&VLOOKUP(E359,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B360&VLOOKUP(A360,List!$B$3:$D$445,2,FALSE)&D360&\"_\"&VLOOKUP(E360,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B361&VLOOKUP(A361,List!$B$3:$D$445,2,FALSE)&D361&\"_\"&VLOOKUP(E361,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B362&VLOOKUP(A362,List!$B$3:$D$445,2,FALSE)&D362&\"_\"&VLOOKUP(E362,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$f":"REPLACE(REPLACE(L362,SEARCH(\"AT%\",L362),,REPT(\" \",25-SEARCH(\"AT%\",L362))),SEARCH(\":\",REPLACE(L362,SEARCH(\"AT%\",L362),,REPT(\" \",25-SEARCH(\"AT%\",L362)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L362,SEARCH(\"AT%\",L362),,REPT(\" \",25-SEARCH(\"AT%\",L362))))))","v":{"$error":"#N/A"}}]
[{"$nulls":10},{"$f":"B363&VLOOKUP(A363,List!$B$3:$D$445,2,FALSE)&D363&\"_\"&VLOOKUP(E363,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B364&VLOOKUP(A364,List!$B$3:$D$445,2,FALSE)&D364&\"_\"&VLOOKUP(E364,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B365&VLOOKUP(A365,List!$B$3:$D$445,2,FALSE)&D365&\"_\"&VLOOKUP(E365,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B366&VLOOKUP(A366,List!$B$3:$D$445,2,FALSE)&D366&\"_\"&VLOOKUP(E366,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B367&VLOOKUP(A367,List!$B$3:$D$445,2,FALSE)&D367&\"_\"&VLOOKUP(E367,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B368&VLOOKUP(A368,List!$B$3:$D$445,2,FALSE)&D368&\"_\"&VLOOKUP(E368,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B369&VLOOKUP(A369,List!$B$3:$D$445,2,FALSE)&D369&\"_\"&VLOOKUP(E369,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B370&VLOOKUP(A370,List!$B$3:$D$445,2,FALSE)&D370&\"_\"&VLOOKUP(E370,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B371&VLOOKUP(A371,List!$B$3:$D$445,2,FALSE)&D371&\"_\"&VLOOKUP(E371,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B372&VLOOKUP(A372,List!$B$3:$D$445,2,FALSE)&D372&\"_\"&VLOOKUP(E372,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B373&VLOOKUP(A373,List!$B$3:$D$445,2,FALSE)&D373&\"_\"&VLOOKUP(E373,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B374&VLOOKUP(A374,List!$B$3:$D$445,2,FALSE)&D374&\"_\"&VLOOKUP(E374,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B375&VLOOKUP(A375,List!$B$3:$D$445,2,FALSE)&D375&\"_\"&VLOOKUP(E375,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B376&VLOOKUP(A376,List!$B$3:$D$445,2,FALSE)&D376&\"_\"&VLOOKUP(E376,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B377&VLOOKUP(A377,List!$B$3:$D$445,2,FALSE)&D377&\"_\"&VLOOKUP(E377,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B378&VLOOKUP(A378,List!$B$3:$D$445,2,FALSE)&D378&\"_\"&VLOOKUP(E378,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B379&VLOOKUP(A379,List!$B$3:$D$445,2,FALSE)&D379&\"_\"&VLOOKUP(E379,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B380&VLOOKUP(A380,List!$B$3:$D$445,2,FALSE)&D380&\"_\"&VLOOKUP(E380,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B381&VLOOKUP(A381,List!$B$3:$D$445,2,FALSE)&D381&\"_\"&VLOOKUP(E381,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B382&VLOOKUP(A382,List!$B$3:$D$445,2,FALSE)&D382&\"_\"&VLOOKUP(E382,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B383&VLOOKUP(A383,List!$B$3:$D$445,2,FALSE)&D383&\"_\"&VLOOKUP(E383,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B384&VLOOKUP(A384,List!$B$3:$D$445,2,FALSE)&D384&\"_\"&VLOOKUP(E384,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"K384&\" \"&\"AT%\"&C384&F384&\" \"&\":\"&I384&\";\"&\" \"&\"(*\"&J384&\"*)\"","v":{"$error":"#N/A"}},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B385&VLOOKUP(A385,List!$B$3:$D$445,2,FALSE)&D385&\"_\"&VLOOKUP(E385,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B386&VLOOKUP(A386,List!$B$3:$D$445,2,FALSE)&D386&\"_\"&VLOOKUP(E386,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B387&VLOOKUP(A387,List!$B$3:$D$445,2,FALSE)&D387&\"_\"&VLOOKUP(E387,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B388&VLOOKUP(A388,List!$B$3:$D$445,2,FALSE)&D388&\"_\"&VLOOKUP(E388,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B389&VLOOKUP(A389,List!$B$3:$D$445,2,FALSE)&D389&\"_\"&VLOOKUP(E389,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B390&VLOOKUP(A390,List!$B$3:$D$445,2,FALSE)&D390&\"_\"&VLOOKUP(E390,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B391&VLOOKUP(A391,List!$B$3:$D$445,2,FALSE)&D391&\"_\"&VLOOKUP(E391,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B392&VLOOKUP(A392,List!$B$3:$D$445,2,FALSE)&D392&\"_\"&VLOOKUP(E392,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B393&VLOOKUP(A393,List!$B$3:$D$445,2,FALSE)&D393&\"_\"&VLOOKUP(E393,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B394&VLOOKUP(A394,List!$B$3:$D$445,2,FALSE)&D394&\"_\"&VLOOKUP(E394,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B395&VLOOKUP(A395,List!$B$3:$D$445,2,FALSE)&D395&\"_\"&VLOOKUP(E395,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B396&VLOOKUP(A396,List!$B$3:$D$445,2,FALSE)&D396&\"_\"&VLOOKUP(E396,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B397&VLOOKUP(A397,List!$B$3:$D$445,2,FALSE)&D397&\"_\"&VLOOKUP(E397,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B398&VLOOKUP(A398,List!$B$3:$D$445,2,FALSE)&D398&\"_\"&VLOOKUP(E398,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B399&VLOOKUP(A399,List!$B$3:$D$445,2,FALSE)&D399&\"_\"&VLOOKUP(E399,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B400&VLOOKUP(A400,List!$B$3:$D$445,2,FALSE)&D400&\"_\"&VLOOKUP(E400,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B401&VLOOKUP(A401,List!$B$3:$D$445,2,FALSE)&D401&\"_\"&VLOOKUP(E401,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B402&VLOOKUP(A402,List!$B$3:$D$445,2,FALSE)&D402&\"_\"&VLOOKUP(E402,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B403&VLOOKUP(A403,List!$B$3:$D$445,2,FALSE)&D403&\"_\"&VLOOKUP(E403,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B404&VLOOKUP(A404,List!$B$3:$D$445,2,FALSE)&D404&\"_\"&VLOOKUP(E404,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B405&VLOOKUP(A405,List!$B$3:$D$445,2,FALSE)&D405&\"_\"&VLOOKUP(E405,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B406&VLOOKUP(A406,List!$B$3:$D$445,2,FALSE)&D406&\"_\"&VLOOKUP(E406,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B407&VLOOKUP(A407,List!$B$3:$D$445,2,FALSE)&D407&\"_\"&VLOOKUP(E407,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B408&VLOOKUP(A408,List!$B$3:$D$445,2,FALSE)&D408&\"_\"&VLOOKUP(E408,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B409&VLOOKUP(A409,List!$B$3:$D$445,2,FALSE)&D409&\"_\"&VLOOKUP(E409,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B410&VLOOKUP(A410,List!$B$3:$D$445,2,FALSE)&D410&\"_\"&VLOOKUP(E410,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B411&VLOOKUP(A411,List!$B$3:$D$445,2,FALSE)&D411&\"_\"&VLOOKUP(E411,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B412&VLOOKUP(A412,List!$B$3:$D$445,2,FALSE)&D412&\"_\"&VLOOKUP(E412,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B413&VLOOKUP(A413,List!$B$3:$D$445,2,FALSE)&D413&\"_\"&VLOOKUP(E413,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B414&VLOOKUP(A414,List!$B$3:$D$445,2,FALSE)&D414&\"_\"&VLOOKUP(E414,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B415&VLOOKUP(A415,List!$B$3:$D$445,2,FALSE)&D415&\"_\"&VLOOKUP(E415,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B416&VLOOKUP(A416,List!$B$3:$D$445,2,FALSE)&D416&\"_\"&VLOOKUP(E416,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B417&VLOOKUP(A417,List!$B$3:$D$445,2,FALSE)&D417&\"_\"&VLOOKUP(E417,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B418&VLOOKUP(A418,List!$B$3:$D$445,2,FALSE)&D418&\"_\"&VLOOKUP(E418,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B419&VLOOKUP(A419,List!$B$3:$D$445,2,FALSE)&D419&\"_\"&VLOOKUP(E419,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B420&VLOOKUP(A420,List!$B$3:$D$445,2,FALSE)&D420&\"_\"&VLOOKUP(E420,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B421&VLOOKUP(A421,List!$B$3:$D$445,2,FALSE)&D421&\"_\"&VLOOKUP(E421,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B422&VLOOKUP(A422,List!$B$3:$D$445,2,FALSE)&D422&\"_\"&VLOOKUP(E422,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B423&VLOOKUP(A423,List!$B$3:$D$445,2,FALSE)&D423&\"_\"&VLOOKUP(E423,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B424&VLOOKUP(A424,List!$B$3:$D$445,2,FALSE)&D424&\"_\"&VLOOKUP(E424,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B425&VLOOKUP(A425,List!$B$3:$D$445,2,FALSE)&D425&\"_\"&VLOOKUP(E425,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B426&VLOOKUP(A426,List!$B$3:$D$445,2,FALSE)&D426&\"_\"&VLOOKUP(E426,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$f":"REPLACE(REPLACE(L426,SEARCH(\"AT%\",L426),,REPT(\" \",25-SEARCH(\"AT%\",L426))),SEARCH(\":\",REPLACE(L426,SEARCH(\"AT%\",L426),,REPT(\" \",25-SEARCH(\"AT%\",L426)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L426,SEARCH(\"AT%\",L426),,REPT(\" \",25-SEARCH(\"AT%\",L426))))))","v":{"$error":"#N/A"}}]
[{"$nulls":10},{"$f":"B427&VLOOKUP(A427,List!$B$3:$D$445,2,FALSE)&D427&\"_\"&VLOOKUP(E427,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B428&VLOOKUP(A428,List!$B$3:$D$445,2,FALSE)&D428&\"_\"&VLOOKUP(E428,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B429&VLOOKUP(A429,List!$B$3:$D$445,2,FALSE)&D429&\"_\"&VLOOKUP(E429,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B430&VLOOKUP(A430,List!$B$3:$D$445,2,FALSE)&D430&\"_\"&VLOOKUP(E430,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B431&VLOOKUP(A431,List!$B$3:$D$445,2,FALSE)&D431&\"_\"&VLOOKUP(E431,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B432&VLOOKUP(A432,List!$B$3:$D$445,2,FALSE)&D432&\"_\"&VLOOKUP(E432,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B433&VLOOKUP(A433,List!$B$3:$D$445,2,FALSE)&D433&\"_\"&VLOOKUP(E433,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B434&VLOOKUP(A434,List!$B$3:$D$445,2,FALSE)&D434&\"_\"&VLOOKUP(E434,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B435&VLOOKUP(A435,List!$B$3:$D$445,2,FALSE)&D435&\"_\"&VLOOKUP(E435,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B436&VLOOKUP(A436,List!$B$3:$D$445,2,FALSE)&D436&\"_\"&VLOOKUP(E436,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B437&VLOOKUP(A437,List!$B$3:$D$445,2,FALSE)&D437&\"_\"&VLOOKUP(E437,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B438&VLOOKUP(A438,List!$B$3:$D$445,2,FALSE)&D438&\"_\"&VLOOKUP(E438,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B439&VLOOKUP(A439,List!$B$3:$D$445,2,FALSE)&D439&\"_\"&VLOOKUP(E439,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B440&VLOOKUP(A440,List!$B$3:$D$445,2,FALSE)&D440&\"_\"&VLOOKUP(E440,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B441&VLOOKUP(A441,List!$B$3:$D$445,2,FALSE)&D441&\"_\"&VLOOKUP(E441,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B442&VLOOKUP(A442,List!$B$3:$D$445,2,FALSE)&D442&\"_\"&VLOOKUP(E442,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B443&VLOOKUP(A443,List!$B$3:$D$445,2,FALSE)&D443&\"_\"&VLOOKUP(E443,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B444&VLOOKUP(A444,List!$B$3:$D$445,2,FALSE)&D444&\"_\"&VLOOKUP(E444,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B445&VLOOKUP(A445,List!$B$3:$D$445,2,FALSE)&D445&\"_\"&VLOOKUP(E445,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B446&VLOOKUP(A446,List!$B$3:$D$445,2,FALSE)&D446&\"_\"&VLOOKUP(E446,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B447&VLOOKUP(A447,List!$B$3:$D$445,2,FALSE)&D447&\"_\"&VLOOKUP(E447,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B448&VLOOKUP(A448,List!$B$3:$D$445,2,FALSE)&D448&\"_\"&VLOOKUP(E448,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"K448&\" \"&\"AT%\"&C448&F448&\" \"&\":\"&I448&\";\"&\" \"&\"(*\"&J448&\"*)\"","v":{"$error":"#N/A"}},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B449&VLOOKUP(A449,List!$B$3:$D$445,2,FALSE)&D449&\"_\"&VLOOKUP(E449,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B450&VLOOKUP(A450,List!$B$3:$D$445,2,FALSE)&D450&\"_\"&VLOOKUP(E450,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B451&VLOOKUP(A451,List!$B$3:$D$445,2,FALSE)&D451&\"_\"&VLOOKUP(E451,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B452&VLOOKUP(A452,List!$B$3:$D$445,2,FALSE)&D452&\"_\"&VLOOKUP(E452,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B453&VLOOKUP(A453,List!$B$3:$D$445,2,FALSE)&D453&\"_\"&VLOOKUP(E453,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B454&VLOOKUP(A454,List!$B$3:$D$445,2,FALSE)&D454&\"_\"&VLOOKUP(E454,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B455&VLOOKUP(A455,List!$B$3:$D$445,2,FALSE)&D455&\"_\"&VLOOKUP(E455,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B456&VLOOKUP(A456,List!$B$3:$D$445,2,FALSE)&D456&\"_\"&VLOOKUP(E456,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B457&VLOOKUP(A457,List!$B$3:$D$445,2,FALSE)&D457&\"_\"&VLOOKUP(E457,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B458&VLOOKUP(A458,List!$B$3:$D$445,2,FALSE)&D458&\"_\"&VLOOKUP(E458,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B459&VLOOKUP(A459,List!$B$3:$D$445,2,FALSE)&D459&\"_\"&VLOOKUP(E459,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B460&VLOOKUP(A460,List!$B$3:$D$445,2,FALSE)&D460&\"_\"&VLOOKUP(E460,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B461&VLOOKUP(A461,List!$B$3:$D$445,2,FALSE)&D461&\"_\"&VLOOKUP(E461,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B462&VLOOKUP(A462,List!$B$3:$D$445,2,FALSE)&D462&\"_\"&VLOOKUP(E462,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B463&VLOOKUP(A463,List!$B$3:$D$445,2,FALSE)&D463&\"_\"&VLOOKUP(E463,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B464&VLOOKUP(A464,List!$B$3:$D$445,2,FALSE)&D464&\"_\"&VLOOKUP(E464,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B465&VLOOKUP(A465,List!$B$3:$D$445,2,FALSE)&D465&\"_\"&VLOOKUP(E465,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B466&VLOOKUP(A466,List!$B$3:$D$445,2,FALSE)&D466&\"_\"&VLOOKUP(E466,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B467&VLOOKUP(A467,List!$B$3:$D$445,2,FALSE)&D467&\"_\"&VLOOKUP(E467,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B468&VLOOKUP(A468,List!$B$3:$D$445,2,FALSE)&D468&\"_\"&VLOOKUP(E468,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B469&VLOOKUP(A469,List!$B$3:$D$445,2,FALSE)&D469&\"_\"&VLOOKUP(E469,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B470&VLOOKUP(A470,List!$B$3:$D$445,2,FALSE)&D470&\"_\"&VLOOKUP(E470,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B471&VLOOKUP(A471,List!$B$3:$D$445,2,FALSE)&D471&\"_\"&VLOOKUP(E471,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B472&VLOOKUP(A472,List!$B$3:$D$445,2,FALSE)&D472&\"_\"&VLOOKUP(E472,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B473&VLOOKUP(A473,List!$B$3:$D$445,2,FALSE)&D473&\"_\"&VLOOKUP(E473,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B474&VLOOKUP(A474,List!$B$3:$D$445,2,FALSE)&D474&\"_\"&VLOOKUP(E474,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B475&VLOOKUP(A475,List!$B$3:$D$445,2,FALSE)&D475&\"_\"&VLOOKUP(E475,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B476&VLOOKUP(A476,List!$B$3:$D$445,2,FALSE)&D476&\"_\"&VLOOKUP(E476,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B477&VLOOKUP(A477,List!$B$3:$D$445,2,FALSE)&D477&\"_\"&VLOOKUP(E477,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B478&VLOOKUP(A478,List!$B$3:$D$445,2,FALSE)&D478&\"_\"&VLOOKUP(E478,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B479&VLOOKUP(A479,List!$B$3:$D$445,2,FALSE)&D479&\"_\"&VLOOKUP(E479,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B480&VLOOKUP(A480,List!$B$3:$D$445,2,FALSE)&D480&\"_\"&VLOOKUP(E480,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B481&VLOOKUP(A481,List!$B$3:$D$445,2,FALSE)&D481&\"_\"&VLOOKUP(E481,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B482&VLOOKUP(A482,List!$B$3:$D$445,2,FALSE)&D482&\"_\"&VLOOKUP(E482,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B483&VLOOKUP(A483,List!$B$3:$D$445,2,FALSE)&D483&\"_\"&VLOOKUP(E483,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B484&VLOOKUP(A484,List!$B$3:$D$445,2,FALSE)&D484&\"_\"&VLOOKUP(E484,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B485&VLOOKUP(A485,List!$B$3:$D$445,2,FALSE)&D485&\"_\"&VLOOKUP(E485,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B486&VLOOKUP(A486,List!$B$3:$D$445,2,FALSE)&D486&\"_\"&VLOOKUP(E486,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B487&VLOOKUP(A487,List!$B$3:$D$445,2,FALSE)&D487&\"_\"&VLOOKUP(E487,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B488&VLOOKUP(A488,List!$B$3:$D$445,2,FALSE)&D488&\"_\"&VLOOKUP(E488,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B489&VLOOKUP(A489,List!$B$3:$D$445,2,FALSE)&D489&\"_\"&VLOOKUP(E489,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B490&VLOOKUP(A490,List!$B$3:$D$445,2,FALSE)&D490&\"_\"&VLOOKUP(E490,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$f":"REPLACE(REPLACE(L490,SEARCH(\"AT%\",L490),,REPT(\" \",25-SEARCH(\"AT%\",L490))),SEARCH(\":\",REPLACE(L490,SEARCH(\"AT%\",L490),,REPT(\" \",25-SEARCH(\"AT%\",L490)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L490,SEARCH(\"AT%\",L490),,REPT(\" \",25-SEARCH(\"AT%\",L490))))))","v":{"$error":"#N/A"}}]
[{"$nulls":10},{"$f":"B491&VLOOKUP(A491,List!$B$3:$D$445,2,FALSE)&D491&\"_\"&VLOOKUP(E491,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B492&VLOOKUP(A492,List!$B$3:$D$445,2,FALSE)&D492&\"_\"&VLOOKUP(E492,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B493&VLOOKUP(A493,List!$B$3:$D$445,2,FALSE)&D493&\"_\"&VLOOKUP(E493,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B494&VLOOKUP(A494,List!$B$3:$D$445,2,FALSE)&D494&\"_\"&VLOOKUP(E494,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B495&VLOOKUP(A495,List!$B$3:$D$445,2,FALSE)&D495&\"_\"&VLOOKUP(E495,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B496&VLOOKUP(A496,List!$B$3:$D$445,2,FALSE)&D496&\"_\"&VLOOKUP(E496,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B497&VLOOKUP(A497,List!$B$3:$D$445,2,FALSE)&D497&\"_\"&VLOOKUP(E497,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B498&VLOOKUP(A498,List!$B$3:$D$445,2,FALSE)&D498&\"_\"&VLOOKUP(E498,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B499&VLOOKUP(A499,List!$B$3:$D$445,2,FALSE)&D499&\"_\"&VLOOKUP(E499,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B500&VLOOKUP(A500,List!$B$3:$D$445,2,FALSE)&D500&\"_\"&VLOOKUP(E500,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B501&VLOOKUP(A501,List!$B$3:$D$445,2,FALSE)&D501&\"_\"&VLOOKUP(E501,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B502&VLOOKUP(A502,List!$B$3:$D$445,2,FALSE)&D502&\"_\"&VLOOKUP(E502,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B503&VLOOKUP(A503,List!$B$3:$D$445,2,FALSE)&D503&\"_\"&VLOOKUP(E503,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B504&VLOOKUP(A504,List!$B$3:$D$445,2,FALSE)&D504&\"_\"&VLOOKUP(E504,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B505&VLOOKUP(A505,List!$B$3:$D$445,2,FALSE)&D505&\"_\"&VLOOKUP(E505,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B506&VLOOKUP(A506,List!$B$3:$D$445,2,FALSE)&D506&\"_\"&VLOOKUP(E506,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B507&VLOOKUP(A507,List!$B$3:$D$445,2,FALSE)&D507&\"_\"&VLOOKUP(E507,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B508&VLOOKUP(A508,List!$B$3:$D$445,2,FALSE)&D508&\"_\"&VLOOKUP(E508,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B509&VLOOKUP(A509,List!$B$3:$D$445,2,FALSE)&D509&\"_\"&VLOOKUP(E509,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B510&VLOOKUP(A510,List!$B$3:$D$445,2,FALSE)&D510&\"_\"&VLOOKUP(E510,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B511&VLOOKUP(A511,List!$B$3:$D$445,2,FALSE)&D511&\"_\"&VLOOKUP(E511,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B512&VLOOKUP(A512,List!$B$3:$D$445,2,FALSE)&D512&\"_\"&VLOOKUP(E512,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"K512&\" \"&\"AT%\"&C512&F512&\" \"&\":\"&I512&\";\"&\" \"&\"(*\"&J512&\"*)\"","v":{"$error":"#N/A"}},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B513&VLOOKUP(A513,List!$B$3:$D$445,2,FALSE)&D513&\"_\"&VLOOKUP(E513,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B514&VLOOKUP(A514,List!$B$3:$D$445,2,FALSE)&D514&\"_\"&VLOOKUP(E514,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B515&VLOOKUP(A515,List!$B$3:$D$445,2,FALSE)&D515&\"_\"&VLOOKUP(E515,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B516&VLOOKUP(A516,List!$B$3:$D$445,2,FALSE)&D516&\"_\"&VLOOKUP(E516,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B517&VLOOKUP(A517,List!$B$3:$D$445,2,FALSE)&D517&\"_\"&VLOOKUP(E517,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B518&VLOOKUP(A518,List!$B$3:$D$445,2,FALSE)&D518&\"_\"&VLOOKUP(E518,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B519&VLOOKUP(A519,List!$B$3:$D$445,2,FALSE)&D519&\"_\"&VLOOKUP(E519,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B520&VLOOKUP(A520,List!$B$3:$D$445,2,FALSE)&D520&\"_\"&VLOOKUP(E520,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B521&VLOOKUP(A521,List!$B$3:$D$445,2,FALSE)&D521&\"_\"&VLOOKUP(E521,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B522&VLOOKUP(A522,List!$B$3:$D$445,2,FALSE)&D522&\"_\"&VLOOKUP(E522,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B523&VLOOKUP(A523,List!$B$3:$D$445,2,FALSE)&D523&\"_\"&VLOOKUP(E523,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B524&VLOOKUP(A524,List!$B$3:$D$445,2,FALSE)&D524&\"_\"&VLOOKUP(E524,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B525&VLOOKUP(A525,List!$B$3:$D$445,2,FALSE)&D525&\"_\"&VLOOKUP(E525,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B526&VLOOKUP(A526,List!$B$3:$D$445,2,FALSE)&D526&\"_\"&VLOOKUP(E526,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B527&VLOOKUP(A527,List!$B$3:$D$445,2,FALSE)&D527&\"_\"&VLOOKUP(E527,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B528&VLOOKUP(A528,List!$B$3:$D$445,2,FALSE)&D528&\"_\"&VLOOKUP(E528,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B529&VLOOKUP(A529,List!$B$3:$D$445,2,FALSE)&D529&\"_\"&VLOOKUP(E529,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B530&VLOOKUP(A530,List!$B$3:$D$445,2,FALSE)&D530&\"_\"&VLOOKUP(E530,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B531&VLOOKUP(A531,List!$B$3:$D$445,2,FALSE)&D531&\"_\"&VLOOKUP(E531,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B532&VLOOKUP(A532,List!$B$3:$D$445,2,FALSE)&D532&\"_\"&VLOOKUP(E532,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B533&VLOOKUP(A533,List!$B$3:$D$445,2,FALSE)&D533&\"_\"&VLOOKUP(E533,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B534&VLOOKUP(A534,List!$B$3:$D$445,2,FALSE)&D534&\"_\"&VLOOKUP(E534,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B535&VLOOKUP(A535,List!$B$3:$D$445,2,FALSE)&D535&\"_\"&VLOOKUP(E535,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B536&VLOOKUP(A536,List!$B$3:$D$445,2,FALSE)&D536&\"_\"&VLOOKUP(E536,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B537&VLOOKUP(A537,List!$B$3:$D$445,2,FALSE)&D537&\"_\"&VLOOKUP(E537,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B538&VLOOKUP(A538,List!$B$3:$D$445,2,FALSE)&D538&\"_\"&VLOOKUP(E538,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B539&VLOOKUP(A539,List!$B$3:$D$445,2,FALSE)&D539&\"_\"&VLOOKUP(E539,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B540&VLOOKUP(A540,List!$B$3:$D$445,2,FALSE)&D540&\"_\"&VLOOKUP(E540,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B541&VLOOKUP(A541,List!$B$3:$D$445,2,FALSE)&D541&\"_\"&VLOOKUP(E541,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B542&VLOOKUP(A542,List!$B$3:$D$445,2,FALSE)&D542&\"_\"&VLOOKUP(E542,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B543&VLOOKUP(A543,List!$B$3:$D$445,2,FALSE)&D543&\"_\"&VLOOKUP(E543,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B544&VLOOKUP(A544,List!$B$3:$D$445,2,FALSE)&D544&\"_\"&VLOOKUP(E544,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B545&VLOOKUP(A545,List!$B$3:$D$445,2,FALSE)&D545&\"_\"&VLOOKUP(E545,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B546&VLOOKUP(A546,List!$B$3:$D$445,2,FALSE)&D546&\"_\"&VLOOKUP(E546,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B547&VLOOKUP(A547,List!$B$3:$D$445,2,FALSE)&D547&\"_\"&VLOOKUP(E547,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B548&VLOOKUP(A548,List!$B$3:$D$445,2,FALSE)&D548&\"_\"&VLOOKUP(E548,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B549&VLOOKUP(A549,List!$B$3:$D$445,2,FALSE)&D549&\"_\"&VLOOKUP(E549,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B550&VLOOKUP(A550,List!$B$3:$D$445,2,FALSE)&D550&\"_\"&VLOOKUP(E550,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B551&VLOOKUP(A551,List!$B$3:$D$445,2,FALSE)&D551&\"_\"&VLOOKUP(E551,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B552&VLOOKUP(A552,List!$B$3:$D$445,2,FALSE)&D552&\"_\"&VLOOKUP(E552,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B553&VLOOKUP(A553,List!$B$3:$D$445,2,FALSE)&D553&\"_\"&VLOOKUP(E553,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B554&VLOOKUP(A554,List!$B$3:$D$445,2,FALSE)&D554&\"_\"&VLOOKUP(E554,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$f":"REPLACE(REPLACE(L554,SEARCH(\"AT%\",L554),,REPT(\" \",25-SEARCH(\"AT%\",L554))),SEARCH(\":\",REPLACE(L554,SEARCH(\"AT%\",L554),,REPT(\" \",25-SEARCH(\"AT%\",L554)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(L554,SEARCH(\"AT%\",L554),,REPT(\" \",25-SEARCH(\"AT%\",L554))))))","v":{"$error":"#N/A"}}]
[{"$nulls":10},{"$f":"B555&VLOOKUP(A555,List!$B$3:$D$445,2,FALSE)&D555&\"_\"&VLOOKUP(E555,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B556&VLOOKUP(A556,List!$B$3:$D$445,2,FALSE)&D556&\"_\"&VLOOKUP(E556,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B557&VLOOKUP(A557,List!$B$3:$D$445,2,FALSE)&D557&\"_\"&VLOOKUP(E557,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B558&VLOOKUP(A558,List!$B$3:$D$445,2,FALSE)&D558&\"_\"&VLOOKUP(E558,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B559&VLOOKUP(A559,List!$B$3:$D$445,2,FALSE)&D559&\"_\"&VLOOKUP(E559,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B560&VLOOKUP(A560,List!$B$3:$D$445,2,FALSE)&D560&\"_\"&VLOOKUP(E560,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B561&VLOOKUP(A561,List!$B$3:$D$445,2,FALSE)&D561&\"_\"&VLOOKUP(E561,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B562&VLOOKUP(A562,List!$B$3:$D$445,2,FALSE)&D562&\"_\"&VLOOKUP(E562,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B563&VLOOKUP(A563,List!$B$3:$D$445,2,FALSE)&D563&\"_\"&VLOOKUP(E563,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B564&VLOOKUP(A564,List!$B$3:$D$445,2,FALSE)&D564&\"_\"&VLOOKUP(E564,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B565&VLOOKUP(A565,List!$B$3:$D$445,2,FALSE)&D565&\"_\"&VLOOKUP(E565,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B566&VLOOKUP(A566,List!$B$3:$D$445,2,FALSE)&D566&\"_\"&VLOOKUP(E566,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B567&VLOOKUP(A567,List!$B$3:$D$445,2,FALSE)&D567&\"_\"&VLOOKUP(E567,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B568&VLOOKUP(A568,List!$B$3:$D$445,2,FALSE)&D568&\"_\"&VLOOKUP(E568,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B569&VLOOKUP(A569,List!$B$3:$D$445,2,FALSE)&D569&\"_\"&VLOOKUP(E569,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B570&VLOOKUP(A570,List!$B$3:$D$445,2,FALSE)&D570&\"_\"&VLOOKUP(E570,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B571&VLOOKUP(A571,List!$B$3:$D$445,2,FALSE)&D571&\"_\"&VLOOKUP(E571,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B572&VLOOKUP(A572,List!$B$3:$D$445,2,FALSE)&D572&\"_\"&VLOOKUP(E572,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B573&VLOOKUP(A573,List!$B$3:$D$445,2,FALSE)&D573&\"_\"&VLOOKUP(E573,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B574&VLOOKUP(A574,List!$B$3:$D$445,2,FALSE)&D574&\"_\"&VLOOKUP(E574,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B575&VLOOKUP(A575,List!$B$3:$D$445,2,FALSE)&D575&\"_\"&VLOOKUP(E575,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B576&VLOOKUP(A576,List!$B$3:$D$445,2,FALSE)&D576&\"_\"&VLOOKUP(E576,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"K576&\" \"&\"AT%\"&C576&F576&\" \"&\":\"&I576&\";\"&\" \"&\"(*\"&J576&\"*)\"","v":{"$error":"#N/A"}},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B577&VLOOKUP(A577,List!$B$3:$D$445,2,FALSE)&D577&\"_\"&VLOOKUP(E577,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B578&VLOOKUP(A578,List!$B$3:$D$445,2,FALSE)&D578&\"_\"&VLOOKUP(E578,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B579&VLOOKUP(A579,List!$B$3:$D$445,2,FALSE)&D579&\"_\"&VLOOKUP(E579,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B580&VLOOKUP(A580,List!$B$3:$D$445,2,FALSE)&D580&\"_\"&VLOOKUP(E580,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B581&VLOOKUP(A581,List!$B$3:$D$445,2,FALSE)&D581&\"_\"&VLOOKUP(E581,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B582&VLOOKUP(A582,List!$B$3:$D$445,2,FALSE)&D582&\"_\"&VLOOKUP(E582,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B583&VLOOKUP(A583,List!$B$3:$D$445,2,FALSE)&D583&\"_\"&VLOOKUP(E583,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B584&VLOOKUP(A584,List!$B$3:$D$445,2,FALSE)&D584&\"_\"&VLOOKUP(E584,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B585&VLOOKUP(A585,List!$B$3:$D$445,2,FALSE)&D585&\"_\"&VLOOKUP(E585,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B586&VLOOKUP(A586,List!$B$3:$D$445,2,FALSE)&D586&\"_\"&VLOOKUP(E586,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B587&VLOOKUP(A587,List!$B$3:$D$445,2,FALSE)&D587&\"_\"&VLOOKUP(E587,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B588&VLOOKUP(A588,List!$B$3:$D$445,2,FALSE)&D588&\"_\"&VLOOKUP(E588,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B589&VLOOKUP(A589,List!$B$3:$D$445,2,FALSE)&D589&\"_\"&VLOOKUP(E589,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B590&VLOOKUP(A590,List!$B$3:$D$445,2,FALSE)&D590&\"_\"&VLOOKUP(E590,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B591&VLOOKUP(A591,List!$B$3:$D$445,2,FALSE)&D591&\"_\"&VLOOKUP(E591,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B592&VLOOKUP(A592,List!$B$3:$D$445,2,FALSE)&D592&\"_\"&VLOOKUP(E592,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B593&VLOOKUP(A593,List!$B$3:$D$445,2,FALSE)&D593&\"_\"&VLOOKUP(E593,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B594&VLOOKUP(A594,List!$B$3:$D$445,2,FALSE)&D594&\"_\"&VLOOKUP(E594,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B595&VLOOKUP(A595,List!$B$3:$D$445,2,FALSE)&D595&\"_\"&VLOOKUP(E595,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B596&VLOOKUP(A596,List!$B$3:$D$445,2,FALSE)&D596&\"_\"&VLOOKUP(E596,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]
[{"$nulls":10},{"$f":"B597&VLOOKUP(A597,List!$B$3:$D$445,2,FALSE)&D597&\"_\"&VLOOKUP(E597,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$error":"#N/A"},{"$error":"#N/A"}]

{"sheet":"L201","index":5,"n_rows":94,"n_cols":45,"rows_kept":94,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[6,1,6,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[75,5,75,6],[75,9,75,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[84,5,84,6],[84,9,84,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[92,5,92,6],[92,9,92,25],[93,5,93,6],[93,9,93,25],[4,1,5,1],[12,1,23,1],[29,1,40,1],[46,1,57,1],[63,1,66,1],[72,1,75,1],[81,1,84,1],[90,1,93,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[16,2,23,4],[33,2,40,4],[50,2,57,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L11",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"EXC-1000"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B13&\"地址: \"&B10&\" *)\"","v":"(* IOM 1601R地址: 0 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH9&AA9&\"-\"&AK9","v":"空调机组NJ-2AP(KT)1-1-运行状态"},{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-2AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-1","02A01","运行状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU02A01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B10*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU02A01_R AT%I0.0 :BOOL; (*空调机组NJ-2AP(KT)1-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9))),SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))))),\" \")","v":"LAHU02A01_R             AT%I0.0        :BOOL; (*空调机组NJ-2AP(KT)1-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM9","v":"L11\\L11AHU02A01_R"},{"$f":"J9","v":"空调机组NJ-2AP(KT)1-1-运行状态"},{"$f":"10000+($B10*16*8+F9-1)","v":10000}]
[null,0,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-2AP(KT)1-1-故障状态",{"$nulls":16},{"$f":"IF(AI10=\"\",\"\",AI10)","v":"NJ-2AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-1","02A01","故障状态",{"$f":"AH10&\"-\"&AK10","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU02A01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B10*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU02A01_F AT%I0.1 :BOOL; (*空调机组NJ-2AP(KT)1-1-故障状态*)"},"LAHU02A01_F             AT%I0.1        :BOOL; (*空调机组NJ-2AP(KT)1-1-故障状态*)",null,"L11\\L11AHU02A01_F",{"$f":"J10","v":"空调机组NJ-2AP(KT)1-1-故障状态"},{"$f":"AS9+1","v":10001}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-2AP(KT)1-1-自动状态",{"$nulls":16},"NJ-2AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-1","02A01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU02A01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B10*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU02A01_A AT%I0.2 :BOOL; (*空调机组NJ-2AP(KT)1-1-自动状态*)"},"LAHU02A01_A             AT%I0.2        :BOOL; (*空调机组NJ-2AP(KT)1-1-自动状态*)",null,"L11\\L11AHU02A01_A","空调机组NJ-2AP(KT)1-1-自动状态",{"$f":"AS10+1","v":10002}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-2AP(KT)1-1-风机压差",{"$nulls":16},"NJ-2AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-1","02A01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU02A01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B10*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU02A01_FPS AT%I0.3 :BOOL; (*空调机组NJ-2AP(KT)1-1-风机压差*)"},"LAHU02A01_FPS           AT%I0.3        :BOOL; (*空调机组NJ-2AP(KT)1-1-风机压差*)",null,"L11\\L11AHU02A01_FPS","空调机组NJ-2AP(KT)1-1-风机压差",10003]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-2AP(KT)1-1-运行状态",{"$nulls":16},"NJ-2AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-1","02A02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU02A02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B10*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU02A02_R AT%I0.4 :BOOL; (*空调机组NJ-2AP(KT)1-1-运行状态*)"},"LAHU02A02_R             AT%I0.4        :BOOL; (*空调机组NJ-2AP(KT)1-1-运行状态*)",null,"L11\\L11AHU02A02_R","空调机组NJ-2AP(KT)1-1-运行状态",10004]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-2AP(KT)1-2-故障状态",{"$nulls":16},"NJ-2AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-2","02A02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU02A02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B10*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU02A02_F AT%I0.5 :BOOL; (*空调机组NJ-2AP(KT)1-2-故障状态*)"},"LAHU02A02_F             AT%I0.5        :BOOL; (*空调机组NJ-2AP(KT)1-2-故障状态*)",null,"L11\\L11AHU02A02_F","空调机组NJ-2AP(KT)1-2-故障状态",10005]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-2AP(KT)1-2-自动状态",{"$nulls":16},"NJ-2AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-2","02A02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU02A02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B10*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU02A02_A AT%I0.6 :BOOL; (*空调机组NJ-2AP(KT)1-2-自动状态*)"},"LAHU02A02_A             AT%I0.6        :BOOL; (*空调机组NJ-2AP(KT)1-2-自动状态*)",null,"L11\\L11AHU02A02_A","空调机组NJ-2AP(KT)1-2-自动状态",10006]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-2AP(KT)1-2-风机压差",{"$nulls":16},"NJ-2AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-2","02A02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU02A02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B10*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU02A02_FPS AT%I0.7 :BOOL; (*空调机组NJ-2AP(KT)1-2-风机压差*)"},"LAHU02A02_FPS           AT%I0.7        :BOOL; (*空调机组NJ-2AP(KT)1-2-风机压差*)",null,"L11\\L11AHU02A02_FPS","空调机组NJ-2AP(KT)1-2-风机压差",10007]
[{"$nulls":5},9,null,17,18,"空调机组NJ-2AP(KT)1-2-运行状态",{"$nulls":16},"NJ-2AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-2","02A03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU02A03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B10*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU02A03_R AT%I1.0 :BOOL; (*空调机组NJ-2AP(KT)1-2-运行状态*)"},"LAHU02A03_R             AT%I1.0        :BOOL; (*空调机组NJ-2AP(KT)1-2-运行状态*)",null,"L11\\L11AHU02A03_R","空调机组NJ-2AP(KT)1-2-运行状态",10008]
[{"$nulls":5},10,null,19,20,"空调机组NJ-2AP(KT)1-3-故障状态",{"$nulls":16},{"$f":"IF(AI18=\"\",\"\",AI18)","v":"NJ-2AP(KT)1-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-3","02A03","故障状态",{"$f":"AH18&\"-\"&AK18","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU02A03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B10*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU02A03_F AT%I1.1 :BOOL; (*空调机组NJ-2AP(KT)1-3-故障状态*)"},"LAHU02A03_F             AT%I1.1        :BOOL; (*空调机组NJ-2AP(KT)1-3-故障状态*)",null,"L11\\L11AHU02A03_F","空调机组NJ-2AP(KT)1-3-故障状态",10009]
[{"$nulls":5},11,null,21,22,"空调机组NJ-2AP(KT)1-3-自动状态",{"$nulls":16},"NJ-2AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-3","02A03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU02A03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B10*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU02A03_A AT%I1.2 :BOOL; (*空调机组NJ-2AP(KT)1-3-自动状态*)"},"LAHU02A03_A             AT%I1.2        :BOOL; (*空调机组NJ-2AP(KT)1-3-自动状态*)",null,"L11\\L11AHU02A03_A","空调机组NJ-2AP(KT)1-3-自动状态",10010]
[{"$nulls":5},12,null,23,24,"空调机组NJ-2AP(KT)1-3-风机压差",{"$nulls":16},"NJ-2AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-3","02A03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU02A03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B10*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU02A03_FPS AT%I1.3 :BOOL; (*空调机组NJ-2AP(KT)1-3-风机压差*)"},"LAHU02A03_FPS           AT%I1.3        :BOOL; (*空调机组NJ-2AP(KT)1-3-风机压差*)",null,"L11\\L11AHU02A03_FPS","空调机组NJ-2AP(KT)1-3-风机压差",10011]
[{"$nulls":5},13,null,25,26,"空调机组NJ-2AP(KT)1-4-运行状态",{"$nulls":16},"NJ-2AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-4","02A04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU02A04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B10*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU02A04_R AT%I1.4 :BOOL; (*空调机组NJ-2AP(KT)1-4-运行状态*)"},"LAHU02A04_R             AT%I1.4        :BOOL; (*空调机组NJ-2AP(KT)1-4-运行状态*)",null,"L11\\L11AHU02A04_R","空调机组NJ-2AP(KT)1-4-运行状态",10012]
[{"$nulls":5},14,null,27,28,"空调机组NJ-2AP(KT)1-4-故障状态",{"$nulls":16},"NJ-2AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-4","02A04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU02A04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B10*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU02A04_F AT%I1.5 :BOOL; (*空调机组NJ-2AP(KT)1-4-故障状态*)"},"LAHU02A04_F             AT%I1.5        :BOOL; (*空调机组NJ-2AP(KT)1-4-故障状态*)",null,"L11\\L11AHU02A04_F","空调机组NJ-2AP(KT)1-4-故障状态",10013]
[{"$nulls":5},15,null,29,30,"空调机组NJ-2AP(KT)1-4-自动状态",{"$nulls":16},"NJ-2AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-4","02A04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU02A04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B10*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU02A04_A AT%I1.6 :BOOL; (*空调机组NJ-2AP(KT)1-4-自动状态*)"},"LAHU02A04_A             AT%I1.6        :BOOL; (*空调机组NJ-2AP(KT)1-4-自动状态*)",null,"L11\\L11AHU02A04_A","空调机组NJ-2AP(KT)1-4-自动状态",10014]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-2AP(KT)1-4-风机压差",{"$nulls":16},"NJ-2AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-4","02A04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH24,List!$B$3:$D$445,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,List!$K$2:$M$447,2,FALSE)","v":"AHU02A04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%I\"&B10*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":"LAHU02A04_FPS AT%I1.7 :BOOL; (*空调机组NJ-2AP(KT)1-4-风机压差*)"},"LAHU02A04_FPS           AT%I1.7        :BOOL; (*空调机组NJ-2AP(KT)1-4-风机压差*)",null,"L11\\L11AHU02A04_FPS","空调机组NJ-2AP(KT)1-4-风机压差",10015]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 1601R地址: 1 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH26&AA26&\"-\"&AK26","v":"空调机组NJ-2AP(KT)1-5-运行状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-2AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-5","02A05","运行状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU02A05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU02A05_R AT%I16.0 :BOOL; (*空调机组NJ-2AP(KT)1-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LAHU02A05_R             AT%I16.0       :BOOL; (*空调机组NJ-2AP(KT)1-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L11\\L11AHU02A05_R"},{"$f":"J26","v":"空调机组NJ-2AP(KT)1-5-运行状态"},{"$f":"10000+($B27*16*8+F26-1)","v":10128}]
[null,1,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-2AP(KT)1-5-故障状态",{"$nulls":16},{"$f":"IF(AI27=\"\",\"\",AI27)","v":"NJ-2AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-5","02A05","故障状态",{"$f":"AH27&\"-\"&AK27","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU02A05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU02A05_F AT%I16.1 :BOOL; (*空调机组NJ-2AP(KT)1-5-故障状态*)"},"LAHU02A05_F             AT%I16.1       :BOOL; (*空调机组NJ-2AP(KT)1-5-故障状态*)",null,"L11\\L11AHU02A05_F",{"$f":"J27","v":"空调机组NJ-2AP(KT)1-5-故障状态"},{"$f":"AS26+1","v":10129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-2AP(KT)1-5-自动状态",{"$nulls":16},"NJ-2AP(KT)1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-5","02A05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU02A05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU02A05_A AT%I16.2 :BOOL; (*空调机组NJ-2AP(KT)1-5-自动状态*)"},"LAHU02A05_A             AT%I16.2       :BOOL; (*空调机组NJ-2AP(KT)1-5-自动状态*)",null,"L11\\L11AHU02A05_A","空调机组NJ-2AP(KT)1-5-自动状态",{"$f":"AS27+1","v":10130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-2AP(KT)1-5-风机压差",{"$nulls":16},"NJ-2AP(KT)1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-5","02A05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU02A05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU02A05_FPS AT%I16.3 :BOOL; (*空调机组NJ-2AP(KT)1-5-风机压差*)"},"LAHU02A05_FPS           AT%I16.3       :BOOL; (*空调机组NJ-2AP(KT)1-5-风机压差*)",null,"L11\\L11AHU02A05_FPS","空调机组NJ-2AP(KT)1-5-风机压差",10131]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-2AL1-1-运行状态",{"$nulls":16},"NJ-2AL1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL1-1","02A01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"LCB02A01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B27*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LLCB02A01_R AT%I16.4 :BOOL; (*照明控制箱NJ-2AL1-1-运行状态*)"},"LLCB02A01_R             AT%I16.4       :BOOL; (*照明控制箱NJ-2AL1-1-运行状态*)",null,"L11\\L11LCB02A01_R","照明控制箱NJ-2AL1-1-运行状态",10132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-2AL1-1-自动状态",{"$nulls":16},"NJ-2AL1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL1-1","02A01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"LCB02A01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B27*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LLCB02A01_A AT%I16.5 :BOOL; (*照明控制箱NJ-2AL1-1-自动状态*)"},"LLCB02A01_A             AT%I16.5       :BOOL; (*照明控制箱NJ-2AL1-1-自动状态*)",null,"L11\\L11LCB02A01_A","照明控制箱NJ-2AL1-1-自动状态",10133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"照明控制箱NJ-2AL1-2-运行状态",{"$nulls":16},"NJ-2AL1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL1-2","02A02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"LCB02A02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B27*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LLCB02A02_R AT%I16.6 :BOOL; (*照明控制箱NJ-2AL1-2-运行状态*)"},"LLCB02A02_R             AT%I16.6       :BOOL; (*照明控制箱NJ-2AL1-2-运行状态*)",null,"L11\\L11LCB02A02_R","照明控制箱NJ-2AL1-2-运行状态",10134]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"照明控制箱NJ-2AL1-2-自动状态",{"$nulls":16},"NJ-2AL1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL1-2","02A02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"LCB02A02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B27*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LLCB02A02_A AT%I16.7 :BOOL; (*照明控制箱NJ-2AL1-2-自动状态*)"},"LLCB02A02_A             AT%I16.7       :BOOL; (*照明控制箱NJ-2AL1-2-自动状态*)",null,"L11\\L11LCB02A02_A","照明控制箱NJ-2AL1-2-自动状态",10135]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-2AL1-3-运行状态",{"$nulls":16},"NJ-2AL1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL1-3","02A03","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"LCB02A03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B27*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LLCB02A03_R AT%I17.0 :BOOL; (*照明控制箱NJ-2AL1-3-运行状态*)"},"LLCB02A03_R             AT%I17.0       :BOOL; (*照明控制箱NJ-2AL1-3-运行状态*)",null,"L11\\L11LCB02A03_R","照明控制箱NJ-2AL1-3-运行状态",10136]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-2AL1-3-自动状态",{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-2AL1-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL1-3","02A03","自动状态",{"$f":"AH35&\"-\"&AK35","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"LCB02A03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B27*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LLCB02A03_A AT%I17.1 :BOOL; (*照明控制箱NJ-2AL1-3-自动状态*)"},"LLCB02A03_A             AT%I17.1       :BOOL; (*照明控制箱NJ-2AL1-3-自动状态*)",null,"L11\\L11LCB02A03_A","照明控制箱NJ-2AL1-3-自动状态",10137]
[{"$nulls":5},11,null,21,22,"照明控制箱NJ-2AL1-4-运行状态",{"$nulls":16},"NJ-2AL1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL1-4","02A04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"LCB02A04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B27*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LLCB02A04_R AT%I17.2 :BOOL; (*照明控制箱NJ-2AL1-4-运行状态*)"},"LLCB02A04_R             AT%I17.2       :BOOL; (*照明控制箱NJ-2AL1-4-运行状态*)",null,"L11\\L11LCB02A04_R","照明控制箱NJ-2AL1-4-运行状态",10138]
[{"$nulls":5},12,null,23,24,"照明控制箱NJ-2AL1-4-自动状态",{"$nulls":16},"NJ-2AL1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL1-4","02A04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"LCB02A04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B27*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LLCB02A04_A AT%I17.3 :BOOL; (*照明控制箱NJ-2AL1-4-自动状态*)"},"LLCB02A04_A             AT%I17.3       :BOOL; (*照明控制箱NJ-2AL1-4-自动状态*)",null,"L11\\L11LCB02A04_A","照明控制箱NJ-2AL1-4-自动状态",10139]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-2AL1-5-运行状态",{"$nulls":16},"NJ-2AL1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL1-5","02A05","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB02A05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B27*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB02A05_R AT%I17.4 :BOOL; (*照明控制箱NJ-2AL1-5-运行状态*)"},"LLCB02A05_R             AT%I17.4       :BOOL; (*照明控制箱NJ-2AL1-5-运行状态*)",null,"L11\\L11LCB02A05_R","照明控制箱NJ-2AL1-5-运行状态",10140]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-2AL1-5-自动状态",{"$nulls":16},"NJ-2AL1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL1-5","02A05","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB02A05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B27*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB02A05_A AT%I17.5 :BOOL; (*照明控制箱NJ-2AL1-5-自动状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN39,SEARCH(\"AT%\",AN39),,REPT(\" \",25-SEARCH(\"AT%\",AN39))),SEARCH(\":\",REPLACE(AN39,SEARCH(\"AT%\",AN39),,REPT(\" \",25-SEARCH(\"AT%\",AN39)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN39,SEARCH(\"AT%\",AN39),,REPT(\" \",25-SEARCH(\"AT%\",AN39)))))),\" \")","v":"LLCB02A05_A             AT%I17.5       :BOOL; (*照明控制箱NJ-2AL1-5-自动状态*)"},null,"L11\\L11LCB02A05_A","照明控制箱NJ-2AL1-5-自动状态",10141]
[{"$nulls":5},15,null,29,30,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B27*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN40,SEARCH(\"AT%\",AN40),,REPT(\" \",30-SEARCH(\"AT%\",AN40))),SEARCH(\":\",REPLACE(AN40,SEARCH(\"AT%\",AN40),,REPT(\" \",30-SEARCH(\"AT%\",AN40)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN40,SEARCH(\"AT%\",AN40),,REPT(\" \",25-SEARCH(\"AT%\",AN40)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",10142]
[".",{"$nulls":4},16,null,31,32,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%I\"&B27*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10143]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 1601D地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH43&AA43&\"-\"&AK43","v":"空调机组NJ-2AP(KT)1-1-启停控制"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-2AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-1","02A01","启停控制",{"$f":"AH43&\"-\"&AK43","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"AHU02A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%Q\"&B44*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LAHU02A01_C AT%Q32.0 :BOOL; (*空调机组NJ-2AP(KT)1-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LAHU02A01_C             AT%Q32.0       :BOOL; (*空调机组NJ-2AP(KT)1-1-启停控制*)"},null,{"$f":"AM43","v":"AHU02A01_C"},{"$f":"J43","v":"空调机组NJ-2AP(KT)1-1-启停控制"},{"$f":"($B44*16*8+F43-1)","v":256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-2AP(KT)1-2-启停控制",{"$nulls":16},{"$f":"IF(AI44=\"\",\"\",AI44)","v":"NJ-2AP(KT)1-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-2","02A02","启停控制",{"$f":"AH44&\"-\"&AK44","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"AHU02A02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%Q\"&B44*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LAHU02A02_C AT%Q32.1 :BOOL; (*空调机组NJ-2AP(KT)1-2-启停控制*)"},"LAHU02A02_C             AT%Q32.1       :BOOL; (*空调机组NJ-2AP(KT)1-2-启停控制*)",null,"AHU02A02_C",{"$f":"J44","v":"空调机组NJ-2AP(KT)1-2-启停控制"},{"$f":"AS43+1","v":257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","空调机组NJ-2AP(KT)1-3-启停控制",{"$nulls":16},"NJ-2AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-3","02A03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"AHU02A03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%Q\"&B44*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LAHU02A03_C AT%Q32.2 :BOOL; (*空调机组NJ-2AP(KT)1-3-启停控制*)"},"LAHU02A03_C             AT%Q32.2       :BOOL; (*空调机组NJ-2AP(KT)1-3-启停控制*)",null,"AHU02A03_C","空调机组NJ-2AP(KT)1-3-启停控制",{"$f":"AS44+1","v":258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","空调机组NJ-2AP(KT)1-4-启停控制",{"$nulls":16},"NJ-2AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-4","02A04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"AHU02A04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%Q\"&B44*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LAHU02A04_C AT%Q32.3 :BOOL; (*空调机组NJ-2AP(KT)1-4-启停控制*)"},"LAHU02A04_C             AT%Q32.3       :BOOL; (*空调机组NJ-2AP(KT)1-4-启停控制*)",null,"AHU02A04_C","空调机组NJ-2AP(KT)1-4-启停控制",259]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-2AP(KT)1-5-启停控制",{"$nulls":16},"NJ-2AP(KT)1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-5","02A05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"AHU02A05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%Q\"&B44*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LAHU02A05_C AT%Q32.4 :BOOL; (*空调机组NJ-2AP(KT)1-5-启停控制*)"},"LAHU02A05_C             AT%Q32.4       :BOOL; (*空调机组NJ-2AP(KT)1-5-启停控制*)",null,"AHU02A05_C","空调机组NJ-2AP(KT)1-5-启停控制",260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","照明控制箱NJ-2AL1-1-启停控制",{"$nulls":16},"NJ-2AL1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL1-1","02A01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"LCB02A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%Q\"&B44*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LLCB02A01_C AT%Q32.5 :BOOL; (*照明控制箱NJ-2AL1-1-启停控制*)"},"LLCB02A01_C             AT%Q32.5       :BOOL; (*照明控制箱NJ-2AL1-1-启停控制*)",null,"LCB02A01_C","照明控制箱NJ-2AL1-1-启停控制",261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","照明控制箱NJ-2AL1-2-启停控制",{"$nulls":16},"NJ-2AL1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过","无法正常控制",null,"照明控制箱","NJ-2AL1-2","02A02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"LCB02A02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%Q\"&B44*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LLCB02A02_C AT%Q32.6 :BOOL; (*照明控制箱NJ-2AL1-2-启停控制*)"},"LLCB02A02_C             AT%Q32.6       :BOOL; (*照明控制箱NJ-2AL1-2-启停控制*)",null,"LCB02A02_C","照明控制箱NJ-2AL1-2-启停控制",262]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-2AL1-3-启停控制",{"$nulls":16},"NJ-2AL1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL1-3","02A03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"LCB02A03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%Q\"&B44*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LLCB02A03_C AT%Q32.7 :BOOL; (*照明控制箱NJ-2AL1-3-启停控制*)"},"LLCB02A03_C             AT%Q32.7       :BOOL; (*照明控制箱NJ-2AL1-3-启停控制*)",null,"LCB02A03_C","照明控制箱NJ-2AL1-3-启停控制",263]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-2AL1-4-启停控制",{"$nulls":16},"NJ-2AL1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL1-4","02A04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"LCB02A04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%Q\"&B44*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LLCB02A04_C AT%Q33.0 :BOOL; (*照明控制箱NJ-2AL1-4-启停控制*)"},"LLCB02A04_C             AT%Q33.0       :BOOL; (*照明控制箱NJ-2AL1-4-启停控制*)",null,"LCB02A04_C","照明控制箱NJ-2AL1-4-启停控制",264]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-2AL1-5-启停控制",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-2AL1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL1-5","02A05","启停控制",{"$f":"AH52&\"-\"&AK52","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"LCB02A05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%Q\"&B44*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LLCB02A05_C AT%Q33.1 :BOOL; (*照明控制箱NJ-2AL1-5-启停控制*)"},"LLCB02A05_C             AT%Q33.1       :BOOL; (*照明控制箱NJ-2AL1-5-启停控制*)",null,"LCB02A05_C",{"$f":"J52","v":"照明控制箱NJ-2AL1-5-启停控制"},265]
[{"$nulls":5},11,null,"11+","11-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%Q\"&B44*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",266]
[{"$nulls":5},12,null,"12+","12-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%Q\"&B44*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",267]
[{"$nulls":5},13,null,"13+","13-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%Q\"&B44*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",268]
[{"$nulls":5},14,null,"14+","14-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%Q\"&B44*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",269]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%Q\"&B44*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",270]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%Q\"&B44*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",271]
[null,{"$f":"B64","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B64&\"地址: \"&B61&\" *)\"","v":"(* IOM 0801U地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH60&AA60&\"-\"&AK60","v":"空调机组NJ-2AP(KT)1-1-回风温度"},{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-2AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-1","02A01","回风温度",{"$f":"AH60&\"-\"&AK60","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"AHU02A01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%I\"&B61*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LAHU02A01_RT AT%I48.0 :INT ; (*空调机组NJ-2AP(KT)1-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60))),SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))))),\" \")","v":"LAHU02A01_RT            AT%I48.0       :INT ; (*空调机组NJ-2AP(KT)1-1-回风温度*)"},null,{"$f":"AM60","v":"AHU02A01_RT"},{"$f":"J60","v":"空调机组NJ-2AP(KT)1-1-回风温度"},{"$f":"30000+($B61*8+F60-1)","v":30024}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-2AP(KT)1-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI61=\"\",\"\",AI61)","v":"NJ-2AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-1","02A01","水阀反馈",{"$f":"AH61&\"-\"&AK61","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"AHU02A01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%I\"&B61*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LAHU02A01_WVB AT%I50.0 :INT ; (*空调机组NJ-2AP(KT)1-1-水阀反馈*)"},"LAHU02A01_WVB           AT%I50.0       :INT ; (*空调机组NJ-2AP(KT)1-1-水阀反馈*)",null,"AHU02A01_WVB",{"$f":"J61","v":"空调机组NJ-2AP(KT)1-1-水阀反馈"},{"$f":"AS60+1","v":30025}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-2AP(KT)1-2-回风温度",{"$nulls":16},"NJ-2AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-2","02A02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"AHU02A02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B61*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LAHU02A02_RT AT%I52.0 :INT ; (*空调机组NJ-2AP(KT)1-2-回风温度*)"},"LAHU02A02_RT            AT%I52.0       :INT ; (*空调机组NJ-2AP(KT)1-2-回风温度*)",null,"AHU02A02_RT","空调机组NJ-2AP(KT)1-2-回风温度",{"$f":"AS61+1","v":30026}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-2AP(KT)1-2-水阀反馈",{"$nulls":16},"NJ-2AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-2","02A02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"AHU02A02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B61*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LAHU02A02_WVB AT%I54.0 :INT ; (*空调机组NJ-2AP(KT)1-2-水阀反馈*)"},"LAHU02A02_WVB           AT%I54.0       :INT ; (*空调机组NJ-2AP(KT)1-2-水阀反馈*)",null,"AHU02A02_WVB","空调机组NJ-2AP(KT)1-2-水阀反馈",30027]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-2AP(KT)1-3-回风温度",{"$nulls":16},"NJ-2AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-3","02A03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"AHU02A03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B61*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LAHU02A03_RT AT%I56.0 :INT ; (*空调机组NJ-2AP(KT)1-3-回风温度*)"},"LAHU02A03_RT            AT%I56.0       :INT ; (*空调机组NJ-2AP(KT)1-3-回风温度*)",null,"AHU02A03_RT","空调机组NJ-2AP(KT)1-3-回风温度",30028]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-2AP(KT)1-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI65=\"\",\"\",AI65)","v":"NJ-2AP(KT)1-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-3","02A03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":"AHU02A03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B61*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":"LAHU02A03_WVB AT%I58.0 :INT ; (*空调机组NJ-2AP(KT)1-3-水阀反馈*)"},"LAHU02A03_WVB           AT%I58.0       :INT ; (*空调机组NJ-2AP(KT)1-3-水阀反馈*)",null,"AHU02A03_WVB",{"$f":"J65","v":"空调机组NJ-2AP(KT)1-3-水阀反馈"},30029]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-2AP(KT)1-4-回风温度",{"$nulls":16},"NJ-2AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-4","02A04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":"AHU02A04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B61*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":"LAHU02A04_RT AT%I60.0 :INT ; (*空调机组NJ-2AP(KT)1-4-回风温度*)"},"LAHU02A04_RT            AT%I60.0       :INT ; (*空调机组NJ-2AP(KT)1-4-回风温度*)",null,"AHU02A04_RT","空调机组NJ-2AP(KT)1-4-回风温度",30030]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-2AP(KT)1-4-水阀反馈",{"$nulls":16},"NJ-2AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-4","02A04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":"AHU02A04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%I\"&B61*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":"LAHU02A04_WVB AT%I62.0 :INT ; (*空调机组NJ-2AP(KT)1-4-水阀反馈*)"},"LAHU02A04_WVB           AT%I62.0       :INT ; (*空调机组NJ-2AP(KT)1-4-水阀反馈*)",null,"AHU02A04_WVB","空调机组NJ-2AP(KT)1-4-水阀反馈",30031]
[null,{"$f":"B73","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B73&\"地址: \"&B70&\" *)\"","v":"(* IOM 0401U地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH69&AA69&\"-\"&AK69","v":"空调机组NJ-2AP(KT)1-5-回风温度"},{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-2AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-5","02A05","回风温度",{"$f":"AH69&\"-\"&AK69","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU02A05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%I\"&B70*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU02A05_RT AT%I64.0 :INT ; (*空调机组NJ-2AP(KT)1-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69))),SEARCH(\":\",REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69)))))),\" \")","v":"LAHU02A05_RT            AT%I64.0       :INT ; (*空调机组NJ-2AP(KT)1-5-回风温度*)"},null,{"$f":"AM69","v":"AHU02A05_RT"},{"$f":"J69","v":"空调机组NJ-2AP(KT)1-5-回风温度"},{"$f":"30000+($B70*8+F69-1)","v":30032}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-2AP(KT)1-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI70=\"\",\"\",AI70)","v":"NJ-2AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-5","02A05","水阀反馈",{"$f":"AH70&\"-\"&AK70","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"AHU02A05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%I\"&B70*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LAHU02A05_WVB AT%I66.0 :INT ; (*空调机组NJ-2AP(KT)1-5-水阀反馈*)"},"LAHU02A05_WVB           AT%I66.0       :INT ; (*空调机组NJ-2AP(KT)1-5-水阀反馈*)",null,"AHU02A05_WVB",{"$f":"J70","v":"空调机组NJ-2AP(KT)1-5-水阀反馈"},{"$f":"AS69+1","v":30033}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),3,1))","v":1},3,null,3,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%I\"&B70*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS70+1","v":30034}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),2,1))","v":0},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%I\"&B70*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30035]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),1,1))","v":0}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B82","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B82&\"地址: \"&B79&\" *)\"","v":"(* IOM 0401A地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH78&AA78&\"-\"&AK78","v":"空调机组NJ-2AP(KT)1-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-2AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-1","02A01","水阀控制",{"$f":"AH78&\"-\"&AK78","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU02A01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B79*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU02A01_WVC AT%Q80.0 :INT ; (*空调机组NJ-2AP(KT)1-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN78,SEARCH(\"AT%\",AN78),,REPT(\" \",25-SEARCH(\"AT%\",AN78))),SEARCH(\":\",REPLACE(AN78,SEARCH(\"AT%\",AN78),,REPT(\" \",25-SEARCH(\"AT%\",AN78)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN78,SEARCH(\"AT%\",AN78),,REPT(\" \",25-SEARCH(\"AT%\",AN78)))))),\" \")","v":"LAHU02A01_WVC           AT%Q80.0       :INT ; (*空调机组NJ-2AP(KT)1-1-水阀控制*)"},null,{"$f":"AM78","v":"AHU02A01_WVC"},{"$f":"J78","v":"空调机组NJ-2AP(KT)1-1-水阀控制"},{"$f":"40000+($B79*8+F78-1)","v":40040}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH79&AA79&\"-\"&AK79","v":"空调机组NJ-2AP(KT)1-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI79=\"\",\"\",AI79)","v":"NJ-2AP(KT)1-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-2","02A02","水阀控制",{"$f":"AH79&\"-\"&AK79","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU02A02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B79*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU02A02_WVC AT%Q82.0 :INT ; (*空调机组NJ-2AP(KT)1-2-水阀控制*)"},"LAHU02A02_WVC           AT%Q82.0       :INT ; (*空调机组NJ-2AP(KT)1-2-水阀控制*)",null,"AHU02A02_WVC",{"$f":"J79","v":"空调机组NJ-2AP(KT)1-2-水阀控制"},{"$f":"AS78+1","v":40041}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH80&AA80&\"-\"&AK80","v":"空调机组NJ-2AP(KT)1-3-水阀控制"},{"$nulls":16},"NJ-2AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-3","02A03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU02A03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B79*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU02A03_WVC AT%Q84.0 :INT ; (*空调机组NJ-2AP(KT)1-3-水阀控制*)"},"LAHU02A03_WVC           AT%Q84.0       :INT ; (*空调机组NJ-2AP(KT)1-3-水阀控制*)",null,"AHU02A03_WVC","空调机组NJ-2AP(KT)1-3-水阀控制",{"$f":"AS79+1","v":40042}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH81&AA81&\"-\"&AK81","v":"空调机组NJ-2AP(KT)1-4-水阀控制"},{"$nulls":16},"NJ-2AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-4","02A04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"AHU02A04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%Q\"&B79*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LAHU02A04_WVC AT%Q86.0 :INT ; (*空调机组NJ-2AP(KT)1-4-水阀控制*)"},"LAHU02A04_WVC           AT%Q86.0       :INT ; (*空调机组NJ-2AP(KT)1-4-水阀控制*)",null,"AHU02A04_WVC","空调机组NJ-2AP(KT)1-4-水阀控制",40043]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B91","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B91&\"地址: \"&B88&\" *)\"","v":"(* IOM 0401A地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH87&AA87&\"-\"&AK87","v":"空调机组NJ-2AP(KT)1-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI87=\"\",\"\",AI87)","v":"NJ-2AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)1-5","02A05","水阀控制",{"$f":"AH87&\"-\"&AK87","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"AHU02A05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%Q\"&B88*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LAHU02A05_WVC AT%Q96.0 :INT ; (*空调机组NJ-2AP(KT)1-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN87,SEARCH(\"AT%\",AN87),,REPT(\" \",25-SEARCH(\"AT%\",AN87))),SEARCH(\":\",REPLACE(AN87,SEARCH(\"AT%\",AN87),,REPT(\" \",25-SEARCH(\"AT%\",AN87)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN87,SEARCH(\"AT%\",AN87),,REPT(\" \",25-SEARCH(\"AT%\",AN87)))))),\" \")","v":"LAHU02A05_WVC           AT%Q96.0       :INT ; (*空调机组NJ-2AP(KT)1-5-水阀控制*)"},null,{"$f":"AM87","v":"AHU02A05_WVC"},{"$f":"J87","v":"空调机组NJ-2AP(KT)1-5-水阀控制"},{"$f":"40000+($B88*8+F87-1)","v":40048}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH88&AA88&\"-\"&AK88","v":"-"},{"$nulls":16},{"$f":"IF(AI88=\"\",\"\",AI88)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},{"$f":"AH88&\"-\"&AK88","v":"-"},{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%Q\"&B88*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J88","v":"-"},{"$f":"AS87+1","v":40049}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH89&AA89&\"-\"&AK89","v":"-"},{"$nulls":16},{"$f":"IF(AI89=\"\",\"\",AI89)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},{"$f":"AH89&\"-\"&AK89","v":"-"},{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%Q\"&B88*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS88+1","v":40050}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH90&AA90&\"-\"&AK90","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%Q\"&B88*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40051]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L101","index":6,"n_rows":93,"n_cols":45,"rows_kept":93,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[41,5,41,6],[41,9,41,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[92,5,92,6],[92,9,92,25],[4,1,5,1],[11,1,22,1],[28,1,39,1],[45,1,56,1],[62,1,65,1],[71,1,74,1],[80,1,83,1],[89,1,92,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[49,2,56,4],[15,2,22,4],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[32,2,39,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L11",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 7 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH8&AA8&\"-\"&AK8","v":"空调机组NJ-1AP(KT)1-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-1AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-1","01A01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH8,List!$B$3:$D$445,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LAHU01A01_R AT%I112.0 :BOOL; (*空调机组NJ-1AP(KT)1-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LAHU01A01_R             AT%I112.0      :BOOL; (*空调机组NJ-1AP(KT)1-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L11\\L11AHU01A01_R"},{"$f":"J8","v":"空调机组NJ-1AP(KT)1-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":10896}]
[null,7,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},2,null,3,4,"空调机组NJ-1AP(KT)1-1-故障状态",{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-1AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-1","01A01","故障状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU01A01_F AT%I112.1 :BOOL; (*空调机组NJ-1AP(KT)1-1-故障状态*)"},"LAHU01A01_F             AT%I112.1      :BOOL; (*空调机组NJ-1AP(KT)1-1-故障状态*)",null,"L11\\L11AHU01A01_F",{"$f":"J9","v":"空调机组NJ-1AP(KT)1-1-故障状态"},{"$f":"AS8+1","v":10897}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},3,null,5,6,"空调机组NJ-1AP(KT)1-1-自动状态",{"$nulls":16},"NJ-1AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-1","01A01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU01A01_A AT%I112.2 :BOOL; (*空调机组NJ-1AP(KT)1-1-自动状态*)"},"LAHU01A01_A             AT%I112.2      :BOOL; (*空调机组NJ-1AP(KT)1-1-自动状态*)",null,"L11\\L11AHU01A01_A","空调机组NJ-1AP(KT)1-1-自动状态",{"$f":"AS9+1","v":10898}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-1AP(KT)1-1-风机压差",{"$nulls":16},"NJ-1AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-1","01A01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU01A01_FPS AT%I112.3 :BOOL; (*空调机组NJ-1AP(KT)1-1-风机压差*)"},"LAHU01A01_FPS           AT%I112.3      :BOOL; (*空调机组NJ-1AP(KT)1-1-风机压差*)",null,"L11\\L11AHU01A01_FPS","空调机组NJ-1AP(KT)1-1-风机压差",10899]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-1AP(KT)1-1-运行状态",{"$nulls":16},"NJ-1AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-1","01A02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU01A02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU01A02_R AT%I112.4 :BOOL; (*空调机组NJ-1AP(KT)1-1-运行状态*)"},"LAHU01A02_R             AT%I112.4      :BOOL; (*空调机组NJ-1AP(KT)1-1-运行状态*)",null,"L11\\L11AHU01A02_R","空调机组NJ-1AP(KT)1-1-运行状态",10900]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-1AP(KT)1-2-故障状态",{"$nulls":16},"NJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-2","01A02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU01A02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU01A02_F AT%I112.5 :BOOL; (*空调机组NJ-1AP(KT)1-2-故障状态*)"},"LAHU01A02_F             AT%I112.5      :BOOL; (*空调机组NJ-1AP(KT)1-2-故障状态*)",null,"L11\\L11AHU01A02_F","空调机组NJ-1AP(KT)1-2-故障状态",10901]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-1AP(KT)1-2-自动状态",{"$nulls":16},"NJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-2","01A02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU01A02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU01A02_A AT%I112.6 :BOOL; (*空调机组NJ-1AP(KT)1-2-自动状态*)"},"LAHU01A02_A             AT%I112.6      :BOOL; (*空调机组NJ-1AP(KT)1-2-自动状态*)",null,"L11\\L11AHU01A02_A","空调机组NJ-1AP(KT)1-2-自动状态",10902]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-1AP(KT)1-2-风机压差",{"$nulls":16},"NJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-2","01A02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU01A02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU01A02_FPS AT%I112.7 :BOOL; (*空调机组NJ-1AP(KT)1-2-风机压差*)"},"LAHU01A02_FPS           AT%I112.7      :BOOL; (*空调机组NJ-1AP(KT)1-2-风机压差*)",null,"L11\\L11AHU01A02_FPS","空调机组NJ-1AP(KT)1-2-风机压差",10903]
[{"$nulls":5},9,null,17,18,"空调机组NJ-1AP(KT)1-2-运行状态",{"$nulls":16},"NJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-2","01A03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU01A03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU01A03_R AT%I113.0 :BOOL; (*空调机组NJ-1AP(KT)1-2-运行状态*)"},"LAHU01A03_R             AT%I113.0      :BOOL; (*空调机组NJ-1AP(KT)1-2-运行状态*)",null,"L11\\L11AHU01A03_R","空调机组NJ-1AP(KT)1-2-运行状态",10904]
[{"$nulls":5},10,null,19,20,"空调机组NJ-1AP(KT)1-3-故障状态",{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-1AP(KT)1-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-3","01A03","故障状态",{"$f":"AH17&\"-\"&AK17","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU01A03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU01A03_F AT%I113.1 :BOOL; (*空调机组NJ-1AP(KT)1-3-故障状态*)"},"LAHU01A03_F             AT%I113.1      :BOOL; (*空调机组NJ-1AP(KT)1-3-故障状态*)",null,"L11\\L11AHU01A03_F","空调机组NJ-1AP(KT)1-3-故障状态",10905]
[{"$nulls":5},11,null,21,22,"空调机组NJ-1AP(KT)1-3-自动状态",{"$nulls":16},"NJ-1AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-3","01A03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU01A03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU01A03_A AT%I113.2 :BOOL; (*空调机组NJ-1AP(KT)1-3-自动状态*)"},"LAHU01A03_A             AT%I113.2      :BOOL; (*空调机组NJ-1AP(KT)1-3-自动状态*)",null,"L11\\L11AHU01A03_A","空调机组NJ-1AP(KT)1-3-自动状态",10906]
[{"$nulls":5},12,null,23,24,"空调机组NJ-1AP(KT)1-3-风机压差",{"$nulls":16},"NJ-1AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-3","01A03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU01A03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU01A03_FPS AT%I113.3 :BOOL; (*空调机组NJ-1AP(KT)1-3-风机压差*)"},"LAHU01A03_FPS           AT%I113.3      :BOOL; (*空调机组NJ-1AP(KT)1-3-风机压差*)",null,"L11\\L11AHU01A03_FPS","空调机组NJ-1AP(KT)1-3-风机压差",10907]
[{"$nulls":5},13,null,25,26,"空调机组NJ-1AP(KT)1-4-运行状态",{"$nulls":16},"NJ-1AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-4","01A04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU01A04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU01A04_R AT%I113.4 :BOOL; (*空调机组NJ-1AP(KT)1-4-运行状态*)"},"LAHU01A04_R             AT%I113.4      :BOOL; (*空调机组NJ-1AP(KT)1-4-运行状态*)",null,"L11\\L11AHU01A04_R","空调机组NJ-1AP(KT)1-4-运行状态",10908]
[{"$nulls":5},14,null,27,28,"空调机组NJ-1AP(KT)1-4-故障状态",{"$nulls":16},"NJ-1AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-4","01A04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU01A04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU01A04_F AT%I113.5 :BOOL; (*空调机组NJ-1AP(KT)1-4-故障状态*)"},"LAHU01A04_F             AT%I113.5      :BOOL; (*空调机组NJ-1AP(KT)1-4-故障状态*)",null,"L11\\L11AHU01A04_F","空调机组NJ-1AP(KT)1-4-故障状态",10909]
[{"$nulls":5},15,null,29,30,"空调机组NJ-1AP(KT)1-4-自动状态",{"$nulls":16},"NJ-1AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-4","01A04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU01A04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU01A04_A AT%I113.6 :BOOL; (*空调机组NJ-1AP(KT)1-4-自动状态*)"},"LAHU01A04_A             AT%I113.6      :BOOL; (*空调机组NJ-1AP(KT)1-4-自动状态*)",null,"L11\\L11AHU01A04_A","空调机组NJ-1AP(KT)1-4-自动状态",10910]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-1AP(KT)1-4-风机压差",{"$nulls":16},"NJ-1AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-4","01A04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU01A04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU01A04_FPS AT%I113.7 :BOOL; (*空调机组NJ-1AP(KT)1-4-风机压差*)"},"LAHU01A04_FPS           AT%I113.7      :BOOL; (*空调机组NJ-1AP(KT)1-4-风机压差*)",null,"L11\\L11AHU01A04_FPS","空调机组NJ-1AP(KT)1-4-风机压差",10911]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 1601R地址: 8 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH25&AA25&\"-\"&AK25","v":"空调机组NJ-1AP(KT)1-5-运行状态"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-1AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-5","01A05","运行状态",{"$f":"AH25&\"-\"&AK25","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"AHU01A05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LAHU01A05_R AT%I128.0 :BOOL; (*空调机组NJ-1AP(KT)1-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LAHU01A05_R             AT%I128.0      :BOOL; (*空调机组NJ-1AP(KT)1-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L11\\L11AHU01A05_R"},{"$f":"J25","v":"空调机组NJ-1AP(KT)1-5-运行状态"},{"$f":"10000+($B26*16*8+F25-1)","v":11024}]
[null,8,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-1AP(KT)1-5-故障状态",{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-1AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-5","01A05","故障状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU01A05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU01A05_F AT%I128.1 :BOOL; (*空调机组NJ-1AP(KT)1-5-故障状态*)"},"LAHU01A05_F             AT%I128.1      :BOOL; (*空调机组NJ-1AP(KT)1-5-故障状态*)",null,"L11\\L11AHU01A05_F",{"$f":"J26","v":"空调机组NJ-1AP(KT)1-5-故障状态"},{"$f":"AS25+1","v":11025}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-1AP(KT)1-5-自动状态",{"$nulls":16},"NJ-1AP(KT)1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-5","01A05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU01A05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU01A05_A AT%I128.2 :BOOL; (*空调机组NJ-1AP(KT)1-5-自动状态*)"},"LAHU01A05_A             AT%I128.2      :BOOL; (*空调机组NJ-1AP(KT)1-5-自动状态*)",null,"L11\\L11AHU01A05_A","空调机组NJ-1AP(KT)1-5-自动状态",{"$f":"AS26+1","v":11026}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-1AP(KT)1-5-风机压差",{"$nulls":16},"NJ-1AP(KT)1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-5","01A05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU01A05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU01A05_FPS AT%I128.3 :BOOL; (*空调机组NJ-1AP(KT)1-5-风机压差*)"},"LAHU01A05_FPS           AT%I128.3      :BOOL; (*空调机组NJ-1AP(KT)1-5-风机压差*)",null,"L11\\L11AHU01A05_FPS","空调机组NJ-1AP(KT)1-5-风机压差",11027]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-1AL1-1-运行状态",{"$nulls":16},"NJ-1AL1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL1-1","01A01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"LCB01A01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LLCB01A01_R AT%I128.4 :BOOL; (*照明控制箱NJ-1AL1-1-运行状态*)"},"LLCB01A01_R             AT%I128.4      :BOOL; (*照明控制箱NJ-1AL1-1-运行状态*)",null,"L11\\L11LCB01A01_R","照明控制箱NJ-1AL1-1-运行状态",11028]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-1AL1-1-自动状态",{"$nulls":16},"NJ-1AL1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL1-1","01A01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"LCB01A01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LLCB01A01_A AT%I128.5 :BOOL; (*照明控制箱NJ-1AL1-1-自动状态*)"},"LLCB01A01_A             AT%I128.5      :BOOL; (*照明控制箱NJ-1AL1-1-自动状态*)",null,"L11\\L11LCB01A01_A","照明控制箱NJ-1AL1-1-自动状态",11029]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"照明控制箱NJ-1AL1-2-运行状态",{"$nulls":16},"NJ-1AL1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL1-2","01A02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"LCB01A02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LLCB01A02_R AT%I128.6 :BOOL; (*照明控制箱NJ-1AL1-2-运行状态*)"},"LLCB01A02_R             AT%I128.6      :BOOL; (*照明控制箱NJ-1AL1-2-运行状态*)",null,"L11\\L11LCB01A02_R","照明控制箱NJ-1AL1-2-运行状态",11030]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"照明控制箱NJ-1AL1-2-自动状态",{"$nulls":16},"NJ-1AL1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL1-2","01A02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"LCB01A02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LLCB01A02_A AT%I128.7 :BOOL; (*照明控制箱NJ-1AL1-2-自动状态*)"},"LLCB01A02_A             AT%I128.7      :BOOL; (*照明控制箱NJ-1AL1-2-自动状态*)",null,"L11\\L11LCB01A02_A","照明控制箱NJ-1AL1-2-自动状态",11031]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-1AL1-3-运行状态",{"$nulls":16},"NJ-1AL1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL1-3","01A03","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"LCB01A03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B26*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LLCB01A03_R AT%I129.0 :BOOL; (*照明控制箱NJ-1AL1-3-运行状态*)"},"LLCB01A03_R             AT%I129.0      :BOOL; (*照明控制箱NJ-1AL1-3-运行状态*)",null,"L11\\L11LCB01A03_R","照明控制箱NJ-1AL1-3-运行状态",11032]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-1AL1-3-自动状态",{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-1AL1-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL1-3","01A03","自动状态",{"$f":"AH34&\"-\"&AK34","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"LCB01A03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B26*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LLCB01A03_A AT%I129.1 :BOOL; (*照明控制箱NJ-1AL1-3-自动状态*)"},"LLCB01A03_A             AT%I129.1      :BOOL; (*照明控制箱NJ-1AL1-3-自动状态*)",null,"L11\\L11LCB01A03_A","照明控制箱NJ-1AL1-3-自动状态",11033]
[{"$nulls":5},11,null,21,22,"照明控制箱NJ-1AL1-4-运行状态",{"$nulls":16},"NJ-1AL1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL1-4","01A04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"LCB01A04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B26*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LLCB01A04_R AT%I129.2 :BOOL; (*照明控制箱NJ-1AL1-4-运行状态*)"},"LLCB01A04_R             AT%I129.2      :BOOL; (*照明控制箱NJ-1AL1-4-运行状态*)",null,"L11\\L11LCB01A04_R","照明控制箱NJ-1AL1-4-运行状态",11034]
[{"$nulls":5},12,null,23,24,"照明控制箱NJ-1AL1-4-自动状态",{"$nulls":16},"NJ-1AL1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL1-4","01A04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"LCB01A04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B26*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LLCB01A04_A AT%I129.3 :BOOL; (*照明控制箱NJ-1AL1-4-自动状态*)"},"LLCB01A04_A             AT%I129.3      :BOOL; (*照明控制箱NJ-1AL1-4-自动状态*)",null,"L11\\L11LCB01A04_A","照明控制箱NJ-1AL1-4-自动状态",11035]
[{"$nulls":5},13,null,25,26,"风机盘管NJ-1AP(KT)1-运行状态",{"$nulls":16},"NJ-1AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)1","01A01","运行状态","风机盘管-运行状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B26*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LFCU01A01_R AT%I129.4 :BOOL; (*风机盘管NJ-1AP(KT)1-运行状态*)"},"LFCU01A01_R             AT%I129.4      :BOOL; (*风机盘管NJ-1AP(KT)1-运行状态*)",null,"L11\\L11FCU01A01_R","风机盘管NJ-1AP(KT)1-运行状态",11036]
[{"$nulls":5},14,null,27,28,"风机盘管NJ-1AP(KT)1-自动状态",{"$nulls":16},"NJ-1AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)1","01A01","自动状态","风机盘管-自动状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B26*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LFCU01A01_A AT%I129.5 :BOOL; (*风机盘管NJ-1AP(KT)1-自动状态*)"},"LFCU01A01_A             AT%I129.5      :BOOL; (*风机盘管NJ-1AP(KT)1-自动状态*)",null,"L11\\L11FCU01A01_A","风机盘管NJ-1AP(KT)1-自动状态",11037]
[{"$nulls":5},15,null,29,30,"风机盘管NJ-1AP(KT)1-电磁阀开启状态",{"$nulls":16},"NJ-1AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)1","01A01","电磁阀开启状态","风机盘管-电磁阀开启状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_EVR"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B26*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LFCU01A01_EVR AT%I129.6 :BOOL; (*风机盘管NJ-1AP(KT)1-电磁阀开启状态*)"},"LFCU01A01_EVR           AT%I129.6      :BOOL; (*风机盘管NJ-1AP(KT)1-电磁阀开启状态*)",null,"L11\\L11FCU01A01_EVR","风机盘管NJ-1AP(KT)1-电磁阀开启状态",11038]
[".",{"$nulls":4},16,null,31,32,"风机盘管NJ-1AP(KT)1-电磁阀自动状态",{"$nulls":16},"NJ-1AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)1","01A01","电磁阀自动状态","风机盘管-电磁阀自动状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_EVA"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B26*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LFCU01A01_EVA AT%I129.7 :BOOL; (*风机盘管NJ-1AP(KT)1-电磁阀自动状态*)"},"LFCU01A01_EVA           AT%I129.7      :BOOL; (*风机盘管NJ-1AP(KT)1-电磁阀自动状态*)",null,"L11\\L11FCU01A01_EVA","风机盘管NJ-1AP(KT)1-电磁阀自动状态",11039]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B46&\"地址: \"&B43&\" *)\"","v":"(* IOM 1601D地址: 9 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH42&AA42&\"-\"&AK42","v":"空调机组NJ-1AP(KT)1-1-启停控制"},{"$nulls":16},{"$f":"IF(AI42=\"\",\"\",AI42)","v":"NJ-1AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-1","01A01","启停控制",{"$f":"AH42&\"-\"&AK42","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%Q\"&B43*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":"LAHU01A01_C AT%Q144.0 :BOOL; (*空调机组NJ-1AP(KT)1-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42))),SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))))),\" \")","v":"LAHU01A01_C             AT%Q144.0      :BOOL; (*空调机组NJ-1AP(KT)1-1-启停控制*)"},null,{"$f":"AM42","v":"AHU01A01_C"},{"$f":"J42","v":"空调机组NJ-1AP(KT)1-1-启停控制"},{"$f":"($B43*16*8+F42-1)","v":1152}]
[null,9,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","空调机组NJ-1AP(KT)1-2-启停控制",{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-1AP(KT)1-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-2","01A02","启停控制",{"$f":"AH43&\"-\"&AK43","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"AHU01A02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%Q\"&B43*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LAHU01A02_C AT%Q144.1 :BOOL; (*空调机组NJ-1AP(KT)1-2-启停控制*)"},"LAHU01A02_C             AT%Q144.1      :BOOL; (*空调机组NJ-1AP(KT)1-2-启停控制*)",null,"AHU01A02_C",{"$f":"J43","v":"空调机组NJ-1AP(KT)1-2-启停控制"},{"$f":"AS42+1","v":1153}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","空调机组NJ-1AP(KT)1-3-启停控制",{"$nulls":16},"NJ-1AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-3","01A03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"AHU01A03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%Q\"&B43*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LAHU01A03_C AT%Q144.2 :BOOL; (*空调机组NJ-1AP(KT)1-3-启停控制*)"},"LAHU01A03_C             AT%Q144.2      :BOOL; (*空调机组NJ-1AP(KT)1-3-启停控制*)",null,"AHU01A03_C","空调机组NJ-1AP(KT)1-3-启停控制",{"$f":"AS43+1","v":1154}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","空调机组NJ-1AP(KT)1-4-启停控制",{"$nulls":16},"NJ-1AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-4","01A04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"AHU01A04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%Q\"&B43*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LAHU01A04_C AT%Q144.3 :BOOL; (*空调机组NJ-1AP(KT)1-4-启停控制*)"},"LAHU01A04_C             AT%Q144.3      :BOOL; (*空调机组NJ-1AP(KT)1-4-启停控制*)",null,"AHU01A04_C","空调机组NJ-1AP(KT)1-4-启停控制",1155]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-1AP(KT)1-5-启停控制",{"$nulls":16},"NJ-1AP(KT)1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-5","01A05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"AHU01A05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%Q\"&B43*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LAHU01A05_C AT%Q144.4 :BOOL; (*空调机组NJ-1AP(KT)1-5-启停控制*)"},"LAHU01A05_C             AT%Q144.4      :BOOL; (*空调机组NJ-1AP(KT)1-5-启停控制*)",null,"AHU01A05_C","空调机组NJ-1AP(KT)1-5-启停控制",1156]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","照明控制箱NJ-1AL1-1-启停控制",{"$nulls":16},"NJ-1AL1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL1-1","01A01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"LCB01A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%Q\"&B43*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LLCB01A01_C AT%Q144.5 :BOOL; (*照明控制箱NJ-1AL1-1-启停控制*)"},"LLCB01A01_C             AT%Q144.5      :BOOL; (*照明控制箱NJ-1AL1-1-启停控制*)",null,"LCB01A01_C","照明控制箱NJ-1AL1-1-启停控制",1157]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","照明控制箱NJ-1AL1-2-启停控制",{"$nulls":16},"NJ-1AL1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL1-2","01A02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"LCB01A02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%Q\"&B43*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LLCB01A02_C AT%Q144.6 :BOOL; (*照明控制箱NJ-1AL1-2-启停控制*)"},"LLCB01A02_C             AT%Q144.6      :BOOL; (*照明控制箱NJ-1AL1-2-启停控制*)",null,"LCB01A02_C","照明控制箱NJ-1AL1-2-启停控制",1158]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-1AL1-3-启停控制",{"$nulls":16},"NJ-1AL1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL1-3","01A03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"LCB01A03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%Q\"&B43*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LLCB01A03_C AT%Q144.7 :BOOL; (*照明控制箱NJ-1AL1-3-启停控制*)"},"LLCB01A03_C             AT%Q144.7      :BOOL; (*照明控制箱NJ-1AL1-3-启停控制*)",null,"LCB01A03_C","照明控制箱NJ-1AL1-3-启停控制",1159]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-1AL1-4-启停控制",{"$nulls":16},"NJ-1AL1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL1-4","01A04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"LCB01A04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%Q\"&B43*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LLCB01A04_C AT%Q145.0 :BOOL; (*照明控制箱NJ-1AL1-4-启停控制*)"},"LLCB01A04_C             AT%Q145.0      :BOOL; (*照明控制箱NJ-1AL1-4-启停控制*)",null,"LCB01A04_C","照明控制箱NJ-1AL1-4-启停控制",1160]
[{"$nulls":5},10,null,"10+","10-","风机盘管NJ-1AP(KT)1-启停控制",{"$nulls":16},{"$f":"IF(AI51=\"\",\"\",AI51)","v":"NJ-1AP(KT)1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)1","01A01","启停控制",{"$f":"AH51&\"-\"&AK51","v":"风机盘管-启停控制"},{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%Q\"&B43*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LFCU01A01_C AT%Q145.1 :BOOL; (*风机盘管NJ-1AP(KT)1-启停控制*)"},"LFCU01A01_C             AT%Q145.1      :BOOL; (*风机盘管NJ-1AP(KT)1-启停控制*)",null,"FCU01A01_C",{"$f":"J51","v":"风机盘管NJ-1AP(KT)1-启停控制"},1161]
[{"$nulls":5},11,null,"11+","11-","风机盘管NJ-1AP(KT)1-电磁阀开关控制",{"$nulls":16},"NJ-1AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)1","01A01","电磁阀开关控制","风机盘管-电磁阀开关控制",{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_EVC"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%Q\"&B43*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LFCU01A01_EVC AT%Q145.2 :BOOL; (*风机盘管NJ-1AP(KT)1-电磁阀开关控制*)"},"LFCU01A01_EVC           AT%Q145.2      :BOOL; (*风机盘管NJ-1AP(KT)1-电磁阀开关控制*)",null,"FCU01A01_EVC","风机盘管NJ-1AP(KT)1-电磁阀开关控制",1162]
[{"$nulls":5},12,null,"12+","12-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%Q\"&B43*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1163]
[{"$nulls":5},13,null,"13+","13-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%Q\"&B43*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1164]
[{"$nulls":5},14,null,"14+","14-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%Q\"&B43*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1165]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%Q\"&B43*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1166]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%Q\"&B43*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1167]
[null,{"$f":"B63","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B63&\"地址: \"&B60&\" *)\"","v":"(* IOM 0801U地址: 10 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH59&AA59&\"-\"&AK59","v":"空调机组NJ-1AP(KT)1-1-回风温度"},{"$nulls":16},{"$f":"IF(AI59=\"\",\"\",AI59)","v":"NJ-1AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-1","01A01","回风温度",{"$f":"AH59&\"-\"&AK59","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH59,List!$B$3:$D$445,2,FALSE)&AJ59&\"_\"&VLOOKUP(AK59,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM59&\" \"&\"AT%I\"&B60*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J59&\"*)\",\" \")","v":"LAHU01A01_RT AT%I160.0 :INT ; (*空调机组NJ-1AP(KT)1-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59))),SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))))),\" \")","v":"LAHU01A01_RT            AT%I160.0      :INT ; (*空调机组NJ-1AP(KT)1-1-回风温度*)"},null,{"$f":"AM59","v":"AHU01A01_RT"},{"$f":"J59","v":"空调机组NJ-1AP(KT)1-1-回风温度"},{"$f":"30000+($B60*8+F59-1)","v":30080}]
[null,10,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-1AP(KT)1-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-1AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-1","01A01","水阀反馈",{"$f":"AH60&\"-\"&AK60","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%I\"&B60*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LAHU01A01_WVB AT%I162.0 :INT ; (*空调机组NJ-1AP(KT)1-1-水阀反馈*)"},"LAHU01A01_WVB           AT%I162.0      :INT ; (*空调机组NJ-1AP(KT)1-1-水阀反馈*)",null,"AHU01A01_WVB",{"$f":"J60","v":"空调机组NJ-1AP(KT)1-1-水阀反馈"},{"$f":"AS59+1","v":30081}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-1AP(KT)1-2-回风温度",{"$nulls":16},"NJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-2","01A02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"AHU01A02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%I\"&B60*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LAHU01A02_RT AT%I164.0 :INT ; (*空调机组NJ-1AP(KT)1-2-回风温度*)"},"LAHU01A02_RT            AT%I164.0      :INT ; (*空调机组NJ-1AP(KT)1-2-回风温度*)",null,"AHU01A02_RT","空调机组NJ-1AP(KT)1-2-回风温度",{"$f":"AS60+1","v":30082}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-1AP(KT)1-2-水阀反馈",{"$nulls":16},"NJ-1AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-2","01A02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"AHU01A02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B60*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LAHU01A02_WVB AT%I166.0 :INT ; (*空调机组NJ-1AP(KT)1-2-水阀反馈*)"},"LAHU01A02_WVB           AT%I166.0      :INT ; (*空调机组NJ-1AP(KT)1-2-水阀反馈*)",null,"AHU01A02_WVB","空调机组NJ-1AP(KT)1-2-水阀反馈",30083]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-1AP(KT)1-3-回风温度",{"$nulls":16},"NJ-1AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-3","01A03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"AHU01A03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B60*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LAHU01A03_RT AT%I168.0 :INT ; (*空调机组NJ-1AP(KT)1-3-回风温度*)"},"LAHU01A03_RT            AT%I168.0      :INT ; (*空调机组NJ-1AP(KT)1-3-回风温度*)",null,"AHU01A03_RT","空调机组NJ-1AP(KT)1-3-回风温度",30084]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-1AP(KT)1-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI64=\"\",\"\",AI64)","v":"NJ-1AP(KT)1-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-3","01A03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"AHU01A03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B60*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LAHU01A03_WVB AT%I170.0 :INT ; (*空调机组NJ-1AP(KT)1-3-水阀反馈*)"},"LAHU01A03_WVB           AT%I170.0      :INT ; (*空调机组NJ-1AP(KT)1-3-水阀反馈*)",null,"AHU01A03_WVB",{"$f":"J64","v":"空调机组NJ-1AP(KT)1-3-水阀反馈"},30085]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-1AP(KT)1-4-回风温度",{"$nulls":16},"NJ-1AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-4","01A04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":"AHU01A04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B60*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":"LAHU01A04_RT AT%I172.0 :INT ; (*空调机组NJ-1AP(KT)1-4-回风温度*)"},"LAHU01A04_RT            AT%I172.0      :INT ; (*空调机组NJ-1AP(KT)1-4-回风温度*)",null,"AHU01A04_RT","空调机组NJ-1AP(KT)1-4-回风温度",30086]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-1AP(KT)1-4-水阀反馈",{"$nulls":16},"NJ-1AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-4","01A04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":"AHU01A04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B60*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":"LAHU01A04_WVB AT%I174.0 :INT ; (*空调机组NJ-1AP(KT)1-4-水阀反馈*)"},"LAHU01A04_WVB           AT%I174.0      :INT ; (*空调机组NJ-1AP(KT)1-4-水阀反馈*)",null,"AHU01A04_WVB","空调机组NJ-1AP(KT)1-4-水阀反馈",30087]
[null,{"$f":"B72","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B72&\"地址: \"&B69&\" *)\"","v":"(* IOM 0401U地址: 11 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH68&AA68&\"-\"&AK68","v":"空调机组NJ-1AP(KT)1-5-回风温度"},{"$nulls":16},{"$f":"IF(AI68=\"\",\"\",AI68)","v":"NJ-1AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-5","01A05","回风温度",{"$f":"AH68&\"-\"&AK68","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"AHU01A05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%I\"&B69*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LAHU01A05_RT AT%I176.0 :INT ; (*空调机组NJ-1AP(KT)1-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68))),SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))))),\" \")","v":"LAHU01A05_RT            AT%I176.0      :INT ; (*空调机组NJ-1AP(KT)1-5-回风温度*)"},null,"AHU01A05_RT",{"$f":"J68","v":"空调机组NJ-1AP(KT)1-5-回风温度"},{"$f":"30000+($B69*8+F68-1)","v":30088}]
[null,11,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-1AP(KT)1-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-1AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-5","01A05","水阀反馈",{"$f":"AH69&\"-\"&AK69","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU01A05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%I\"&B69*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU01A05_WVB AT%I178.0 :INT ; (*空调机组NJ-1AP(KT)1-5-水阀反馈*)"},"LAHU01A05_WVB           AT%I178.0      :INT ; (*空调机组NJ-1AP(KT)1-5-水阀反馈*)",null,"AHU01A05_WVB",{"$f":"J69","v":"空调机组NJ-1AP(KT)1-5-水阀反馈"},{"$f":"AS68+1","v":30089}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":0},3,null,3,"0V","风机盘管NJ-1AP(KT)1-温度状态",{"$nulls":16},"NJ-1AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)1","01A01","温度状态","风机盘管-温度状态",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"FCU01A01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%I\"&B69*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LFCU01A01_T AT%I180.0 :INT ; (*风机盘管NJ-1AP(KT)1-温度状态*)"},"LFCU01A01_T             AT%I180.0      :INT ; (*风机盘管NJ-1AP(KT)1-温度状态*)",null,"FCU01A01_T","风机盘管NJ-1AP(KT)1-温度状态",{"$f":"AS69+1","v":30090}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":1},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%I\"&B69*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30091]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":0}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B81","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B81&\"地址: \"&B78&\" *)\"","v":"(* IOM 0401A地址: 12 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH77&AA77&\"-\"&AK77","v":"空调机组NJ-1AP(KT)1-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-1AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-1","01A01","水阀控制",{"$f":"AH77&\"-\"&AK77","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"AHU01A01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%Q\"&B78*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LAHU01A01_WVC AT%Q192.0 :INT ; (*空调机组NJ-1AP(KT)1-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77))),SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))))),\" \")","v":"LAHU01A01_WVC           AT%Q192.0      :INT ; (*空调机组NJ-1AP(KT)1-1-水阀控制*)"},null,{"$f":"AM77","v":"AHU01A01_WVC"},{"$f":"J77","v":"空调机组NJ-1AP(KT)1-1-水阀控制"},{"$f":"40000+($B78*8+F77-1)","v":40096}]
[null,12,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH78&AA78&\"-\"&AK78","v":"空调机组NJ-1AP(KT)1-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-1AP(KT)1-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-2","01A02","水阀控制",{"$f":"AH78&\"-\"&AK78","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU01A02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B78*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU01A02_WVC AT%Q194.0 :INT ; (*空调机组NJ-1AP(KT)1-2-水阀控制*)"},"LAHU01A02_WVC           AT%Q194.0      :INT ; (*空调机组NJ-1AP(KT)1-2-水阀控制*)",null,"AHU01A02_WVC",{"$f":"J78","v":"空调机组NJ-1AP(KT)1-2-水阀控制"},{"$f":"AS77+1","v":40097}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH79&AA79&\"-\"&AK79","v":"空调机组NJ-1AP(KT)1-3-水阀控制"},{"$nulls":16},"NJ-1AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-3","01A03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU01A03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B78*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU01A03_WVC AT%Q196.0 :INT ; (*空调机组NJ-1AP(KT)1-3-水阀控制*)"},"LAHU01A03_WVC           AT%Q196.0      :INT ; (*空调机组NJ-1AP(KT)1-3-水阀控制*)",null,"AHU01A03_WVC","空调机组NJ-1AP(KT)1-3-水阀控制",{"$f":"AS78+1","v":40098}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH80&AA80&\"-\"&AK80","v":"空调机组NJ-1AP(KT)1-4-水阀控制"},{"$nulls":16},"NJ-1AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-4","01A04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU01A04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B78*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU01A04_WVC AT%Q198.0 :INT ; (*空调机组NJ-1AP(KT)1-4-水阀控制*)"},"LAHU01A04_WVC           AT%Q198.0      :INT ; (*空调机组NJ-1AP(KT)1-4-水阀控制*)",null,"AHU01A04_WVC","空调机组NJ-1AP(KT)1-4-水阀控制",40099]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B90","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B90&\"地址: \"&B87&\" *)\"","v":"(* IOM 0401A地址: 13 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH86&AA86&\"-\"&AK86","v":"空调机组NJ-1AP(KT)1-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-1AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)1-5","01A05","水阀控制",{"$f":"AH86&\"-\"&AK86","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"AHU01A05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%Q\"&B87*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LAHU01A05_WVC AT%Q208.0 :INT ; (*空调机组NJ-1AP(KT)1-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86))),SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))))),\" \")","v":"LAHU01A05_WVC           AT%Q208.0      :INT ; (*空调机组NJ-1AP(KT)1-5-水阀控制*)"},null,{"$f":"AM86","v":"AHU01A05_WVC"},{"$f":"J86","v":"空调机组NJ-1AP(KT)1-5-水阀控制"},{"$f":"40000+($B87*8+F86-1)","v":40104}]
[null,13,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH87&AA87&\"-\"&AK87","v":"-"},{"$nulls":16},{"$f":"IF(AI87=\"\",\"\",AI87)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},{"$f":"AH87&\"-\"&AK87","v":"-"},{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%Q\"&B87*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J87","v":"-"},{"$f":"AS86+1","v":40105}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH88&AA88&\"-\"&AK88","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%Q\"&B87*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS87+1","v":40106}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH89&AA89&\"-\"&AK89","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%Q\"&B87*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40107]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L202","index":7,"n_rows":60,"n_cols":45,"rows_kept":60,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[6,1,6,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[41,5,41,6],[41,9,41,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[4,1,5,1],[12,1,23,1],[29,1,32,1],[38,1,41,1],[47,1,50,1],[56,1,59,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[16,2,23,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L12",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"EXC-1000"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B13&\"地址: \"&B10&\" *)\"","v":"(* IOM 1601R地址: 0 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH9&AA9&\"-\"&AK9","v":"空调机组NJ-2AP(KT)2-1-运行状态"},{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-2AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-1","02B01","运行状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU02B01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B10*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU02B01_R AT%I0.0 :BOOL; (*空调机组NJ-2AP(KT)2-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9))),SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))))),\" \")","v":"LAHU02B01_R             AT%I0.0        :BOOL; (*空调机组NJ-2AP(KT)2-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM9","v":"L12\\L12AHU02B01_R"},{"$f":"J9","v":"空调机组NJ-2AP(KT)2-1-运行状态"},{"$f":"10000+($B10*16*8+F9-1)","v":10000}]
[null,0,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-2AP(KT)2-1-故障状态",{"$nulls":16},{"$f":"IF(AI10=\"\",\"\",AI10)","v":"NJ-2AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-1","02B01","故障状态",{"$f":"AH10&\"-\"&AK10","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU02B01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B10*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU02B01_F AT%I0.1 :BOOL; (*空调机组NJ-2AP(KT)2-1-故障状态*)"},"LAHU02B01_F             AT%I0.1        :BOOL; (*空调机组NJ-2AP(KT)2-1-故障状态*)",null,"L12\\L12AHU02B01_F",{"$f":"J10","v":"空调机组NJ-2AP(KT)2-1-故障状态"},{"$f":"AS9+1","v":10001}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-2AP(KT)2-1-自动状态",{"$nulls":16},"NJ-2AP(KT)2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-1","02B01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU02B01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B10*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU02B01_A AT%I0.2 :BOOL; (*空调机组NJ-2AP(KT)2-1-自动状态*)"},"LAHU02B01_A             AT%I0.2        :BOOL; (*空调机组NJ-2AP(KT)2-1-自动状态*)",null,"L12\\L12AHU02B01_A","空调机组NJ-2AP(KT)2-1-自动状态",{"$f":"AS10+1","v":10002}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-2AP(KT)2-1-风机压差",{"$nulls":16},"NJ-2AP(KT)2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-1","02B01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU02B01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B10*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU02B01_FPS AT%I0.3 :BOOL; (*空调机组NJ-2AP(KT)2-1-风机压差*)"},"LAHU02B01_FPS           AT%I0.3        :BOOL; (*空调机组NJ-2AP(KT)2-1-风机压差*)",null,"L12\\L12AHU02B01_FPS","空调机组NJ-2AP(KT)2-1-风机压差",10003]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-2AP(KT)2-1-运行状态",{"$nulls":16},"NJ-2AP(KT)2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-1","02B02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU02B02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B10*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU02B02_R AT%I0.4 :BOOL; (*空调机组NJ-2AP(KT)2-1-运行状态*)"},"LAHU02B02_R             AT%I0.4        :BOOL; (*空调机组NJ-2AP(KT)2-1-运行状态*)",null,"L12\\L12AHU02B02_R","空调机组NJ-2AP(KT)2-1-运行状态",10004]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-2AP(KT)2-2-故障状态",{"$nulls":16},"NJ-2AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-2","02B02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU02B02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B10*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU02B02_F AT%I0.5 :BOOL; (*空调机组NJ-2AP(KT)2-2-故障状态*)"},"LAHU02B02_F             AT%I0.5        :BOOL; (*空调机组NJ-2AP(KT)2-2-故障状态*)",null,"L12\\L12AHU02B02_F","空调机组NJ-2AP(KT)2-2-故障状态",10005]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-2AP(KT)2-2-自动状态",{"$nulls":16},"NJ-2AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-2","02B02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU02B02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B10*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU02B02_A AT%I0.6 :BOOL; (*空调机组NJ-2AP(KT)2-2-自动状态*)"},"LAHU02B02_A             AT%I0.6        :BOOL; (*空调机组NJ-2AP(KT)2-2-自动状态*)",null,"L12\\L12AHU02B02_A","空调机组NJ-2AP(KT)2-2-自动状态",10006]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-2AP(KT)2-2-风机压差",{"$nulls":16},"NJ-2AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-2","02B02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU02B02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B10*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU02B02_FPS AT%I0.7 :BOOL; (*空调机组NJ-2AP(KT)2-2-风机压差*)"},"LAHU02B02_FPS           AT%I0.7        :BOOL; (*空调机组NJ-2AP(KT)2-2-风机压差*)",null,"L12\\L12AHU02B02_FPS","空调机组NJ-2AP(KT)2-2-风机压差",10007]
[{"$nulls":5},9,null,17,18,"空调机组NJ-2AP(KT)2-2-运行状态",{"$nulls":16},"NJ-2AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-2","02B03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU02B03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B10*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU02B03_R AT%I1.0 :BOOL; (*空调机组NJ-2AP(KT)2-2-运行状态*)"},"LAHU02B03_R             AT%I1.0        :BOOL; (*空调机组NJ-2AP(KT)2-2-运行状态*)",null,"L12\\L12AHU02B03_R","空调机组NJ-2AP(KT)2-2-运行状态",10008]
[{"$nulls":5},10,null,19,20,"空调机组NJ-2AP(KT)2-3-故障状态",{"$nulls":16},{"$f":"IF(AI18=\"\",\"\",AI18)","v":"NJ-2AP(KT)2-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-3","02B03","故障状态",{"$f":"AH18&\"-\"&AK18","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU02B03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B10*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU02B03_F AT%I1.1 :BOOL; (*空调机组NJ-2AP(KT)2-3-故障状态*)"},"LAHU02B03_F             AT%I1.1        :BOOL; (*空调机组NJ-2AP(KT)2-3-故障状态*)",null,"L12\\L12AHU02B03_F","空调机组NJ-2AP(KT)2-3-故障状态",10009]
[{"$nulls":5},11,null,21,22,"空调机组NJ-2AP(KT)2-3-自动状态",{"$nulls":16},"NJ-2AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-3","02B03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU02B03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B10*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU02B03_A AT%I1.2 :BOOL; (*空调机组NJ-2AP(KT)2-3-自动状态*)"},"LAHU02B03_A             AT%I1.2        :BOOL; (*空调机组NJ-2AP(KT)2-3-自动状态*)",null,"L12\\L12AHU02B03_A","空调机组NJ-2AP(KT)2-3-自动状态",10010]
[{"$nulls":5},12,null,23,24,"空调机组NJ-2AP(KT)2-3-风机压差",{"$nulls":16},"NJ-2AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-3","02B03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU02B03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B10*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU02B03_FPS AT%I1.3 :BOOL; (*空调机组NJ-2AP(KT)2-3-风机压差*)"},"LAHU02B03_FPS           AT%I1.3        :BOOL; (*空调机组NJ-2AP(KT)2-3-风机压差*)",null,"L12\\L12AHU02B03_FPS","空调机组NJ-2AP(KT)2-3-风机压差",10011]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-2AL2-1-运行状态",{"$nulls":16},"NJ-2AL2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL2-1","02B01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"LCB02B01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B10*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LLCB02B01_R AT%I1.4 :BOOL; (*照明控制箱NJ-2AL2-1-运行状态*)"},"LLCB02B01_R             AT%I1.4        :BOOL; (*照明控制箱NJ-2AL2-1-运行状态*)",null,"L12\\L12LCB02B01_R","照明控制箱NJ-2AL2-1-运行状态",10012]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-2AL2-1-自动状态",{"$nulls":16},"NJ-2AL2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL2-1","02B01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"LCB02B01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B10*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LLCB02B01_A AT%I1.5 :BOOL; (*照明控制箱NJ-2AL2-1-自动状态*)"},"LLCB02B01_A             AT%I1.5        :BOOL; (*照明控制箱NJ-2AL2-1-自动状态*)",null,"L12\\L12LCB02B01_A","照明控制箱NJ-2AL2-1-自动状态",10013]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-2AL2-2-运行状态",{"$nulls":16},"NJ-2AL2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL2-2","02B02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"LCB02B02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B10*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LLCB02B02_R AT%I1.6 :BOOL; (*照明控制箱NJ-2AL2-2-运行状态*)"},"LLCB02B02_R             AT%I1.6        :BOOL; (*照明控制箱NJ-2AL2-2-运行状态*)",null,"L12\\L12LCB02B02_R","照明控制箱NJ-2AL2-2-运行状态",10014]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-2AL2-2-自动状态",{"$nulls":16},"NJ-2AL2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL2-2","02B02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH24,List!$B$3:$D$445,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,List!$K$2:$M$447,2,FALSE)","v":"LCB02B02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%I\"&B10*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":"LLCB02B02_A AT%I1.7 :BOOL; (*照明控制箱NJ-2AL2-2-自动状态*)"},"LLCB02B02_A             AT%I1.7        :BOOL; (*照明控制箱NJ-2AL2-2-自动状态*)",null,"L12\\L12LCB02B02_A","照明控制箱NJ-2AL2-2-自动状态",10015]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 0801R 地址: 1 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},1,null,1,"C",{"$f":"AH26&AA26&\"-\"&AK26","v":"照明控制箱NJ-2AL2-3-运行状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-2AL2-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL2-3","02B03","运行状态",{"$f":"AH26&\"-\"&AK26","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"LCB02B03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LLCB02B03_R AT%I16.0 :BOOL; (*照明控制箱NJ-2AL2-3-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LLCB02B03_R             AT%I16.0       :BOOL; (*照明控制箱NJ-2AL2-3-运行状态*)"},null,{"$f":"AM26","v":"LCB02B03_R"},{"$f":"J26","v":"照明控制箱NJ-2AL2-3-运行状态"},{"$f":"10000+($B27*16*8+F26-1)","v":10128}]
[null,1,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,2,"C",{"$f":"AH27&AA27&\"-\"&AK27","v":"照明控制箱NJ-2AL2-3-自动状态"},{"$nulls":16},{"$f":"IF(AI27=\"\",\"\",AI27)","v":"NJ-2AL2-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL2-3","02B03","自动状态",{"$f":"AH27&\"-\"&AK27","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"LCB02B03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LLCB02B03_A AT%I16.1 :BOOL; (*照明控制箱NJ-2AL2-3-自动状态*)"},"LLCB02B03_A             AT%I16.1       :BOOL; (*照明控制箱NJ-2AL2-3-自动状态*)",null,{"$f":"AM27","v":"LCB02B03_A"},{"$f":"J27","v":"照明控制箱NJ-2AL2-3-自动状态"},{"$f":"AS26+1","v":10129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,3,"C",{"$f":"AH28&AA28&\"-\"&AK28","v":"照明控制箱NJ-2AL2-4-运行状态"},{"$nulls":16},"NJ-2AL2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL2-4","02B04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"LCB02B04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LLCB02B04_R AT%I16.2 :BOOL; (*照明控制箱NJ-2AL2-4-运行状态*)"},"LLCB02B04_R             AT%I16.2       :BOOL; (*照明控制箱NJ-2AL2-4-运行状态*)",null,"LCB02B04_R","照明控制箱NJ-2AL2-4-运行状态",{"$f":"AS27+1","v":10130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,4,"C",{"$f":"AH29&AA29&\"-\"&AK29","v":"照明控制箱NJ-2AL2-4-自动状态"},{"$nulls":16},"NJ-2AL2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL2-4","02B04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"LCB02B04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LLCB02B04_A AT%I16.3 :BOOL; (*照明控制箱NJ-2AL2-4-自动状态*)"},"LLCB02B04_A             AT%I16.3       :BOOL; (*照明控制箱NJ-2AL2-4-自动状态*)",null,"LCB02B04_A","照明控制箱NJ-2AL2-4-自动状态",10131]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},5,null,5,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B27*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B27*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B27*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10134]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B27*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10135]
[null,"IOM 0801D",{"$nulls":38},{"$f":"\"(* \"&B39&\"地址: \"&B36&\" *)\"","v":"(* IOM 0801D地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH35&AA35&\"-\"&AK35","v":"空调机组NJ-2AP(KT)2-1-启停控制"},{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-2AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-1","02B01","启停控制",{"$f":"AH35&\"-\"&AK35","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU02B01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%Q\"&B36*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU02B01_C AT%Q32.0 :BOOL; (*空调机组NJ-2AP(KT)2-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35))),SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35)))))),\" \")","v":"LAHU02B01_C             AT%Q32.0       :BOOL; (*空调机组NJ-2AP(KT)2-1-启停控制*)"},null,{"$f":"AM35","v":"AHU02B01_C"},{"$f":"J35","v":"空调机组NJ-2AP(KT)2-1-启停控制"},{"$f":"($B36*16*8+F35-1)","v":256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-2AP(KT)2-2-启停控制",{"$nulls":16},{"$f":"IF(AI36=\"\",\"\",AI36)","v":"NJ-2AP(KT)2-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-2","02B02","启停控制",{"$f":"AH36&\"-\"&AK36","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU02B02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%Q\"&B36*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU02B02_C AT%Q32.1 :BOOL; (*空调机组NJ-2AP(KT)2-2-启停控制*)"},"LAHU02B02_C             AT%Q32.1       :BOOL; (*空调机组NJ-2AP(KT)2-2-启停控制*)",null,"AHU02B02_C",{"$f":"J36","v":"空调机组NJ-2AP(KT)2-2-启停控制"},{"$f":"AS35+1","v":257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","空调机组NJ-2AP(KT)2-3-启停控制",{"$nulls":16},"NJ-2AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-3","02B03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"AHU02B03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%Q\"&B36*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LAHU02B03_C AT%Q32.2 :BOOL; (*空调机组NJ-2AP(KT)2-3-启停控制*)"},"LAHU02B03_C             AT%Q32.2       :BOOL; (*空调机组NJ-2AP(KT)2-3-启停控制*)",null,"AHU02B03_C","空调机组NJ-2AP(KT)2-3-启停控制",{"$f":"AS36+1","v":258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","照明控制箱NJ-2AL2-1-启停控制",{"$nulls":16},"NJ-2AL2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL2-1","02B01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB02B01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%Q\"&B36*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB02B01_C AT%Q32.3 :BOOL; (*照明控制箱NJ-2AL2-1-启停控制*)"},"LLCB02B01_C             AT%Q32.3       :BOOL; (*照明控制箱NJ-2AL2-1-启停控制*)",null,"LCB02B01_C","照明控制箱NJ-2AL2-1-启停控制",259]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","照明控制箱NJ-2AL2-2-启停控制",{"$nulls":16},"NJ-2AL2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL2-2","02B02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB02B02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%Q\"&B36*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB02B02_C AT%Q32.4 :BOOL; (*照明控制箱NJ-2AL2-2-启停控制*)"},"LLCB02B02_C             AT%Q32.4       :BOOL; (*照明控制箱NJ-2AL2-2-启停控制*)",null,"LCB02B02_C","照明控制箱NJ-2AL2-2-启停控制",260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","照明控制箱NJ-2AL2-3-启停控制",{"$nulls":16},"NJ-2AL2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL2-3","02B03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"LCB02B03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%Q\"&B36*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LLCB02B03_C AT%Q32.5 :BOOL; (*照明控制箱NJ-2AL2-3-启停控制*)"},"LLCB02B03_C             AT%Q32.5       :BOOL; (*照明控制箱NJ-2AL2-3-启停控制*)",null,"LCB02B03_C","照明控制箱NJ-2AL2-3-启停控制",261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","照明控制箱NJ-2AL2-4-启停控制",{"$nulls":16},"NJ-2AL2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL2-4","02B04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":"LCB02B04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%Q\"&B36*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":"LLCB02B04_C AT%Q32.6 :BOOL; (*照明控制箱NJ-2AL2-4-启停控制*)"},"LLCB02B04_C             AT%Q32.6       :BOOL; (*照明控制箱NJ-2AL2-4-启停控制*)",null,"LCB02B04_C","照明控制箱NJ-2AL2-4-启停控制",262]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%Q\"&B36*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",263]
[null,{"$f":"B48","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B48&\"地址: \"&B45&\" *)\"","v":"(* IOM 0801U地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH44&AA44&\"-\"&AK44","v":"空调机组NJ-2AP(KT)2-1-回风温度"},{"$nulls":16},{"$f":"IF(AI44=\"\",\"\",AI44)","v":"NJ-2AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-1","02B01","回风温度",{"$f":"AH44&\"-\"&AK44","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"AHU02B01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B45*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LAHU02B01_RT AT%I48.0 :INT ; (*空调机组NJ-2AP(KT)2-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN44,SEARCH(\"AT%\",AN44),,REPT(\" \",25-SEARCH(\"AT%\",AN44))),SEARCH(\":\",REPLACE(AN44,SEARCH(\"AT%\",AN44),,REPT(\" \",25-SEARCH(\"AT%\",AN44)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN44,SEARCH(\"AT%\",AN44),,REPT(\" \",25-SEARCH(\"AT%\",AN44)))))),\" \")","v":"LAHU02B01_RT            AT%I48.0       :INT ; (*空调机组NJ-2AP(KT)2-1-回风温度*)"},null,{"$f":"AM44","v":"AHU02B01_RT"},{"$f":"J44","v":"空调机组NJ-2AP(KT)2-1-回风温度"},{"$f":"30000+($B45*8+F44-1)","v":30024}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-2AP(KT)2-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI45=\"\",\"\",AI45)","v":"NJ-2AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-1","02B01","水阀反馈",{"$f":"AH45&\"-\"&AK45","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"AHU02B01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B45*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LAHU02B01_WVB AT%I50.0 :INT ; (*空调机组NJ-2AP(KT)2-1-水阀反馈*)"},"LAHU02B01_WVB           AT%I50.0       :INT ; (*空调机组NJ-2AP(KT)2-1-水阀反馈*)",null,"AHU02B01_WVB",{"$f":"J45","v":"空调机组NJ-2AP(KT)2-1-水阀反馈"},{"$f":"AS44+1","v":30025}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-2AP(KT)2-2-回风温度",{"$nulls":16},"NJ-2AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-2","02B02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"AHU02B02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B45*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LAHU02B02_RT AT%I52.0 :INT ; (*空调机组NJ-2AP(KT)2-2-回风温度*)"},"LAHU02B02_RT            AT%I52.0       :INT ; (*空调机组NJ-2AP(KT)2-2-回风温度*)",null,"AHU02B02_RT","空调机组NJ-2AP(KT)2-2-回风温度",{"$f":"AS45+1","v":30026}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-2AP(KT)2-2-水阀反馈",{"$nulls":16},"NJ-2AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-2","02B02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"AHU02B02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B45*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LAHU02B02_WVB AT%I54.0 :INT ; (*空调机组NJ-2AP(KT)2-2-水阀反馈*)"},"LAHU02B02_WVB           AT%I54.0       :INT ; (*空调机组NJ-2AP(KT)2-2-水阀反馈*)",null,"AHU02B02_WVB","空调机组NJ-2AP(KT)2-2-水阀反馈",30027]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-2AP(KT)2-3-回风温度",{"$nulls":16},"NJ-2AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-3","02B03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"AHU02B03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B45*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LAHU02B03_RT AT%I56.0 :INT ; (*空调机组NJ-2AP(KT)2-3-回风温度*)"},"LAHU02B03_RT            AT%I56.0       :INT ; (*空调机组NJ-2AP(KT)2-3-回风温度*)",null,"AHU02B03_RT","空调机组NJ-2AP(KT)2-3-回风温度",30028]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B47=20,1,IF(B47=50,10,IF(B47=125,11,IF(B47=250,100,IF(B47=500,101,IF(B47=800,110,IF(B47=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B47=20,1,IF(B47=50,10,IF(B47=125,11,IF(B47=250,100,IF(B47=500,101,IF(B47=800,110,IF(B47=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-2AP(KT)2-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI49=\"\",\"\",AI49)","v":"NJ-2AP(KT)2-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-3","02B03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"AHU02B03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B45*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LAHU02B03_WVB AT%I58.0 :INT ; (*空调机组NJ-2AP(KT)2-3-水阀反馈*)"},"LAHU02B03_WVB           AT%I58.0       :INT ; (*空调机组NJ-2AP(KT)2-3-水阀反馈*)",null,"AHU02B03_WVB",{"$f":"J49","v":"空调机组NJ-2AP(KT)2-3-水阀反馈"},30029]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B47=20,1,IF(B47=50,10,IF(B47=125,11,IF(B47=250,100,IF(B47=500,101,IF(B47=800,110,IF(B47=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B47=20,1,IF(B47=50,10,IF(B47=125,11,IF(B47=250,100,IF(B47=500,101,IF(B47=800,110,IF(B47=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B45*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30030]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B47=20,1,IF(B47=50,10,IF(B47=125,11,IF(B47=250,100,IF(B47=500,101,IF(B47=800,110,IF(B47=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B47=20,1,IF(B47=50,10,IF(B47=125,11,IF(B47=250,100,IF(B47=500,101,IF(B47=800,110,IF(B47=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B45*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30031]
[null,{"$f":"B57","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B57&\"地址: \"&B54&\" *)\"","v":"(* IOM 0401A地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH53&AA53&\"-\"&AK53","v":"空调机组NJ-2AP(KT)2-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI53=\"\",\"\",AI53)","v":"NJ-2AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-1","02B01","水阀控制",{"$f":"AH53&\"-\"&AK53","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"AHU02B01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%Q\"&B54*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LAHU02B01_WVC AT%Q64.0 :INT ; (*空调机组NJ-2AP(KT)2-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN53,SEARCH(\"AT%\",AN53),,REPT(\" \",25-SEARCH(\"AT%\",AN53))),SEARCH(\":\",REPLACE(AN53,SEARCH(\"AT%\",AN53),,REPT(\" \",25-SEARCH(\"AT%\",AN53)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN53,SEARCH(\"AT%\",AN53),,REPT(\" \",25-SEARCH(\"AT%\",AN53)))))),\" \")","v":"LAHU02B01_WVC           AT%Q64.0       :INT ; (*空调机组NJ-2AP(KT)2-1-水阀控制*)"},null,{"$f":"AM53","v":"AHU02B01_WVC"},{"$f":"J53","v":"空调机组NJ-2AP(KT)2-1-水阀控制"},{"$f":"40000+($B54*8+F53-1)","v":40032}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH54&AA54&\"-\"&AK54","v":"空调机组NJ-2AP(KT)2-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI54=\"\",\"\",AI54)","v":"NJ-2AP(KT)2-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-2","02B02","水阀控制",{"$f":"AH54&\"-\"&AK54","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"AHU02B02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%Q\"&B54*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LAHU02B02_WVC AT%Q66.0 :INT ; (*空调机组NJ-2AP(KT)2-2-水阀控制*)"},"LAHU02B02_WVC           AT%Q66.0       :INT ; (*空调机组NJ-2AP(KT)2-2-水阀控制*)",null,"AHU02B02_WVC",{"$f":"J54","v":"空调机组NJ-2AP(KT)2-2-水阀控制"},{"$f":"AS53+1","v":40033}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH55&AA55&\"-\"&AK55","v":"空调机组NJ-2AP(KT)2-3-水阀控制"},{"$nulls":16},"NJ-2AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)2-3","02B03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"AHU02B03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%Q\"&B54*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LAHU02B03_WVC AT%Q68.0 :INT ; (*空调机组NJ-2AP(KT)2-3-水阀控制*)"},"LAHU02B03_WVC           AT%Q68.0       :INT ; (*空调机组NJ-2AP(KT)2-3-水阀控制*)",null,"AHU02B03_WVC","空调机组NJ-2AP(KT)2-3-水阀控制",{"$f":"AS54+1","v":40034}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH56&AA56&\"-\"&AK56","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%Q\"&B54*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40035]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B56=20,1,IF(B56=50,10,IF(B56=125,11,IF(B56=250,100,IF(B56=500,101,IF(B56=800,110,IF(B56=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B56=20,1,IF(B56=50,10,IF(B56=125,11,IF(B56=250,100,IF(B56=500,101,IF(B56=800,110,IF(B56=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B56=20,1,IF(B56=50,10,IF(B56=125,11,IF(B56=250,100,IF(B56=500,101,IF(B56=800,110,IF(B56=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B56=20,1,IF(B56=50,10,IF(B56=125,11,IF(B56=250,100,IF(B56=500,101,IF(B56=800,110,IF(B56=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B56=20,1,IF(B56=50,10,IF(B56=125,11,IF(B56=250,100,IF(B56=500,101,IF(B56=800,110,IF(B56=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B56=20,1,IF(B56=50,10,IF(B56=125,11,IF(B56=250,100,IF(B56=500,101,IF(B56=800,110,IF(B56=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L102","index":8,"n_rows":59,"n_cols":45,"rows_kept":59,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[58,5,58,6],[58,9,58,25],[4,1,5,1],[11,1,22,1],[28,1,31,1],[37,1,40,1],[46,1,49,1],[55,1,58,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[15,2,22,4],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L12",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH8&AA8&\"-\"&AK8","v":"空调机组NJ-1AP(KT)2-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-1AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-1","01B01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH8,List!$B$3:$D$445,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,List!$K$2:$M$447,2,FALSE)","v":"AHU01B01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LAHU01B01_R AT%I80.0 :BOOL; (*空调机组NJ-1AP(KT)2-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LAHU01B01_R             AT%I80.0       :BOOL; (*空调机组NJ-1AP(KT)2-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L12\\L12AHU01B01_R"},{"$f":"J8","v":"空调机组NJ-1AP(KT)2-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":10640}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-1AP(KT)2-1-故障状态",{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-1AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-1","01B01","故障状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU01B01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU01B01_F AT%I80.1 :BOOL; (*空调机组NJ-1AP(KT)2-1-故障状态*)"},"LAHU01B01_F             AT%I80.1       :BOOL; (*空调机组NJ-1AP(KT)2-1-故障状态*)",null,"L12\\L12AHU01B01_F",{"$f":"J9","v":"空调机组NJ-1AP(KT)2-1-故障状态"},{"$f":"AS8+1","v":10641}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},3,null,5,6,"空调机组NJ-1AP(KT)2-1-自动状态",{"$nulls":16},"NJ-1AP(KT)2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-1","01B01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU01B01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU01B01_A AT%I80.2 :BOOL; (*空调机组NJ-1AP(KT)2-1-自动状态*)"},"LAHU01B01_A             AT%I80.2       :BOOL; (*空调机组NJ-1AP(KT)2-1-自动状态*)",null,"L12\\L12AHU01B01_A","空调机组NJ-1AP(KT)2-1-自动状态",{"$f":"AS9+1","v":10642}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-1AP(KT)2-1-风机压差",{"$nulls":16},"NJ-1AP(KT)2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-1","01B01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU01B01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU01B01_FPS AT%I80.3 :BOOL; (*空调机组NJ-1AP(KT)2-1-风机压差*)"},"LAHU01B01_FPS           AT%I80.3       :BOOL; (*空调机组NJ-1AP(KT)2-1-风机压差*)",null,"L12\\L12AHU01B01_FPS","空调机组NJ-1AP(KT)2-1-风机压差",10643]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-1AP(KT)2-1-运行状态",{"$nulls":16},"NJ-1AP(KT)2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-1","01B02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU01B02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU01B02_R AT%I80.4 :BOOL; (*空调机组NJ-1AP(KT)2-1-运行状态*)"},"LAHU01B02_R             AT%I80.4       :BOOL; (*空调机组NJ-1AP(KT)2-1-运行状态*)",null,"L12\\L12AHU01B02_R","空调机组NJ-1AP(KT)2-1-运行状态",10644]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-1AP(KT)2-2-故障状态",{"$nulls":16},"NJ-1AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-2","01B02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU01B02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU01B02_F AT%I80.5 :BOOL; (*空调机组NJ-1AP(KT)2-2-故障状态*)"},"LAHU01B02_F             AT%I80.5       :BOOL; (*空调机组NJ-1AP(KT)2-2-故障状态*)",null,"L12\\L12AHU01B02_F","空调机组NJ-1AP(KT)2-2-故障状态",10645]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-1AP(KT)2-2-自动状态",{"$nulls":16},"NJ-1AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-2","01B02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU01B02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU01B02_A AT%I80.6 :BOOL; (*空调机组NJ-1AP(KT)2-2-自动状态*)"},"LAHU01B02_A             AT%I80.6       :BOOL; (*空调机组NJ-1AP(KT)2-2-自动状态*)",null,"L12\\L12AHU01B02_A","空调机组NJ-1AP(KT)2-2-自动状态",10646]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-1AP(KT)2-2-风机压差",{"$nulls":16},"NJ-1AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-2","01B02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU01B02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU01B02_FPS AT%I80.7 :BOOL; (*空调机组NJ-1AP(KT)2-2-风机压差*)"},"LAHU01B02_FPS           AT%I80.7       :BOOL; (*空调机组NJ-1AP(KT)2-2-风机压差*)",null,"L12\\L12AHU01B02_FPS","空调机组NJ-1AP(KT)2-2-风机压差",10647]
[{"$nulls":5},9,null,17,18,"空调机组NJ-1AP(KT)2-2-运行状态",{"$nulls":16},"NJ-1AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-2","01B03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU01B03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU01B03_R AT%I81.0 :BOOL; (*空调机组NJ-1AP(KT)2-2-运行状态*)"},"LAHU01B03_R             AT%I81.0       :BOOL; (*空调机组NJ-1AP(KT)2-2-运行状态*)",null,"L12\\L12AHU01B03_R","空调机组NJ-1AP(KT)2-2-运行状态",10648]
[{"$nulls":5},10,null,19,20,"空调机组NJ-1AP(KT)2-3-故障状态",{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-1AP(KT)2-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-3","01B03","故障状态",{"$f":"AH17&\"-\"&AK17","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU01B03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU01B03_F AT%I81.1 :BOOL; (*空调机组NJ-1AP(KT)2-3-故障状态*)"},"LAHU01B03_F             AT%I81.1       :BOOL; (*空调机组NJ-1AP(KT)2-3-故障状态*)",null,"L12\\L12AHU01B03_F","空调机组NJ-1AP(KT)2-3-故障状态",10649]
[{"$nulls":5},11,null,21,22,"空调机组NJ-1AP(KT)2-3-自动状态",{"$nulls":16},"NJ-1AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-3","01B03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU01B03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU01B03_A AT%I81.2 :BOOL; (*空调机组NJ-1AP(KT)2-3-自动状态*)"},"LAHU01B03_A             AT%I81.2       :BOOL; (*空调机组NJ-1AP(KT)2-3-自动状态*)",null,"L12\\L12AHU01B03_A","空调机组NJ-1AP(KT)2-3-自动状态",10650]
[{"$nulls":5},12,null,23,24,"空调机组NJ-1AP(KT)2-3-风机压差",{"$nulls":16},"NJ-1AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-3","01B03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU01B03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU01B03_FPS AT%I81.3 :BOOL; (*空调机组NJ-1AP(KT)2-3-风机压差*)"},"LAHU01B03_FPS           AT%I81.3       :BOOL; (*空调机组NJ-1AP(KT)2-3-风机压差*)",null,"L12\\L12AHU01B03_FPS","空调机组NJ-1AP(KT)2-3-风机压差",10651]
[{"$nulls":5},13,null,25,26,"空调机组NJ-1AP(KT)2-4-运行状态",{"$nulls":16},"NJ-1AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-4","01B04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU01B04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU01B04_R AT%I81.4 :BOOL; (*空调机组NJ-1AP(KT)2-4-运行状态*)"},"LAHU01B04_R             AT%I81.4       :BOOL; (*空调机组NJ-1AP(KT)2-4-运行状态*)",null,"L12\\L12AHU01B04_R","空调机组NJ-1AP(KT)2-4-运行状态",10652]
[{"$nulls":5},14,null,27,28,"空调机组NJ-1AP(KT)2-4-故障状态",{"$nulls":16},"NJ-1AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-4","01B04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU01B04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU01B04_F AT%I81.5 :BOOL; (*空调机组NJ-1AP(KT)2-4-故障状态*)"},"LAHU01B04_F             AT%I81.5       :BOOL; (*空调机组NJ-1AP(KT)2-4-故障状态*)",null,"L12\\L12AHU01B04_F","空调机组NJ-1AP(KT)2-4-故障状态",10653]
[{"$nulls":5},15,null,29,30,"空调机组NJ-1AP(KT)2-4-自动状态",{"$nulls":16},"NJ-1AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-4","01B04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU01B04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU01B04_A AT%I81.6 :BOOL; (*空调机组NJ-1AP(KT)2-4-自动状态*)"},"LAHU01B04_A             AT%I81.6       :BOOL; (*空调机组NJ-1AP(KT)2-4-自动状态*)",null,"L12\\L12AHU01B04_A","空调机组NJ-1AP(KT)2-4-自动状态",10654]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-1AP(KT)2-4-风机压差",{"$nulls":16},"NJ-1AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-4","01B04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU01B04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU01B04_FPS AT%I81.7 :BOOL; (*空调机组NJ-1AP(KT)2-4-风机压差*)"},"LAHU01B04_FPS           AT%I81.7       :BOOL; (*空调机组NJ-1AP(KT)2-4-风机压差*)",null,"L12\\L12AHU01B04_FPS","空调机组NJ-1AP(KT)2-4-风机压差",10655]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 0801R 地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH25&AA25&\"-\"&AK25","v":"照明控制箱NJ-1AL2-1-运行状态"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-1AL2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL2-1","01B01","运行状态",{"$f":"AH25&\"-\"&AK25","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"LCB01B01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LLCB01B01_R AT%I96.0 :BOOL; (*照明控制箱NJ-1AL2-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LLCB01B01_R             AT%I96.0       :BOOL; (*照明控制箱NJ-1AL2-1-运行状态*)"},null,{"$f":"AM25","v":"LCB01B01_R"},{"$f":"J25","v":"照明控制箱NJ-1AL2-1-运行状态"},{"$f":"10000+($B26*16*8+F25-1)","v":10768}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},2,null,2,"C",{"$f":"AH26&AA26&\"-\"&AK26","v":"照明控制箱NJ-1AL2-1-自动状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-1AL2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL2-1","01B01","自动状态",{"$f":"AH26&\"-\"&AK26","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"LCB01B01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LLCB01B01_A AT%I96.1 :BOOL; (*照明控制箱NJ-1AL2-1-自动状态*)"},"LLCB01B01_A             AT%I96.1       :BOOL; (*照明控制箱NJ-1AL2-1-自动状态*)",null,{"$f":"AM26","v":"LCB01B01_A"},{"$f":"J26","v":"照明控制箱NJ-1AL2-1-自动状态"},{"$f":"AS25+1","v":10769}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},3,null,3,"C",{"$f":"AH27&AA27&\"-\"&AK27","v":"照明控制箱NJ-1AL2-2-运行状态"},{"$nulls":16},"NJ-1AL2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL2-2","01B02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"LCB01B02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LLCB01B02_R AT%I96.2 :BOOL; (*照明控制箱NJ-1AL2-2-运行状态*)"},"LLCB01B02_R             AT%I96.2       :BOOL; (*照明控制箱NJ-1AL2-2-运行状态*)",null,"LCB01B02_R","照明控制箱NJ-1AL2-2-运行状态",{"$f":"AS26+1","v":10770}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":0},4,null,4,"C",{"$f":"AH28&AA28&\"-\"&AK28","v":"照明控制箱NJ-1AL2-2-自动状态"},{"$nulls":16},"NJ-1AL2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL2-2","01B02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"LCB01B02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LLCB01B02_A AT%I96.3 :BOOL; (*照明控制箱NJ-1AL2-2-自动状态*)"},"LLCB01B02_A             AT%I96.3       :BOOL; (*照明控制箱NJ-1AL2-2-自动状态*)",null,"LCB01B02_A","照明控制箱NJ-1AL2-2-自动状态",10771]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,5,"C","照明控制箱NJ-1AL2-3-运行状态",{"$nulls":16},"NJ-1AL2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL2-3","01B03","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"LCB01B03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LLCB01B03_R AT%I96.4 :BOOL; (*照明控制箱NJ-1AL2-3-运行状态*)"},"LLCB01B03_R             AT%I96.4       :BOOL; (*照明控制箱NJ-1AL2-3-运行状态*)",null,"LCB01B03_R","照明控制箱NJ-1AL2-3-运行状态",10772]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","照明控制箱NJ-1AL2-3-自动状态",{"$nulls":16},"NJ-1AL2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL2-3","01B03","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"LCB01B03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LLCB01B03_A AT%I96.5 :BOOL; (*照明控制箱NJ-1AL2-3-自动状态*)"},"LLCB01B03_A             AT%I96.5       :BOOL; (*照明控制箱NJ-1AL2-3-自动状态*)",null,"LCB01B03_A","照明控制箱NJ-1AL2-3-自动状态",10773]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","照明控制箱NJ-1AL2-4-运行状态",{"$nulls":16},"NJ-1AL2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL2-4","01B04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"LCB01B04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LLCB01B04_R AT%I96.6 :BOOL; (*照明控制箱NJ-1AL2-4-运行状态*)"},"LLCB01B04_R             AT%I96.6       :BOOL; (*照明控制箱NJ-1AL2-4-运行状态*)",null,"LCB01B04_R","照明控制箱NJ-1AL2-4-运行状态",10774]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","照明控制箱NJ-1AL2-4-自动状态",{"$nulls":16},"NJ-1AL2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL2-4","01B04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"LCB01B04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LLCB01B04_A AT%I96.7 :BOOL; (*照明控制箱NJ-1AL2-4-自动状态*)"},"LLCB01B04_A             AT%I96.7       :BOOL; (*照明控制箱NJ-1AL2-4-自动状态*)",null,"LCB01B04_A","照明控制箱NJ-1AL2-4-自动状态",10775]
[null,"IOM 0801D",{"$nulls":38},{"$f":"\"(* \"&B38&\"地址: \"&B35&\" *)\"","v":"(* IOM 0801D地址: 7 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH34&AA34&\"-\"&AK34","v":"空调机组NJ-1AP(KT)2-1-启停控制"},{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-1AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-1","01B01","启停控制",{"$f":"AH34&\"-\"&AK34","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU01B01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%Q\"&B35*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU01B01_C AT%Q112.0 :BOOL; (*空调机组NJ-1AP(KT)2-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34))),SEARCH(\":\",REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34)))))),\" \")","v":"LAHU01B01_C             AT%Q112.0      :BOOL; (*空调机组NJ-1AP(KT)2-1-启停控制*)"},null,{"$f":"AM34","v":"AHU01B01_C"},{"$f":"J34","v":"空调机组NJ-1AP(KT)2-1-启停控制"},{"$f":"($B35*16*8+F34-1)","v":896}]
[null,7,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-1AP(KT)2-2-启停控制",{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-1AP(KT)2-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-2","01B02","启停控制",{"$f":"AH35&\"-\"&AK35","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU01B02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%Q\"&B35*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU01B02_C AT%Q112.1 :BOOL; (*空调机组NJ-1AP(KT)2-2-启停控制*)"},"LAHU01B02_C             AT%Q112.1      :BOOL; (*空调机组NJ-1AP(KT)2-2-启停控制*)",null,"AHU01B02_C",{"$f":"J35","v":"空调机组NJ-1AP(KT)2-2-启停控制"},{"$f":"AS34+1","v":897}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-1AP(KT)2-3-启停控制",{"$nulls":16},"NJ-1AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-3","01B03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU01B03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%Q\"&B35*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU01B03_C AT%Q112.2 :BOOL; (*空调机组NJ-1AP(KT)2-3-启停控制*)"},"LAHU01B03_C             AT%Q112.2      :BOOL; (*空调机组NJ-1AP(KT)2-3-启停控制*)",null,"AHU01B03_C","空调机组NJ-1AP(KT)2-3-启停控制",{"$f":"AS35+1","v":898}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","空调机组NJ-1AP(KT)2-4-启停控制",{"$nulls":16},"NJ-1AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-4","01B04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"AHU01B04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%Q\"&B35*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LAHU01B04_C AT%Q112.3 :BOOL; (*空调机组NJ-1AP(KT)2-4-启停控制*)"},"LAHU01B04_C             AT%Q112.3      :BOOL; (*空调机组NJ-1AP(KT)2-4-启停控制*)",null,"AHU01B04_C","空调机组NJ-1AP(KT)2-4-启停控制",899]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","照明控制箱NJ-1AL2-1-启停控制",{"$nulls":16},"NJ-1AL2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL2-1","01B01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB01B01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%Q\"&B35*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB01B01_C AT%Q112.4 :BOOL; (*照明控制箱NJ-1AL2-1-启停控制*)"},"LLCB01B01_C             AT%Q112.4      :BOOL; (*照明控制箱NJ-1AL2-1-启停控制*)",null,"LCB01B01_C","照明控制箱NJ-1AL2-1-启停控制",900]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","照明控制箱NJ-1AL2-2-启停控制",{"$nulls":16},"NJ-1AL2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-1AL2-2","01B02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB01B02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%Q\"&B35*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB01B02_C AT%Q112.5 :BOOL; (*照明控制箱NJ-1AL2-2-启停控制*)"},"LLCB01B02_C             AT%Q112.5      :BOOL; (*照明控制箱NJ-1AL2-2-启停控制*)",null,"LCB01B02_C","照明控制箱NJ-1AL2-2-启停控制",901]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","照明控制箱NJ-1AL2-3-启停控制",{"$nulls":16},"NJ-1AL2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL2-3","01B03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"LCB01B03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%Q\"&B35*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LLCB01B03_C AT%Q112.6 :BOOL; (*照明控制箱NJ-1AL2-3-启停控制*)"},"LLCB01B03_C             AT%Q112.6      :BOOL; (*照明控制箱NJ-1AL2-3-启停控制*)",null,"LCB01B03_C","照明控制箱NJ-1AL2-3-启停控制",902]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-1AL2-4-启停控制",{"$nulls":16},"NJ-1AL2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL2-4","01B04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":"LCB01B04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%Q\"&B35*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":"LLCB01B04_C AT%Q112.7 :BOOL; (*照明控制箱NJ-1AL2-4-启停控制*)"},"LLCB01B04_C             AT%Q112.7      :BOOL; (*照明控制箱NJ-1AL2-4-启停控制*)",null,"LCB01B04_C","照明控制箱NJ-1AL2-4-启停控制",903]
[null,{"$f":"B47","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 0801U地址: 8 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH43&AA43&\"-\"&AK43","v":"空调机组NJ-1AP(KT)2-1-回风温度"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-1AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-1","01B01","回风温度",{"$f":"AH43&\"-\"&AK43","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"AHU01B01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B44*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LAHU01B01_RT AT%I128.0 :INT ; (*空调机组NJ-1AP(KT)2-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LAHU01B01_RT            AT%I128.0      :INT ; (*空调机组NJ-1AP(KT)2-1-回风温度*)"},null,{"$f":"AM43","v":"AHU01B01_RT"},{"$f":"J43","v":"空调机组NJ-1AP(KT)2-1-回风温度"},{"$f":"30000+($B44*8+F43-1)","v":30064}]
[null,8,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-1AP(KT)2-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI44=\"\",\"\",AI44)","v":"NJ-1AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-1","01B01","水阀反馈",{"$f":"AH44&\"-\"&AK44","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"AHU01B01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B44*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LAHU01B01_WVB AT%I130.0 :INT ; (*空调机组NJ-1AP(KT)2-1-水阀反馈*)"},"LAHU01B01_WVB           AT%I130.0      :INT ; (*空调机组NJ-1AP(KT)2-1-水阀反馈*)",null,"AHU01B01_WVB",{"$f":"J44","v":"空调机组NJ-1AP(KT)2-1-水阀反馈"},{"$f":"AS43+1","v":30065}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-1AP(KT)2-2-回风温度",{"$nulls":16},"NJ-1AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-2","01B02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"AHU01B02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B44*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LAHU01B02_RT AT%I132.0 :INT ; (*空调机组NJ-1AP(KT)2-2-回风温度*)"},"LAHU01B02_RT            AT%I132.0      :INT ; (*空调机组NJ-1AP(KT)2-2-回风温度*)",null,"AHU01B02_RT","空调机组NJ-1AP(KT)2-2-回风温度",{"$f":"AS44+1","v":30066}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-1AP(KT)2-2-水阀反馈",{"$nulls":16},"NJ-1AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-2","01B02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"AHU01B02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B44*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LAHU01B02_WVB AT%I134.0 :INT ; (*空调机组NJ-1AP(KT)2-2-水阀反馈*)"},"LAHU01B02_WVB           AT%I134.0      :INT ; (*空调机组NJ-1AP(KT)2-2-水阀反馈*)",null,"AHU01B02_WVB","空调机组NJ-1AP(KT)2-2-水阀反馈",30067]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-1AP(KT)2-3-回风温度",{"$nulls":16},"NJ-1AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-3","01B03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"AHU01B03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B44*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LAHU01B03_RT AT%I136.0 :INT ; (*空调机组NJ-1AP(KT)2-3-回风温度*)"},"LAHU01B03_RT            AT%I136.0      :INT ; (*空调机组NJ-1AP(KT)2-3-回风温度*)",null,"AHU01B03_RT","空调机组NJ-1AP(KT)2-3-回风温度",30068]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-1AP(KT)2-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI48=\"\",\"\",AI48)","v":"NJ-1AP(KT)2-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-3","01B03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"AHU01B03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B44*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LAHU01B03_WVB AT%I138.0 :INT ; (*空调机组NJ-1AP(KT)2-3-水阀反馈*)"},"LAHU01B03_WVB           AT%I138.0      :INT ; (*空调机组NJ-1AP(KT)2-3-水阀反馈*)",null,"AHU01B03_WVB",{"$f":"J48","v":"空调机组NJ-1AP(KT)2-3-水阀反馈"},30069]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-1AP(KT)2-4-回风温度",{"$nulls":16},"NJ-1AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-4","01B04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"AHU01B04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B44*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LAHU01B04_RT AT%I140.0 :INT ; (*空调机组NJ-1AP(KT)2-4-回风温度*)"},"LAHU01B04_RT            AT%I140.0      :INT ; (*空调机组NJ-1AP(KT)2-4-回风温度*)",null,"AHU01B04_RT","空调机组NJ-1AP(KT)2-4-回风温度",30070]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-1AP(KT)2-4-水阀反馈",{"$nulls":16},"NJ-1AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-4","01B04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"AHU01B04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B44*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LAHU01B04_WVB AT%I142.0 :INT ; (*空调机组NJ-1AP(KT)2-4-水阀反馈*)"},"LAHU01B04_WVB           AT%I142.0      :INT ; (*空调机组NJ-1AP(KT)2-4-水阀反馈*)",null,"AHU01B04_WVB","空调机组NJ-1AP(KT)2-4-水阀反馈",30071]
[null,{"$f":"B56","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B56&\"地址: \"&B53&\" *)\"","v":"(* IOM 0401A地址: 9 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH52&AA52&\"-\"&AK52","v":"空调机组NJ-1AP(KT)2-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-1AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-1","01B01","水阀控制",{"$f":"AH52&\"-\"&AK52","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"AHU01B01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%Q\"&B53*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LAHU01B01_WVC AT%Q144.0 :INT ; (*空调机组NJ-1AP(KT)2-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN52,SEARCH(\"AT%\",AN52),,REPT(\" \",25-SEARCH(\"AT%\",AN52))),SEARCH(\":\",REPLACE(AN52,SEARCH(\"AT%\",AN52),,REPT(\" \",25-SEARCH(\"AT%\",AN52)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN52,SEARCH(\"AT%\",AN52),,REPT(\" \",25-SEARCH(\"AT%\",AN52)))))),\" \")","v":"LAHU01B01_WVC           AT%Q144.0      :INT ; (*空调机组NJ-1AP(KT)2-1-水阀控制*)"},null,{"$f":"AM52","v":"AHU01B01_WVC"},{"$f":"J52","v":"空调机组NJ-1AP(KT)2-1-水阀控制"},{"$f":"40000+($B53*8+F52-1)","v":40072}]
[null,9,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH53&AA53&\"-\"&AK53","v":"空调机组NJ-1AP(KT)2-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI53=\"\",\"\",AI53)","v":"NJ-1AP(KT)2-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-2","01B02","水阀控制",{"$f":"AH53&\"-\"&AK53","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"AHU01B02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%Q\"&B53*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LAHU01B02_WVC AT%Q146.0 :INT ; (*空调机组NJ-1AP(KT)2-2-水阀控制*)"},"LAHU01B02_WVC           AT%Q146.0      :INT ; (*空调机组NJ-1AP(KT)2-2-水阀控制*)",null,"AHU01B02_WVC",{"$f":"J53","v":"空调机组NJ-1AP(KT)2-2-水阀控制"},{"$f":"AS52+1","v":40073}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH54&AA54&\"-\"&AK54","v":"空调机组NJ-1AP(KT)2-3-水阀控制"},{"$nulls":16},"NJ-1AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-3","01B03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"AHU01B03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%Q\"&B53*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LAHU01B03_WVC AT%Q148.0 :INT ; (*空调机组NJ-1AP(KT)2-3-水阀控制*)"},"LAHU01B03_WVC           AT%Q148.0      :INT ; (*空调机组NJ-1AP(KT)2-3-水阀控制*)",null,"AHU01B03_WVC","空调机组NJ-1AP(KT)2-3-水阀控制",{"$f":"AS53+1","v":40074}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH55&AA55&\"-\"&AK55","v":"空调机组NJ-1AP(KT)2-4-水阀控制"},{"$nulls":16},"NJ-1AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)2-4","01B04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"AHU01B04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%Q\"&B53*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LAHU01B04_WVC AT%Q150.0 :INT ; (*空调机组NJ-1AP(KT)2-4-水阀控制*)"},"LAHU01B04_WVC           AT%Q150.0      :INT ; (*空调机组NJ-1AP(KT)2-4-水阀控制*)",null,"AHU01B04_WVC","空调机组NJ-1AP(KT)2-4-水阀控制",40075]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L203","index":9,"n_rows":60,"n_cols":45,"rows_kept":60,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[6,1,6,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[41,5,41,6],[41,9,41,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[4,1,5,1],[12,1,23,1],[29,1,32,1],[38,1,41,1],[47,1,50,1],[56,1,59,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[16,2,23,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L13",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"EXC-1000"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B13&\"地址: \"&B10&\" *)\"","v":"(* IOM 1601R地址: 0 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH9&AA9&\"-\"&AK9","v":"空调机组NJ-2AP(KT)3-1-运行状态"},{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-2AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-1","02C01","运行状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU02C01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B10*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU02C01_R AT%I0.0 :BOOL; (*空调机组NJ-2AP(KT)3-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9))),SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))))),\" \")","v":"LAHU02C01_R             AT%I0.0        :BOOL; (*空调机组NJ-2AP(KT)3-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM9","v":"L13\\L13AHU02C01_R"},{"$f":"J9","v":"空调机组NJ-2AP(KT)3-1-运行状态"},{"$f":"10000+($B10*16*8+F9-1)","v":10000}]
[null,0,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-2AP(KT)3-1-故障状态",{"$nulls":16},{"$f":"IF(AI10=\"\",\"\",AI10)","v":"NJ-2AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-1","02C01","故障状态",{"$f":"AH10&\"-\"&AK10","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU02C01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B10*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU02C01_F AT%I0.1 :BOOL; (*空调机组NJ-2AP(KT)3-1-故障状态*)"},"LAHU02C01_F             AT%I0.1        :BOOL; (*空调机组NJ-2AP(KT)3-1-故障状态*)",null,"L13\\L13AHU02C01_F",{"$f":"J10","v":"空调机组NJ-2AP(KT)3-1-故障状态"},{"$f":"AS9+1","v":10001}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-2AP(KT)3-1-自动状态",{"$nulls":16},"NJ-2AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-1","02C01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU02C01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B10*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU02C01_A AT%I0.2 :BOOL; (*空调机组NJ-2AP(KT)3-1-自动状态*)"},"LAHU02C01_A             AT%I0.2        :BOOL; (*空调机组NJ-2AP(KT)3-1-自动状态*)",null,"L13\\L13AHU02C01_A","空调机组NJ-2AP(KT)3-1-自动状态",{"$f":"AS10+1","v":10002}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-2AP(KT)3-1-风机压差",{"$nulls":16},"NJ-2AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-1","02C01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU02C01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B10*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU02C01_FPS AT%I0.3 :BOOL; (*空调机组NJ-2AP(KT)3-1-风机压差*)"},"LAHU02C01_FPS           AT%I0.3        :BOOL; (*空调机组NJ-2AP(KT)3-1-风机压差*)",null,"L13\\L13AHU02C01_FPS","空调机组NJ-2AP(KT)3-1-风机压差",10003]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-2AP(KT)3-1-运行状态",{"$nulls":16},"NJ-2AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-1","02C02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU02C02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B10*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU02C02_R AT%I0.4 :BOOL; (*空调机组NJ-2AP(KT)3-1-运行状态*)"},"LAHU02C02_R             AT%I0.4        :BOOL; (*空调机组NJ-2AP(KT)3-1-运行状态*)",null,"L13\\L13AHU02C02_R","空调机组NJ-2AP(KT)3-1-运行状态",10004]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-2AP(KT)3-2-故障状态",{"$nulls":16},"NJ-2AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-2","02C02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU02C02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B10*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU02C02_F AT%I0.5 :BOOL; (*空调机组NJ-2AP(KT)3-2-故障状态*)"},"LAHU02C02_F             AT%I0.5        :BOOL; (*空调机组NJ-2AP(KT)3-2-故障状态*)",null,"L13\\L13AHU02C02_F","空调机组NJ-2AP(KT)3-2-故障状态",10005]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-2AP(KT)3-2-自动状态",{"$nulls":16},"NJ-2AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-2","02C02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU02C02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B10*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU02C02_A AT%I0.6 :BOOL; (*空调机组NJ-2AP(KT)3-2-自动状态*)"},"LAHU02C02_A             AT%I0.6        :BOOL; (*空调机组NJ-2AP(KT)3-2-自动状态*)",null,"L13\\L13AHU02C02_A","空调机组NJ-2AP(KT)3-2-自动状态",10006]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-2AP(KT)3-2-风机压差",{"$nulls":16},"NJ-2AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-2","02C02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU02C02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B10*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU02C02_FPS AT%I0.7 :BOOL; (*空调机组NJ-2AP(KT)3-2-风机压差*)"},"LAHU02C02_FPS           AT%I0.7        :BOOL; (*空调机组NJ-2AP(KT)3-2-风机压差*)",null,"L13\\L13AHU02C02_FPS","空调机组NJ-2AP(KT)3-2-风机压差",10007]
[{"$nulls":5},9,null,17,18,"空调机组NJ-2AP(KT)3-2-运行状态",{"$nulls":16},"NJ-2AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-2","02C03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU02C03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B10*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU02C03_R AT%I1.0 :BOOL; (*空调机组NJ-2AP(KT)3-2-运行状态*)"},"LAHU02C03_R             AT%I1.0        :BOOL; (*空调机组NJ-2AP(KT)3-2-运行状态*)",null,"L13\\L13AHU02C03_R","空调机组NJ-2AP(KT)3-2-运行状态",10008]
[{"$nulls":5},10,null,19,20,"空调机组NJ-2AP(KT)3-3-故障状态",{"$nulls":16},{"$f":"IF(AI18=\"\",\"\",AI18)","v":"NJ-2AP(KT)3-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-3","02C03","故障状态",{"$f":"AH18&\"-\"&AK18","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU02C03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B10*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU02C03_F AT%I1.1 :BOOL; (*空调机组NJ-2AP(KT)3-3-故障状态*)"},"LAHU02C03_F             AT%I1.1        :BOOL; (*空调机组NJ-2AP(KT)3-3-故障状态*)",null,"L13\\L13AHU02C03_F","空调机组NJ-2AP(KT)3-3-故障状态",10009]
[{"$nulls":5},11,null,21,22,"空调机组NJ-2AP(KT)3-3-自动状态",{"$nulls":16},"NJ-2AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-3","02C03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU02C03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B10*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU02C03_A AT%I1.2 :BOOL; (*空调机组NJ-2AP(KT)3-3-自动状态*)"},"LAHU02C03_A             AT%I1.2        :BOOL; (*空调机组NJ-2AP(KT)3-3-自动状态*)",null,"L13\\L13AHU02C03_A","空调机组NJ-2AP(KT)3-3-自动状态",10010]
[{"$nulls":5},12,null,23,24,"空调机组NJ-2AP(KT)3-3-风机压差",{"$nulls":16},"NJ-2AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-3","02C03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU02C03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B10*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU02C03_FPS AT%I1.3 :BOOL; (*空调机组NJ-2AP(KT)3-3-风机压差*)"},"LAHU02C03_FPS           AT%I1.3        :BOOL; (*空调机组NJ-2AP(KT)3-3-风机压差*)",null,"L13\\L13AHU02C03_FPS","空调机组NJ-2AP(KT)3-3-风机压差",10011]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-2AL3-1-运行状态",{"$nulls":16},"NJ-2AL3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL3-1","02C01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"LCB02C01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B10*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LLCB02C01_R AT%I1.4 :BOOL; (*照明控制箱NJ-2AL3-1-运行状态*)"},"LLCB02C01_R             AT%I1.4        :BOOL; (*照明控制箱NJ-2AL3-1-运行状态*)",null,"L13\\L13LCB02C01_R","照明控制箱NJ-2AL3-1-运行状态",10012]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-2AL3-1-自动状态",{"$nulls":16},"NJ-2AL3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL3-1","02C01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"LCB02C01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B10*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LLCB02C01_A AT%I1.5 :BOOL; (*照明控制箱NJ-2AL3-1-自动状态*)"},"LLCB02C01_A             AT%I1.5        :BOOL; (*照明控制箱NJ-2AL3-1-自动状态*)",null,"L13\\L13LCB02C01_A","照明控制箱NJ-2AL3-1-自动状态",10013]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-2AL3-2-运行状态",{"$nulls":16},"NJ-2AL3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL3-2","02C02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"LCB02C02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B10*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LLCB02C02_R AT%I1.6 :BOOL; (*照明控制箱NJ-2AL3-2-运行状态*)"},"LLCB02C02_R             AT%I1.6        :BOOL; (*照明控制箱NJ-2AL3-2-运行状态*)",null,"L13\\L13LCB02C02_R","照明控制箱NJ-2AL3-2-运行状态",10014]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-2AL3-2-自动状态",{"$nulls":16},"NJ-2AL3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL3-2","02C02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH24,List!$B$3:$D$445,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,List!$K$2:$M$447,2,FALSE)","v":"LCB02C02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%I\"&B10*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":"LLCB02C02_A AT%I1.7 :BOOL; (*照明控制箱NJ-2AL3-2-自动状态*)"},"LLCB02C02_A             AT%I1.7        :BOOL; (*照明控制箱NJ-2AL3-2-自动状态*)",null,"L13\\L13LCB02C02_A","照明控制箱NJ-2AL3-2-自动状态",10015]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 0801R 地址: 1 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},1,null,1,"C",{"$f":"AH26&AA26&\"-\"&AK26","v":"照明控制箱NJ-2AL3-3-运行状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-2AL3-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL3-3","02C03","运行状态",{"$f":"AH26&\"-\"&AK26","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"LCB02C03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LLCB02C03_R AT%I16.0 :BOOL; (*照明控制箱NJ-2AL3-3-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LLCB02C03_R             AT%I16.0       :BOOL; (*照明控制箱NJ-2AL3-3-运行状态*)"},null,{"$f":"AM26","v":"LCB02C03_R"},{"$f":"J26","v":"照明控制箱NJ-2AL3-3-运行状态"},{"$f":"10000+($B27*16*8+F26-1)","v":10128}]
[null,1,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,2,"C",{"$f":"AH27&AA27&\"-\"&AK27","v":"照明控制箱NJ-2AL3-3-自动状态"},{"$nulls":16},{"$f":"IF(AI27=\"\",\"\",AI27)","v":"NJ-2AL3-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL3-3","02C03","自动状态",{"$f":"AH27&\"-\"&AK27","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"LCB02C03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LLCB02C03_A AT%I16.1 :BOOL; (*照明控制箱NJ-2AL3-3-自动状态*)"},"LLCB02C03_A             AT%I16.1       :BOOL; (*照明控制箱NJ-2AL3-3-自动状态*)",null,{"$f":"AM27","v":"LCB02C03_A"},{"$f":"J27","v":"照明控制箱NJ-2AL3-3-自动状态"},{"$f":"AS26+1","v":10129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,3,"C",{"$f":"AH28&AA28&\"-\"&AK28","v":"照明控制箱NJ-2AL3-4-运行状态"},{"$nulls":16},"NJ-2AL3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL3-4","02C04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"LCB02C04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LLCB02C04_R AT%I16.2 :BOOL; (*照明控制箱NJ-2AL3-4-运行状态*)"},"LLCB02C04_R             AT%I16.2       :BOOL; (*照明控制箱NJ-2AL3-4-运行状态*)",null,"LCB02C04_R","照明控制箱NJ-2AL3-4-运行状态",{"$f":"AS27+1","v":10130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,4,"C",{"$f":"AH29&AA29&\"-\"&AK29","v":"照明控制箱NJ-2AL3-4-自动状态"},{"$nulls":16},"NJ-2AL3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL3-4","02C04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"LCB02C04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LLCB02C04_A AT%I16.3 :BOOL; (*照明控制箱NJ-2AL3-4-自动状态*)"},"LLCB02C04_A             AT%I16.3       :BOOL; (*照明控制箱NJ-2AL3-4-自动状态*)",null,"LCB02C04_A","照明控制箱NJ-2AL3-4-自动状态",10131]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},5,null,5,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B27*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B27*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B27*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10134]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B27*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10135]
[null,"IOM 0801D",{"$nulls":38},{"$f":"\"(* \"&B39&\"地址: \"&B36&\" *)\"","v":"(* IOM 0801D地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH35&AA35&\"-\"&AK35","v":"空调机组NJ-2AP(KT)3-1-启停控制"},{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-2AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-1","02C01","启停控制",{"$f":"AH35&\"-\"&AK35","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU02C01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%Q\"&B36*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU02C01_C AT%Q32.0 :BOOL; (*空调机组NJ-2AP(KT)3-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35))),SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35)))))),\" \")","v":"LAHU02C01_C             AT%Q32.0       :BOOL; (*空调机组NJ-2AP(KT)3-1-启停控制*)"},null,{"$f":"AM35","v":"AHU02C01_C"},{"$f":"J35","v":"空调机组NJ-2AP(KT)3-1-启停控制"},{"$f":"($B36*16*8+F35-1)","v":256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-2AP(KT)3-2-启停控制",{"$nulls":16},{"$f":"IF(AI36=\"\",\"\",AI36)","v":"NJ-2AP(KT)3-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-2","02C02","启停控制",{"$f":"AH36&\"-\"&AK36","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU02C02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%Q\"&B36*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU02C02_C AT%Q32.1 :BOOL; (*空调机组NJ-2AP(KT)3-2-启停控制*)"},"LAHU02C02_C             AT%Q32.1       :BOOL; (*空调机组NJ-2AP(KT)3-2-启停控制*)",null,"AHU02C02_C",{"$f":"J36","v":"空调机组NJ-2AP(KT)3-2-启停控制"},{"$f":"AS35+1","v":257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","空调机组NJ-2AP(KT)3-3-启停控制",{"$nulls":16},"NJ-2AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-3","02C03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"AHU02C03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%Q\"&B36*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LAHU02C03_C AT%Q32.2 :BOOL; (*空调机组NJ-2AP(KT)3-3-启停控制*)"},"LAHU02C03_C             AT%Q32.2       :BOOL; (*空调机组NJ-2AP(KT)3-3-启停控制*)",null,"AHU02C03_C","空调机组NJ-2AP(KT)3-3-启停控制",{"$f":"AS36+1","v":258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","照明控制箱NJ-2AL3-1-启停控制",{"$nulls":16},"NJ-2AL3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL3-1","02C01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB02C01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%Q\"&B36*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB02C01_C AT%Q32.3 :BOOL; (*照明控制箱NJ-2AL3-1-启停控制*)"},"LLCB02C01_C             AT%Q32.3       :BOOL; (*照明控制箱NJ-2AL3-1-启停控制*)",null,"LCB02C01_C","照明控制箱NJ-2AL3-1-启停控制",259]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","照明控制箱NJ-2AL3-2-启停控制",{"$nulls":16},"NJ-2AL3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL3-2","02C02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB02C02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%Q\"&B36*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB02C02_C AT%Q32.4 :BOOL; (*照明控制箱NJ-2AL3-2-启停控制*)"},"LLCB02C02_C             AT%Q32.4       :BOOL; (*照明控制箱NJ-2AL3-2-启停控制*)",null,"LCB02C02_C","照明控制箱NJ-2AL3-2-启停控制",260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","照明控制箱NJ-2AL3-3-启停控制",{"$nulls":16},"NJ-2AL3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL3-3","02C03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"LCB02C03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%Q\"&B36*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LLCB02C03_C AT%Q32.5 :BOOL; (*照明控制箱NJ-2AL3-3-启停控制*)"},"LLCB02C03_C             AT%Q32.5       :BOOL; (*照明控制箱NJ-2AL3-3-启停控制*)",null,"LCB02C03_C","照明控制箱NJ-2AL3-3-启停控制",261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","照明控制箱NJ-2AL3-4-启停控制",{"$nulls":16},"NJ-2AL3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL3-4","02C04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":"LCB02C04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%Q\"&B36*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":"LLCB02C04_C AT%Q32.6 :BOOL; (*照明控制箱NJ-2AL3-4-启停控制*)"},"LLCB02C04_C             AT%Q32.6       :BOOL; (*照明控制箱NJ-2AL3-4-启停控制*)",null,"LCB02C04_C","照明控制箱NJ-2AL3-4-启停控制",262]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%Q\"&B36*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",263]
[null,{"$f":"B48","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B48&\"地址: \"&B45&\" *)\"","v":"(* IOM 0801U地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH44&AA44&\"-\"&AK44","v":"空调机组NJ-2AP(KT)3-1-回风温度"},{"$nulls":16},{"$f":"IF(AI44=\"\",\"\",AI44)","v":"NJ-2AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-1","02C01","回风温度",{"$f":"AH44&\"-\"&AK44","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"AHU02C01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B45*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LAHU02C01_RT AT%I48.0 :INT ; (*空调机组NJ-2AP(KT)3-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN44,SEARCH(\"AT%\",AN44),,REPT(\" \",25-SEARCH(\"AT%\",AN44))),SEARCH(\":\",REPLACE(AN44,SEARCH(\"AT%\",AN44),,REPT(\" \",25-SEARCH(\"AT%\",AN44)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN44,SEARCH(\"AT%\",AN44),,REPT(\" \",25-SEARCH(\"AT%\",AN44)))))),\" \")","v":"LAHU02C01_RT            AT%I48.0       :INT ; (*空调机组NJ-2AP(KT)3-1-回风温度*)"},null,{"$f":"AM44","v":"AHU02C01_RT"},{"$f":"J44","v":"空调机组NJ-2AP(KT)3-1-回风温度"},{"$f":"30000+($B45*8+F44-1)","v":30024}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-2AP(KT)3-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI45=\"\",\"\",AI45)","v":"NJ-2AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-1","02C01","水阀反馈",{"$f":"AH45&\"-\"&AK45","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"AHU02C01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B45*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LAHU02C01_WVB AT%I50.0 :INT ; (*空调机组NJ-2AP(KT)3-1-水阀反馈*)"},"LAHU02C01_WVB           AT%I50.0       :INT ; (*空调机组NJ-2AP(KT)3-1-水阀反馈*)",null,"AHU02C01_WVB",{"$f":"J45","v":"空调机组NJ-2AP(KT)3-1-水阀反馈"},{"$f":"AS44+1","v":30025}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-2AP(KT)3-2-回风温度",{"$nulls":16},"NJ-2AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-2","02C02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"AHU02C02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B45*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LAHU02C02_RT AT%I52.0 :INT ; (*空调机组NJ-2AP(KT)3-2-回风温度*)"},"LAHU02C02_RT            AT%I52.0       :INT ; (*空调机组NJ-2AP(KT)3-2-回风温度*)",null,"AHU02C02_RT","空调机组NJ-2AP(KT)3-2-回风温度",{"$f":"AS45+1","v":30026}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-2AP(KT)3-2-水阀反馈",{"$nulls":16},"NJ-2AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-2","02C02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"AHU02C02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B45*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LAHU02C02_WVB AT%I54.0 :INT ; (*空调机组NJ-2AP(KT)3-2-水阀反馈*)"},"LAHU02C02_WVB           AT%I54.0       :INT ; (*空调机组NJ-2AP(KT)3-2-水阀反馈*)",null,"AHU02C02_WVB","空调机组NJ-2AP(KT)3-2-水阀反馈",30027]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B45),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-2AP(KT)3-3-回风温度",{"$nulls":16},"NJ-2AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-3","02C03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"AHU02C03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B45*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LAHU02C03_RT AT%I56.0 :INT ; (*空调机组NJ-2AP(KT)3-3-回风温度*)"},"LAHU02C03_RT            AT%I56.0       :INT ; (*空调机组NJ-2AP(KT)3-3-回风温度*)",null,"AHU02C03_RT","空调机组NJ-2AP(KT)3-3-回风温度",30028]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B47=20,1,IF(B47=50,10,IF(B47=125,11,IF(B47=250,100,IF(B47=500,101,IF(B47=800,110,IF(B47=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B47=20,1,IF(B47=50,10,IF(B47=125,11,IF(B47=250,100,IF(B47=500,101,IF(B47=800,110,IF(B47=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-2AP(KT)3-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI49=\"\",\"\",AI49)","v":"NJ-2AP(KT)3-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-3","02C03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"AHU02C03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B45*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LAHU02C03_WVB AT%I58.0 :INT ; (*空调机组NJ-2AP(KT)3-3-水阀反馈*)"},"LAHU02C03_WVB           AT%I58.0       :INT ; (*空调机组NJ-2AP(KT)3-3-水阀反馈*)",null,"AHU02C03_WVB",{"$f":"J49","v":"空调机组NJ-2AP(KT)3-3-水阀反馈"},30029]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B47=20,1,IF(B47=50,10,IF(B47=125,11,IF(B47=250,100,IF(B47=500,101,IF(B47=800,110,IF(B47=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B47=20,1,IF(B47=50,10,IF(B47=125,11,IF(B47=250,100,IF(B47=500,101,IF(B47=800,110,IF(B47=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B45*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30030]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B47=20,1,IF(B47=50,10,IF(B47=125,11,IF(B47=250,100,IF(B47=500,101,IF(B47=800,110,IF(B47=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B47=20,1,IF(B47=50,10,IF(B47=125,11,IF(B47=250,100,IF(B47=500,101,IF(B47=800,110,IF(B47=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B45*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30031]
[null,{"$f":"B57","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B57&\"地址: \"&B54&\" *)\"","v":"(* IOM 0401A地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH53&AA53&\"-\"&AK53","v":"空调机组NJ-2AP(KT)3-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI53=\"\",\"\",AI53)","v":"NJ-2AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-1","02C01","水阀控制",{"$f":"AH53&\"-\"&AK53","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"AHU02C01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%Q\"&B54*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LAHU02C01_WVC AT%Q64.0 :INT ; (*空调机组NJ-2AP(KT)3-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN53,SEARCH(\"AT%\",AN53),,REPT(\" \",25-SEARCH(\"AT%\",AN53))),SEARCH(\":\",REPLACE(AN53,SEARCH(\"AT%\",AN53),,REPT(\" \",25-SEARCH(\"AT%\",AN53)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN53,SEARCH(\"AT%\",AN53),,REPT(\" \",25-SEARCH(\"AT%\",AN53)))))),\" \")","v":"LAHU02C01_WVC           AT%Q64.0       :INT ; (*空调机组NJ-2AP(KT)3-1-水阀控制*)"},null,{"$f":"AM53","v":"AHU02C01_WVC"},{"$f":"J53","v":"空调机组NJ-2AP(KT)3-1-水阀控制"},{"$f":"40000+($B54*8+F53-1)","v":40032}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH54&AA54&\"-\"&AK54","v":"空调机组NJ-2AP(KT)3-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI54=\"\",\"\",AI54)","v":"NJ-2AP(KT)3-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-2","02C02","水阀控制",{"$f":"AH54&\"-\"&AK54","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"AHU02C02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%Q\"&B54*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LAHU02C02_WVC AT%Q66.0 :INT ; (*空调机组NJ-2AP(KT)3-2-水阀控制*)"},"LAHU02C02_WVC           AT%Q66.0       :INT ; (*空调机组NJ-2AP(KT)3-2-水阀控制*)",null,"AHU02C02_WVC",{"$f":"J54","v":"空调机组NJ-2AP(KT)3-2-水阀控制"},{"$f":"AS53+1","v":40033}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH55&AA55&\"-\"&AK55","v":"空调机组NJ-2AP(KT)3-3-水阀控制"},{"$nulls":16},"NJ-2AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)3-3","02C03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"AHU02C03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%Q\"&B54*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LAHU02C03_WVC AT%Q68.0 :INT ; (*空调机组NJ-2AP(KT)3-3-水阀控制*)"},"LAHU02C03_WVC           AT%Q68.0       :INT ; (*空调机组NJ-2AP(KT)3-3-水阀控制*)",null,"AHU02C03_WVC","空调机组NJ-2AP(KT)3-3-水阀控制",{"$f":"AS54+1","v":40034}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH56&AA56&\"-\"&AK56","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%Q\"&B54*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40035]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B54),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B56=20,1,IF(B56=50,10,IF(B56=125,11,IF(B56=250,100,IF(B56=500,101,IF(B56=800,110,IF(B56=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B56=20,1,IF(B56=50,10,IF(B56=125,11,IF(B56=250,100,IF(B56=500,101,IF(B56=800,110,IF(B56=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B56=20,1,IF(B56=50,10,IF(B56=125,11,IF(B56=250,100,IF(B56=500,101,IF(B56=800,110,IF(B56=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B56=20,1,IF(B56=50,10,IF(B56=125,11,IF(B56=250,100,IF(B56=500,101,IF(B56=800,110,IF(B56=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B56=20,1,IF(B56=50,10,IF(B56=125,11,IF(B56=250,100,IF(B56=500,101,IF(B56=800,110,IF(B56=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B56=20,1,IF(B56=50,10,IF(B56=125,11,IF(B56=250,100,IF(B56=500,101,IF(B56=800,110,IF(B56=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L103","index":10,"n_rows":84,"n_cols":45,"rows_kept":84,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[41,5,41,6],[41,9,41,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[4,1,5,1],[11,1,22,1],[28,1,39,1],[45,1,56,1],[62,1,65,1],[71,1,74,1],[80,1,83,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[49,2,56,4],[32,2,39,4],[15,2,22,4],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L13",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH8&AA8&\"-\"&AK8","v":"空调机组NJ-1AP(KT)3-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-1AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)3-1","01C01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH8,List!$B$3:$D$445,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,List!$K$2:$M$447,2,FALSE)","v":"AHU01C01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LAHU01C01_R AT%I80.0 :BOOL; (*空调机组NJ-1AP(KT)3-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LAHU01C01_R             AT%I80.0       :BOOL; (*空调机组NJ-1AP(KT)3-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L13\\L13AHU01C01_R"},{"$f":"J8","v":"空调机组NJ-1AP(KT)3-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":10640}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-1AP(KT)3-1-故障状态",{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-1AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)3-1","01C01","故障状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU01C01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU01C01_F AT%I80.1 :BOOL; (*空调机组NJ-1AP(KT)3-1-故障状态*)"},"LAHU01C01_F             AT%I80.1       :BOOL; (*空调机组NJ-1AP(KT)3-1-故障状态*)",null,"L13\\L13AHU01C01_F",{"$f":"J9","v":"空调机组NJ-1AP(KT)3-1-故障状态"},{"$f":"AS8+1","v":10641}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},3,null,5,6,"空调机组NJ-1AP(KT)3-1-自动状态",{"$nulls":16},"NJ-1AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)3-1","01C01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU01C01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU01C01_A AT%I80.2 :BOOL; (*空调机组NJ-1AP(KT)3-1-自动状态*)"},"LAHU01C01_A             AT%I80.2       :BOOL; (*空调机组NJ-1AP(KT)3-1-自动状态*)",null,"L13\\L13AHU01C01_A","空调机组NJ-1AP(KT)3-1-自动状态",{"$f":"AS9+1","v":10642}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-1AP(KT)3-1-风机压差",{"$nulls":16},"NJ-1AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)3-1","01C01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU01C01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU01C01_FPS AT%I80.3 :BOOL; (*空调机组NJ-1AP(KT)3-1-风机压差*)"},"LAHU01C01_FPS           AT%I80.3       :BOOL; (*空调机组NJ-1AP(KT)3-1-风机压差*)",null,"L13\\L13AHU01C01_FPS","空调机组NJ-1AP(KT)3-1-风机压差",10643]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-1AP(KT)3-1-运行状态",{"$nulls":16},"NJ-1AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)3-1","01C02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU01C02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU01C02_R AT%I80.4 :BOOL; (*空调机组NJ-1AP(KT)3-1-运行状态*)"},"LAHU01C02_R             AT%I80.4       :BOOL; (*空调机组NJ-1AP(KT)3-1-运行状态*)",null,"L13\\L13AHU01C02_R","空调机组NJ-1AP(KT)3-1-运行状态",10644]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-1AP(KT)3-2-故障状态",{"$nulls":16},"NJ-1AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)3-2","01C02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU01C02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU01C02_F AT%I80.5 :BOOL; (*空调机组NJ-1AP(KT)3-2-故障状态*)"},"LAHU01C02_F             AT%I80.5       :BOOL; (*空调机组NJ-1AP(KT)3-2-故障状态*)",null,"L13\\L13AHU01C02_F","空调机组NJ-1AP(KT)3-2-故障状态",10645]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-1AP(KT)3-2-自动状态",{"$nulls":16},"NJ-1AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)3-2","01C02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU01C02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU01C02_A AT%I80.6 :BOOL; (*空调机组NJ-1AP(KT)3-2-自动状态*)"},"LAHU01C02_A             AT%I80.6       :BOOL; (*空调机组NJ-1AP(KT)3-2-自动状态*)",null,"L13\\L13AHU01C02_A","空调机组NJ-1AP(KT)3-2-自动状态",10646]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-1AP(KT)3-2-风机压差",{"$nulls":16},"NJ-1AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)3-2","01C02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU01C02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU01C02_FPS AT%I80.7 :BOOL; (*空调机组NJ-1AP(KT)3-2-风机压差*)"},"LAHU01C02_FPS           AT%I80.7       :BOOL; (*空调机组NJ-1AP(KT)3-2-风机压差*)",null,"L13\\L13AHU01C02_FPS","空调机组NJ-1AP(KT)3-2-风机压差",10647]
[{"$nulls":5},9,null,17,18,"空调机组NJ-1AP(KT)3-2-运行状态",{"$nulls":16},"NJ-1AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)3-2","01C03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU01C03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU01C03_R AT%I81.0 :BOOL; (*空调机组NJ-1AP(KT)3-2-运行状态*)"},"LAHU01C03_R             AT%I81.0       :BOOL; (*空调机组NJ-1AP(KT)3-2-运行状态*)",null,"L13\\L13AHU01C03_R","空调机组NJ-1AP(KT)3-2-运行状态",10648]
[{"$nulls":5},10,null,19,20,"空调机组NJ-1AP(KT)3-3-故障状态",{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-1AP(KT)3-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)3-3","01C03","故障状态",{"$f":"AH17&\"-\"&AK17","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU01C03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU01C03_F AT%I81.1 :BOOL; (*空调机组NJ-1AP(KT)3-3-故障状态*)"},"LAHU01C03_F             AT%I81.1       :BOOL; (*空调机组NJ-1AP(KT)3-3-故障状态*)",null,"L13\\L13AHU01C03_F","空调机组NJ-1AP(KT)3-3-故障状态",10649]
[{"$nulls":5},11,null,21,22,"空调机组NJ-1AP(KT)3-3-自动状态",{"$nulls":16},"NJ-1AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)3-3","01C03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU01C03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU01C03_A AT%I81.2 :BOOL; (*空调机组NJ-1AP(KT)3-3-自动状态*)"},"LAHU01C03_A             AT%I81.2       :BOOL; (*空调机组NJ-1AP(KT)3-3-自动状态*)",null,"L13\\L13AHU01C03_A","空调机组NJ-1AP(KT)3-3-自动状态",10650]
[{"$nulls":5},12,null,23,24,"空调机组NJ-1AP(KT)3-3-风机压差",{"$nulls":16},"NJ-1AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)3-3","01C03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU01C03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU01C03_FPS AT%I81.3 :BOOL; (*空调机组NJ-1AP(KT)3-3-风机压差*)"},"LAHU01C03_FPS           AT%I81.3       :BOOL; (*空调机组NJ-1AP(KT)3-3-风机压差*)",null,"L13\\L13AHU01C03_FPS","空调机组NJ-1AP(KT)3-3-风机压差",10651]
[{"$nulls":5},13,null,25,26,"空调机组NJ-1AP(KT)3-4-运行状态",{"$nulls":16},"NJ-1AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)3-4","01C04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU01C04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU01C04_R AT%I81.4 :BOOL; (*空调机组NJ-1AP(KT)3-4-运行状态*)"},"LAHU01C04_R             AT%I81.4       :BOOL; (*空调机组NJ-1AP(KT)3-4-运行状态*)",null,"L13\\L13AHU01C04_R","空调机组NJ-1AP(KT)3-4-运行状态",10652]
[{"$nulls":5},14,null,27,28,"空调机组NJ-1AP(KT)3-4-故障状态",{"$nulls":16},"NJ-1AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)3-4","01C04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU01C04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU01C04_F AT%I81.5 :BOOL; (*空调机组NJ-1AP(KT)3-4-故障状态*)"},"LAHU01C04_F             AT%I81.5       :BOOL; (*空调机组NJ-1AP(KT)3-4-故障状态*)",null,"L13\\L13AHU01C04_F","空调机组NJ-1AP(KT)3-4-故障状态",10653]
[{"$nulls":5},15,null,29,30,"空调机组NJ-1AP(KT)3-4-自动状态",{"$nulls":16},"NJ-1AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)3-4","01C04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU01C04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU01C04_A AT%I81.6 :BOOL; (*空调机组NJ-1AP(KT)3-4-自动状态*)"},"LAHU01C04_A             AT%I81.6       :BOOL; (*空调机组NJ-1AP(KT)3-4-自动状态*)",null,"L13\\L13AHU01C04_A","空调机组NJ-1AP(KT)3-4-自动状态",10654]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-1AP(KT)3-4-风机压差",{"$nulls":16},"NJ-1AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)3-4","01C04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU01C04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU01C04_FPS AT%I81.7 :BOOL; (*空调机组NJ-1AP(KT)3-4-风机压差*)"},"LAHU01C04_FPS           AT%I81.7       :BOOL; (*空调机组NJ-1AP(KT)3-4-风机压差*)",null,"L13\\L13AHU01C04_FPS","空调机组NJ-1AP(KT)3-4-风机压差",10655]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 1601R地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH25&AA25&\"-\"&AK25","v":"照明控制箱NJ-1AL3-1-运行状态"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-1AL3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-1AL3-1","01C01","运行状态",{"$f":"AH25&\"-\"&AK25","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"LCB01C01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LLCB01C01_R AT%I96.0 :BOOL; (*照明控制箱NJ-1AL3-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LLCB01C01_R             AT%I96.0       :BOOL; (*照明控制箱NJ-1AL3-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L13\\L13LCB01C01_R"},{"$f":"J25","v":"照明控制箱NJ-1AL3-1-运行状态"},{"$f":"10000+($B26*16*8+F25-1)","v":10768}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},2,null,3,4,"照明控制箱NJ-1AL3-1-自动状态",{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-1AL3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-1AL3-1","01C01","自动状态",{"$f":"AH26&\"-\"&AK26","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"LCB01C01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LLCB01C01_A AT%I96.1 :BOOL; (*照明控制箱NJ-1AL3-1-自动状态*)"},"LLCB01C01_A             AT%I96.1       :BOOL; (*照明控制箱NJ-1AL3-1-自动状态*)",null,"L13\\L13LCB01C01_A",{"$f":"J26","v":"照明控制箱NJ-1AL3-1-自动状态"},{"$f":"AS25+1","v":10769}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},3,null,5,6,"照明控制箱NJ-1AL3-2-运行状态",{"$nulls":16},"NJ-1AL3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-1AL3-2","01C02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"LCB01C02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LLCB01C02_R AT%I96.2 :BOOL; (*照明控制箱NJ-1AL3-2-运行状态*)"},"LLCB01C02_R             AT%I96.2       :BOOL; (*照明控制箱NJ-1AL3-2-运行状态*)",null,"L13\\L13LCB01C02_R","照明控制箱NJ-1AL3-2-运行状态",{"$f":"AS26+1","v":10770}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":0},4,null,7,8,"照明控制箱NJ-1AL3-2-自动状态",{"$nulls":16},"NJ-1AL3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-1AL3-2","01C02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"LCB01C02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LLCB01C02_A AT%I96.3 :BOOL; (*照明控制箱NJ-1AL3-2-自动状态*)"},"LLCB01C02_A             AT%I96.3       :BOOL; (*照明控制箱NJ-1AL3-2-自动状态*)",null,"L13\\L13LCB01C02_A","照明控制箱NJ-1AL3-2-自动状态",10771]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-1AL3-3-运行状态",{"$nulls":16},"NJ-1AL3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-1AL3-3","01C03","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"LCB01C03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LLCB01C03_R AT%I96.4 :BOOL; (*照明控制箱NJ-1AL3-3-运行状态*)"},"LLCB01C03_R             AT%I96.4       :BOOL; (*照明控制箱NJ-1AL3-3-运行状态*)",null,"L13\\L13LCB01C03_R","照明控制箱NJ-1AL3-3-运行状态",10772]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-1AL3-3-自动状态",{"$nulls":16},"NJ-1AL3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-1AL3-3","01C03","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"LCB01C03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LLCB01C03_A AT%I96.5 :BOOL; (*照明控制箱NJ-1AL3-3-自动状态*)"},"LLCB01C03_A             AT%I96.5       :BOOL; (*照明控制箱NJ-1AL3-3-自动状态*)",null,"L13\\L13LCB01C03_A","照明控制箱NJ-1AL3-3-自动状态",10773]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"照明控制箱NJ-1AL3-4-运行状态",{"$nulls":16},"NJ-1AL3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-1AL3-4","01C04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"LCB01C04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LLCB01C04_R AT%I96.6 :BOOL; (*照明控制箱NJ-1AL3-4-运行状态*)"},"LLCB01C04_R             AT%I96.6       :BOOL; (*照明控制箱NJ-1AL3-4-运行状态*)",null,"L13\\L13LCB01C04_R","照明控制箱NJ-1AL3-4-运行状态",10774]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"照明控制箱NJ-1AL3-4-自动状态",{"$nulls":16},"NJ-1AL3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-1AL3-4","01C04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"LCB01C04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LLCB01C04_A AT%I96.7 :BOOL; (*照明控制箱NJ-1AL3-4-自动状态*)"},"LLCB01C04_A             AT%I96.7       :BOOL; (*照明控制箱NJ-1AL3-4-自动状态*)",null,"L13\\L13LCB01C04_A","照明控制箱NJ-1AL3-4-自动状态",10775]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-1AL3-5-运行状态",{"$nulls":16},"NJ-1AL3-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-1AL3-5","01C05","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"LCB01C05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B26*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LLCB01C05_R AT%I97.0 :BOOL; (*照明控制箱NJ-1AL3-5-运行状态*)"},"LLCB01C05_R             AT%I97.0       :BOOL; (*照明控制箱NJ-1AL3-5-运行状态*)",null,"L13\\L13LCB01C05_R","照明控制箱NJ-1AL3-5-运行状态",10776]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-1AL3-5-自动状态",{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-1AL3-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-1AL3-5","01C05","自动状态",{"$f":"AH34&\"-\"&AK34","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"LCB01C05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B26*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LLCB01C05_A AT%I97.1 :BOOL; (*照明控制箱NJ-1AL3-5-自动状态*)"},"LLCB01C05_A             AT%I97.1       :BOOL; (*照明控制箱NJ-1AL3-5-自动状态*)",null,"L13\\L13LCB01C05_A","照明控制箱NJ-1AL3-5-自动状态",10777]
[{"$nulls":5},11,null,21,22,"风机盘管NJ-1AP(KT)3-运行状态",{"$nulls":16},"NJ-1AP(KT)3",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)3","01C01","运行状态","风机盘管-运行状态",{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"FCU01C01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B26*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LFCU01C01_R AT%I97.2 :BOOL; (*风机盘管NJ-1AP(KT)3-运行状态*)"},"LFCU01C01_R             AT%I97.2       :BOOL; (*风机盘管NJ-1AP(KT)3-运行状态*)",null,"L13\\L13FCU01C01_R","风机盘管NJ-1AP(KT)3-运行状态",10778]
[{"$nulls":5},12,null,23,24,"风机盘管NJ-1AP(KT)3-自动状态",{"$nulls":16},"NJ-1AP(KT)3",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)3","01C01","自动状态","风机盘管-自动状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"FCU01C01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B26*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LFCU01C01_A AT%I97.3 :BOOL; (*风机盘管NJ-1AP(KT)3-自动状态*)"},"LFCU01C01_A             AT%I97.3       :BOOL; (*风机盘管NJ-1AP(KT)3-自动状态*)",null,"L13\\L13FCU01C01_A","风机盘管NJ-1AP(KT)3-自动状态",10779]
[{"$nulls":5},13,null,25,26,"风机盘管NJ-1AP(KT)3-电磁阀开启状态",{"$nulls":16},"NJ-1AP(KT)3",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)3","01C01","电磁阀开启状态","风机盘管-电磁阀开启状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"FCU01C01_EVR"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B26*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LFCU01C01_EVR AT%I97.4 :BOOL; (*风机盘管NJ-1AP(KT)3-电磁阀开启状态*)"},"LFCU01C01_EVR           AT%I97.4       :BOOL; (*风机盘管NJ-1AP(KT)3-电磁阀开启状态*)",null,"L13\\L13FCU01C01_EVR","风机盘管NJ-1AP(KT)3-电磁阀开启状态",10780]
[{"$nulls":5},14,null,27,28,"风机盘管NJ-1AP(KT)3-电磁阀自动状态",{"$nulls":16},"NJ-1AP(KT)3",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)3","01C01","电磁阀自动状态","风机盘管-电磁阀自动状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"FCU01C01_EVA"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B26*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LFCU01C01_EVA AT%I97.5 :BOOL; (*风机盘管NJ-1AP(KT)3-电磁阀自动状态*)"},"LFCU01C01_EVA           AT%I97.5       :BOOL; (*风机盘管NJ-1AP(KT)3-电磁阀自动状态*)",null,"L13\\L13FCU01C01_EVA","风机盘管NJ-1AP(KT)3-电磁阀自动状态",10781]
[{"$nulls":5},15,null,29,30,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B26*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10782]
[".",{"$nulls":4},16,null,31,32,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B26*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN40,SEARCH(\"AT%\",AN40),,REPT(\" \",30-SEARCH(\"AT%\",AN40))),SEARCH(\":\",REPLACE(AN40,SEARCH(\"AT%\",AN40),,REPT(\" \",30-SEARCH(\"AT%\",AN40)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN40,SEARCH(\"AT%\",AN40),,REPT(\" \",25-SEARCH(\"AT%\",AN40)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",10783]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B46&\"地址: \"&B43&\" *)\"","v":"(* IOM 1601D地址: 7 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH42&AA42&\"-\"&AK42","v":"空调机组NJ-1AP(KT)3-1-启停控制"},{"$nulls":16},{"$f":"IF(AI42=\"\",\"\",AI42)","v":"NJ-1AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","NJ-1AP(KT)3-1","01C01","启停控制",{"$f":"AH42&\"-\"&AK42","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":"AHU01C01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%Q\"&B43*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":"LAHU01C01_C AT%Q112.0 :BOOL; (*空调机组NJ-1AP(KT)3-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42))),SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))))),\" \")","v":"LAHU01C01_C             AT%Q112.0      :BOOL; (*空调机组NJ-1AP(KT)3-1-启停控制*)"},null,{"$f":"AM42","v":"AHU01C01_C"},{"$f":"J42","v":"空调机组NJ-1AP(KT)3-1-启停控制"},{"$f":"($B43*16*8+F42-1)","v":896}]
[null,7,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-1AP(KT)3-2-启停控制",{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-1AP(KT)3-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","NJ-1AP(KT)3-2","01C02","启停控制",{"$f":"AH43&\"-\"&AK43","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"AHU01C02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%Q\"&B43*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LAHU01C02_C AT%Q112.1 :BOOL; (*空调机组NJ-1AP(KT)3-2-启停控制*)"},"LAHU01C02_C             AT%Q112.1      :BOOL; (*空调机组NJ-1AP(KT)3-2-启停控制*)",null,"AHU01C02_C",{"$f":"J43","v":"空调机组NJ-1AP(KT)3-2-启停控制"},{"$f":"AS42+1","v":897}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-1AP(KT)3-3-启停控制",{"$nulls":16},"NJ-1AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","NJ-1AP(KT)3-3","01C03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"AHU01C03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%Q\"&B43*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LAHU01C03_C AT%Q112.2 :BOOL; (*空调机组NJ-1AP(KT)3-3-启停控制*)"},"LAHU01C03_C             AT%Q112.2      :BOOL; (*空调机组NJ-1AP(KT)3-3-启停控制*)",null,"AHU01C03_C","空调机组NJ-1AP(KT)3-3-启停控制",{"$f":"AS43+1","v":898}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","空调机组NJ-1AP(KT)3-4-启停控制",{"$nulls":16},"NJ-1AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","NJ-1AP(KT)3-4","01C04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"AHU01C04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%Q\"&B43*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LAHU01C04_C AT%Q112.3 :BOOL; (*空调机组NJ-1AP(KT)3-4-启停控制*)"},"LAHU01C04_C             AT%Q112.3      :BOOL; (*空调机组NJ-1AP(KT)3-4-启停控制*)",null,"AHU01C04_C","空调机组NJ-1AP(KT)3-4-启停控制",899]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","照明控制箱NJ-1AL3-1-启停控制",{"$nulls":16},"NJ-1AL3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-1AL3-1","01C01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"LCB01C01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%Q\"&B43*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LLCB01C01_C AT%Q112.4 :BOOL; (*照明控制箱NJ-1AL3-1-启停控制*)"},"LLCB01C01_C             AT%Q112.4      :BOOL; (*照明控制箱NJ-1AL3-1-启停控制*)",null,"LCB01C01_C","照明控制箱NJ-1AL3-1-启停控制",900]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","照明控制箱NJ-1AL3-2-启停控制",{"$nulls":16},"NJ-1AL3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-1AL3-2","01C02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"LCB01C02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%Q\"&B43*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LLCB01C02_C AT%Q112.5 :BOOL; (*照明控制箱NJ-1AL3-2-启停控制*)"},"LLCB01C02_C             AT%Q112.5      :BOOL; (*照明控制箱NJ-1AL3-2-启停控制*)",null,"LCB01C02_C","照明控制箱NJ-1AL3-2-启停控制",901]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","照明控制箱NJ-1AL3-3-启停控制",{"$nulls":16},"NJ-1AL3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-1AL3-3","01C03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"LCB01C03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%Q\"&B43*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LLCB01C03_C AT%Q112.6 :BOOL; (*照明控制箱NJ-1AL3-3-启停控制*)"},"LLCB01C03_C             AT%Q112.6      :BOOL; (*照明控制箱NJ-1AL3-3-启停控制*)",null,"LCB01C03_C","照明控制箱NJ-1AL3-3-启停控制",902]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-1AL3-4-启停控制",{"$nulls":16},"NJ-1AL3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-1AL3-4","01C04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"LCB01C04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%Q\"&B43*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LLCB01C04_C AT%Q112.7 :BOOL; (*照明控制箱NJ-1AL3-4-启停控制*)"},"LLCB01C04_C             AT%Q112.7      :BOOL; (*照明控制箱NJ-1AL3-4-启停控制*)",null,"LCB01C04_C","照明控制箱NJ-1AL3-4-启停控制",903]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-1AL3-5-启停控制",{"$nulls":16},"NJ-1AL3-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-1AL3-5","01C05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"LCB01C05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%Q\"&B43*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LLCB01C05_C AT%Q113.0 :BOOL; (*照明控制箱NJ-1AL3-5-启停控制*)"},"LLCB01C05_C             AT%Q113.0      :BOOL; (*照明控制箱NJ-1AL3-5-启停控制*)",null,"LCB01C05_C","照明控制箱NJ-1AL3-5-启停控制",904]
[{"$nulls":5},10,null,"10+","10-","风机盘管NJ-1AP(KT)3-启停控制",{"$nulls":16},{"$f":"IF(AI51=\"\",\"\",AI51)","v":"NJ-1AP(KT)3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"风机盘管","NJ-1AP(KT)3","01C01","启停控制",{"$f":"AH51&\"-\"&AK51","v":"风机盘管-启停控制"},{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"FCU01C01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%Q\"&B43*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LFCU01C01_C AT%Q113.1 :BOOL; (*风机盘管NJ-1AP(KT)3-启停控制*)"},"LFCU01C01_C             AT%Q113.1      :BOOL; (*风机盘管NJ-1AP(KT)3-启停控制*)",null,"FCU01C01_C",{"$f":"J51","v":"风机盘管NJ-1AP(KT)3-启停控制"},905]
[{"$nulls":5},11,null,"11+","11-","风机盘管NJ-1AP(KT)3-电磁阀开关控制",{"$nulls":16},"NJ-1AP(KT)3",{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"风机盘管","NJ-1AP(KT)3","01C01","电磁阀开关控制","风机盘管-电磁阀开关控制",{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"FCU01C01_EVC"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%Q\"&B43*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LFCU01C01_EVC AT%Q113.2 :BOOL; (*风机盘管NJ-1AP(KT)3-电磁阀开关控制*)"},"LFCU01C01_EVC           AT%Q113.2      :BOOL; (*风机盘管NJ-1AP(KT)3-电磁阀开关控制*)",null,"FCU01C01_EVC","风机盘管NJ-1AP(KT)3-电磁阀开关控制",906]
[{"$nulls":5},12,null,"12+","12-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%Q\"&B43*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",907]
[{"$nulls":5},13,null,"13+","13-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%Q\"&B43*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",908]
[{"$nulls":5},14,null,"14+","14-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%Q\"&B43*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",909]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%Q\"&B43*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",910]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%Q\"&B43*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",911]
[null,{"$f":"B63","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B63&\"地址: \"&B60&\" *)\"","v":"(* IOM 0801U地址: 8 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH59&AA59&\"-\"&AK59","v":"空调机组NJ-1AP(KT)3-1-回风温度"},{"$nulls":16},{"$f":"IF(AI59=\"\",\"\",AI59)","v":"NJ-1AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","NJ-1AP(KT)3-1","01C01","回风温度",{"$f":"AH59&\"-\"&AK59","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH59,List!$B$3:$D$445,2,FALSE)&AJ59&\"_\"&VLOOKUP(AK59,List!$K$2:$M$447,2,FALSE)","v":"AHU01C01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM59&\" \"&\"AT%I\"&B60*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J59&\"*)\",\" \")","v":"LAHU01C01_RT AT%I128.0 :INT ; (*空调机组NJ-1AP(KT)3-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59))),SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))))),\" \")","v":"LAHU01C01_RT            AT%I128.0      :INT ; (*空调机组NJ-1AP(KT)3-1-回风温度*)"},null,{"$f":"AM59","v":"AHU01C01_RT"},{"$f":"J59","v":"空调机组NJ-1AP(KT)3-1-回风温度"},{"$f":"30000+($B60*8+F59-1)","v":30064}]
[null,8,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-1AP(KT)3-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-1AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","NJ-1AP(KT)3-1","01C01","水阀反馈",{"$f":"AH60&\"-\"&AK60","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"AHU01C01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%I\"&B60*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LAHU01C01_WVB AT%I130.0 :INT ; (*空调机组NJ-1AP(KT)3-1-水阀反馈*)"},"LAHU01C01_WVB           AT%I130.0      :INT ; (*空调机组NJ-1AP(KT)3-1-水阀反馈*)",null,"AHU01C01_WVB",{"$f":"J60","v":"空调机组NJ-1AP(KT)3-1-水阀反馈"},{"$f":"AS59+1","v":30065}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-1AP(KT)3-2-回风温度",{"$nulls":16},"NJ-1AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","NJ-1AP(KT)3-2","01C02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"AHU01C02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%I\"&B60*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LAHU01C02_RT AT%I132.0 :INT ; (*空调机组NJ-1AP(KT)3-2-回风温度*)"},"LAHU01C02_RT            AT%I132.0      :INT ; (*空调机组NJ-1AP(KT)3-2-回风温度*)",null,"AHU01C02_RT","空调机组NJ-1AP(KT)3-2-回风温度",{"$f":"AS60+1","v":30066}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-1AP(KT)3-2-水阀反馈",{"$nulls":16},"NJ-1AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","NJ-1AP(KT)3-2","01C02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"AHU01C02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B60*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LAHU01C02_WVB AT%I134.0 :INT ; (*空调机组NJ-1AP(KT)3-2-水阀反馈*)"},"LAHU01C02_WVB           AT%I134.0      :INT ; (*空调机组NJ-1AP(KT)3-2-水阀反馈*)",null,"AHU01C02_WVB","空调机组NJ-1AP(KT)3-2-水阀反馈",30067]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-1AP(KT)3-3-回风温度",{"$nulls":16},"NJ-1AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","NJ-1AP(KT)3-3","01C03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"AHU01C03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B60*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LAHU01C03_RT AT%I136.0 :INT ; (*空调机组NJ-1AP(KT)3-3-回风温度*)"},"LAHU01C03_RT            AT%I136.0      :INT ; (*空调机组NJ-1AP(KT)3-3-回风温度*)",null,"AHU01C03_RT","空调机组NJ-1AP(KT)3-3-回风温度",30068]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-1AP(KT)3-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI64=\"\",\"\",AI64)","v":"NJ-1AP(KT)3-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","NJ-1AP(KT)3-3","01C03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"AHU01C03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B60*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LAHU01C03_WVB AT%I138.0 :INT ; (*空调机组NJ-1AP(KT)3-3-水阀反馈*)"},"LAHU01C03_WVB           AT%I138.0      :INT ; (*空调机组NJ-1AP(KT)3-3-水阀反馈*)",null,"AHU01C03_WVB",{"$f":"J64","v":"空调机组NJ-1AP(KT)3-3-水阀反馈"},30069]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-1AP(KT)3-4-回风温度",{"$nulls":16},"NJ-1AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","NJ-1AP(KT)3-4","01C04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":"AHU01C04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B60*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":"LAHU01C04_RT AT%I140.0 :INT ; (*空调机组NJ-1AP(KT)3-4-回风温度*)"},"LAHU01C04_RT            AT%I140.0      :INT ; (*空调机组NJ-1AP(KT)3-4-回风温度*)",null,"AHU01C04_RT","空调机组NJ-1AP(KT)3-4-回风温度",30070]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-1AP(KT)3-4-水阀反馈",{"$nulls":16},"NJ-1AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","NJ-1AP(KT)3-4","01C04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":"AHU01C04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B60*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":"LAHU01C04_WVB AT%I142.0 :INT ; (*空调机组NJ-1AP(KT)3-4-水阀反馈*)"},"LAHU01C04_WVB           AT%I142.0      :INT ; (*空调机组NJ-1AP(KT)3-4-水阀反馈*)",null,"AHU01C04_WVB","空调机组NJ-1AP(KT)3-4-水阀反馈",30071]
[null,{"$f":"B72","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B72&\"地址: \"&B69&\" *)\"","v":"(* IOM 0401U地址: 9 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH68&AA68&\"-\"&AK68","v":"风机盘管NJ-1AP(KT)3-温度状态"},{"$nulls":16},{"$f":"IF(AI68=\"\",\"\",AI68)","v":"NJ-1AP(KT)3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"风机盘管","NJ-1AP(KT)3","01C01","温度状态",{"$f":"AH68&\"-\"&AK68","v":"风机盘管-温度状态"},{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"FCU01C01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%I\"&B69*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LFCU01C01_T AT%I144.0 :INT ; (*风机盘管NJ-1AP(KT)3-温度状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68))),SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))))),\" \")","v":"LFCU01C01_T             AT%I144.0      :INT ; (*风机盘管NJ-1AP(KT)3-温度状态*)"},null,"FCU01C01_T",{"$f":"J68","v":"风机盘管NJ-1AP(KT)3-温度状态"},{"$f":"30000+($B69*8+F68-1)","v":30072}]
[null,9,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":0},2,null,2,"0V","-",{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},{"$f":"AH69&\"-\"&AK69","v":"-"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%I\"&B69*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J69","v":"-"},{"$f":"AS68+1","v":30073}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":0},3,null,3,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%I\"&B69*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS69+1","v":30074}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":1},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%I\"&B69*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30075]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":0}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B81","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B81&\"地址: \"&B78&\" *)\"","v":"(* IOM 0401A地址: 10 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH77&AA77&\"-\"&AK77","v":"空调机组NJ-1AP(KT)3-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-1AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","NJ-1AP(KT)3-1","01C01","水阀控制",{"$f":"AH77&\"-\"&AK77","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"AHU01C01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%Q\"&B78*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LAHU01C01_WVC AT%Q160.0 :INT ; (*空调机组NJ-1AP(KT)3-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77))),SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))))),\" \")","v":"LAHU01C01_WVC           AT%Q160.0      :INT ; (*空调机组NJ-1AP(KT)3-1-水阀控制*)"},null,{"$f":"AM77","v":"AHU01C01_WVC"},{"$f":"J77","v":"空调机组NJ-1AP(KT)3-1-水阀控制"},{"$f":"40000+($B78*8+F77-1)","v":40080}]
[null,10,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH78&AA78&\"-\"&AK78","v":"空调机组NJ-1AP(KT)3-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-1AP(KT)3-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","NJ-1AP(KT)3-2","01C02","水阀控制",{"$f":"AH78&\"-\"&AK78","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU01C02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B78*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU01C02_WVC AT%Q162.0 :INT ; (*空调机组NJ-1AP(KT)3-2-水阀控制*)"},"LAHU01C02_WVC           AT%Q162.0      :INT ; (*空调机组NJ-1AP(KT)3-2-水阀控制*)",null,"AHU01C02_WVC",{"$f":"J78","v":"空调机组NJ-1AP(KT)3-2-水阀控制"},{"$f":"AS77+1","v":40081}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH79&AA79&\"-\"&AK79","v":"空调机组NJ-1AP(KT)3-3-水阀控制"},{"$nulls":16},"NJ-1AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","NJ-1AP(KT)3-3","01C03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU01C03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B78*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU01C03_WVC AT%Q164.0 :INT ; (*空调机组NJ-1AP(KT)3-3-水阀控制*)"},"LAHU01C03_WVC           AT%Q164.0      :INT ; (*空调机组NJ-1AP(KT)3-3-水阀控制*)",null,"AHU01C03_WVC","空调机组NJ-1AP(KT)3-3-水阀控制",{"$f":"AS78+1","v":40082}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH80&AA80&\"-\"&AK80","v":"空调机组NJ-1AP(KT)3-4-水阀控制"},{"$nulls":16},"NJ-1AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"空调机组","NJ-1AP(KT)3-4","01C04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU01C04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B78*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU01C04_WVC AT%Q166.0 :INT ; (*空调机组NJ-1AP(KT)3-4-水阀控制*)"},"LAHU01C04_WVC           AT%Q166.0      :INT ; (*空调机组NJ-1AP(KT)3-4-水阀控制*)",null,"AHU01C04_WVC","空调机组NJ-1AP(KT)3-4-水阀控制",40083]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L204","index":11,"n_rows":102,"n_cols":45,"rows_kept":102,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[6,1,6,25],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[41,5,41,6],[41,9,41,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[92,5,92,6],[92,9,92,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[101,5,101,6],[101,9,101,25],[4,1,5,1],[11,1,22,1],[28,1,39,1],[45,1,48,1],[54,1,65,1],[71,1,74,1],[80,1,83,1],[89,1,92,1],[98,1,101,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4],[32,2,39,4],[58,2,65,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L14",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"EXC-1000"]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH8&AA8&\"-\"&AK8","v":"空调机组NJ-2AP(KT)4-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-2AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-1","02D01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH8,List!$B$3:$D$445,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,List!$K$2:$M$447,2,FALSE)","v":"AHU02D01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LAHU02D01_R AT%I0.0 :BOOL; (*空调机组NJ-2AP(KT)4-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LAHU02D01_R             AT%I0.0        :BOOL; (*空调机组NJ-2AP(KT)4-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L14\\L14AHU02D01_R"},{"$f":"J8","v":"空调机组NJ-2AP(KT)4-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":10000}]
[null,0,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-2AP(KT)4-1-故障状态",{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-2AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-1","02D01","故障状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU02D01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU02D01_F AT%I0.1 :BOOL; (*空调机组NJ-2AP(KT)4-1-故障状态*)"},"LAHU02D01_F             AT%I0.1        :BOOL; (*空调机组NJ-2AP(KT)4-1-故障状态*)",null,"L14\\L14AHU02D01_F",{"$f":"J9","v":"空调机组NJ-2AP(KT)4-1-故障状态"},{"$f":"AS8+1","v":10001}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-2AP(KT)4-1-自动状态",{"$nulls":16},"NJ-2AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-1","02D01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU02D01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU02D01_A AT%I0.2 :BOOL; (*空调机组NJ-2AP(KT)4-1-自动状态*)"},"LAHU02D01_A             AT%I0.2        :BOOL; (*空调机组NJ-2AP(KT)4-1-自动状态*)",null,"L14\\L14AHU02D01_A","空调机组NJ-2AP(KT)4-1-自动状态",{"$f":"AS9+1","v":10002}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-2AP(KT)4-1-风机压差",{"$nulls":16},"NJ-2AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-1","02D01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU02D01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU02D01_FPS AT%I0.3 :BOOL; (*空调机组NJ-2AP(KT)4-1-风机压差*)"},"LAHU02D01_FPS           AT%I0.3        :BOOL; (*空调机组NJ-2AP(KT)4-1-风机压差*)",null,"L14\\L14AHU02D01_FPS","空调机组NJ-2AP(KT)4-1-风机压差",10003]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-2AP(KT)4-1-运行状态",{"$nulls":16},"NJ-2AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-1","02D02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU02D02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU02D02_R AT%I0.4 :BOOL; (*空调机组NJ-2AP(KT)4-1-运行状态*)"},"LAHU02D02_R             AT%I0.4        :BOOL; (*空调机组NJ-2AP(KT)4-1-运行状态*)",null,"L14\\L14AHU02D02_R","空调机组NJ-2AP(KT)4-1-运行状态",10004]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-2AP(KT)4-2-故障状态",{"$nulls":16},"NJ-2AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-2","02D02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU02D02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU02D02_F AT%I0.5 :BOOL; (*空调机组NJ-2AP(KT)4-2-故障状态*)"},"LAHU02D02_F             AT%I0.5        :BOOL; (*空调机组NJ-2AP(KT)4-2-故障状态*)",null,"L14\\L14AHU02D02_F","空调机组NJ-2AP(KT)4-2-故障状态",10005]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-2AP(KT)4-2-自动状态",{"$nulls":16},"NJ-2AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-2","02D02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU02D02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU02D02_A AT%I0.6 :BOOL; (*空调机组NJ-2AP(KT)4-2-自动状态*)"},"LAHU02D02_A             AT%I0.6        :BOOL; (*空调机组NJ-2AP(KT)4-2-自动状态*)",null,"L14\\L14AHU02D02_A","空调机组NJ-2AP(KT)4-2-自动状态",10006]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-2AP(KT)4-2-风机压差",{"$nulls":16},"NJ-2AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-2","02D02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU02D02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU02D02_FPS AT%I0.7 :BOOL; (*空调机组NJ-2AP(KT)4-2-风机压差*)"},"LAHU02D02_FPS           AT%I0.7        :BOOL; (*空调机组NJ-2AP(KT)4-2-风机压差*)",null,"L14\\L14AHU02D02_FPS","空调机组NJ-2AP(KT)4-2-风机压差",10007]
[{"$nulls":5},9,null,17,18,"空调机组NJ-2AP(KT)4-2-运行状态",{"$nulls":16},"NJ-2AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-2","02D03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU02D03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU02D03_R AT%I1.0 :BOOL; (*空调机组NJ-2AP(KT)4-2-运行状态*)"},"LAHU02D03_R             AT%I1.0        :BOOL; (*空调机组NJ-2AP(KT)4-2-运行状态*)",null,"L14\\L14AHU02D03_R","空调机组NJ-2AP(KT)4-2-运行状态",10008]
[{"$nulls":5},10,null,19,20,"空调机组NJ-2AP(KT)4-3-故障状态",{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-2AP(KT)4-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-3","02D03","故障状态",{"$f":"AH17&\"-\"&AK17","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU02D03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU02D03_F AT%I1.1 :BOOL; (*空调机组NJ-2AP(KT)4-3-故障状态*)"},"LAHU02D03_F             AT%I1.1        :BOOL; (*空调机组NJ-2AP(KT)4-3-故障状态*)",null,"L14\\L14AHU02D03_F","空调机组NJ-2AP(KT)4-3-故障状态",10009]
[{"$nulls":5},11,null,21,22,"空调机组NJ-2AP(KT)4-3-自动状态",{"$nulls":16},"NJ-2AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-3","02D03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU02D03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU02D03_A AT%I1.2 :BOOL; (*空调机组NJ-2AP(KT)4-3-自动状态*)"},"LAHU02D03_A             AT%I1.2        :BOOL; (*空调机组NJ-2AP(KT)4-3-自动状态*)",null,"L14\\L14AHU02D03_A","空调机组NJ-2AP(KT)4-3-自动状态",10010]
[{"$nulls":5},12,null,23,24,"空调机组NJ-2AP(KT)4-3-风机压差",{"$nulls":16},"NJ-2AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-3","02D03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU02D03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU02D03_FPS AT%I1.3 :BOOL; (*空调机组NJ-2AP(KT)4-3-风机压差*)"},"LAHU02D03_FPS           AT%I1.3        :BOOL; (*空调机组NJ-2AP(KT)4-3-风机压差*)",null,"L14\\L14AHU02D03_FPS","空调机组NJ-2AP(KT)4-3-风机压差",10011]
[{"$nulls":5},13,null,25,26,"空调机组NJ-2AP(KT)4-4-运行状态",{"$nulls":16},"NJ-2AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-4","02D04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU02D04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU02D04_R AT%I1.4 :BOOL; (*空调机组NJ-2AP(KT)4-4-运行状态*)"},"LAHU02D04_R             AT%I1.4        :BOOL; (*空调机组NJ-2AP(KT)4-4-运行状态*)",null,"L14\\L14AHU02D04_R","空调机组NJ-2AP(KT)4-4-运行状态",10012]
[{"$nulls":5},14,null,27,28,"空调机组NJ-2AP(KT)4-4-故障状态",{"$nulls":16},"NJ-2AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-4","02D04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU02D04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU02D04_F AT%I1.5 :BOOL; (*空调机组NJ-2AP(KT)4-4-故障状态*)"},"LAHU02D04_F             AT%I1.5        :BOOL; (*空调机组NJ-2AP(KT)4-4-故障状态*)",null,"L14\\L14AHU02D04_F","空调机组NJ-2AP(KT)4-4-故障状态",10013]
[{"$nulls":5},15,null,29,30,"空调机组NJ-2AP(KT)4-4-自动状态",{"$nulls":16},"NJ-2AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-4","02D04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU02D04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU02D04_A AT%I1.6 :BOOL; (*空调机组NJ-2AP(KT)4-4-自动状态*)"},"LAHU02D04_A             AT%I1.6        :BOOL; (*空调机组NJ-2AP(KT)4-4-自动状态*)",null,"L14\\L14AHU02D04_A","空调机组NJ-2AP(KT)4-4-自动状态",10014]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-2AP(KT)4-4-风机压差",{"$nulls":16},"NJ-2AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-4","02D04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU02D04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU02D04_FPS AT%I1.7 :BOOL; (*空调机组NJ-2AP(KT)4-4-风机压差*)"},"LAHU02D04_FPS           AT%I1.7        :BOOL; (*空调机组NJ-2AP(KT)4-4-风机压差*)",null,"L14\\L14AHU02D04_FPS","空调机组NJ-2AP(KT)4-4-风机压差",10015]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 1601R地址: 1 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH25&AA25&\"-\"&AK25","v":"空调机组NJ-2AP(KT)4-5-运行状态"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-2AP(KT)4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-5","02D05","运行状态",{"$f":"AH25&\"-\"&AK25","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"AHU02D05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LAHU02D05_R AT%I16.0 :BOOL; (*空调机组NJ-2AP(KT)4-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LAHU02D05_R             AT%I16.0       :BOOL; (*空调机组NJ-2AP(KT)4-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L14\\L14AHU02D05_R"},{"$f":"J25","v":"空调机组NJ-2AP(KT)4-5-运行状态"},{"$f":"10000+($B26*16*8+F25-1)","v":10128}]
[null,1,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-2AP(KT)4-5-故障状态",{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-2AP(KT)4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-5","02D05","故障状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU02D05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU02D05_F AT%I16.1 :BOOL; (*空调机组NJ-2AP(KT)4-5-故障状态*)"},"LAHU02D05_F             AT%I16.1       :BOOL; (*空调机组NJ-2AP(KT)4-5-故障状态*)",null,"L14\\L14AHU02D05_F",{"$f":"J26","v":"空调机组NJ-2AP(KT)4-5-故障状态"},{"$f":"AS25+1","v":10129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-2AP(KT)4-5-自动状态",{"$nulls":16},"NJ-2AP(KT)4-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-5","02D05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU02D05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU02D05_A AT%I16.2 :BOOL; (*空调机组NJ-2AP(KT)4-5-自动状态*)"},"LAHU02D05_A             AT%I16.2       :BOOL; (*空调机组NJ-2AP(KT)4-5-自动状态*)",null,"L14\\L14AHU02D05_A","空调机组NJ-2AP(KT)4-5-自动状态",{"$f":"AS26+1","v":10130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-2AP(KT)4-5-风机压差",{"$nulls":16},"NJ-2AP(KT)4-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-5","02D05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU02D05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU02D05_FPS AT%I16.3 :BOOL; (*空调机组NJ-2AP(KT)4-5-风机压差*)"},"LAHU02D05_FPS           AT%I16.3       :BOOL; (*空调机组NJ-2AP(KT)4-5-风机压差*)",null,"L14\\L14AHU02D05_FPS","空调机组NJ-2AP(KT)4-5-风机压差",10131]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-2AP(KT)4-6-运行状态",{"$nulls":16},"NJ-2AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-6","02D06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU02D06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU02D06_R AT%I16.4 :BOOL; (*空调机组NJ-2AP(KT)4-6-运行状态*)"},"LAHU02D06_R             AT%I16.4       :BOOL; (*空调机组NJ-2AP(KT)4-6-运行状态*)",null,"L14\\L14AHU02D06_R","空调机组NJ-2AP(KT)4-6-运行状态",10132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-2AP(KT)4-6-故障状态",{"$nulls":16},"NJ-2AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-6","02D06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU02D06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU02D06_F AT%I16.5 :BOOL; (*空调机组NJ-2AP(KT)4-6-故障状态*)"},"LAHU02D06_F             AT%I16.5       :BOOL; (*空调机组NJ-2AP(KT)4-6-故障状态*)",null,"L14\\L14AHU02D06_F","空调机组NJ-2AP(KT)4-6-故障状态",10133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-2AP(KT)4-6-自动状态",{"$nulls":16},"NJ-2AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-6","02D06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU02D06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU02D06_A AT%I16.6 :BOOL; (*空调机组NJ-2AP(KT)4-6-自动状态*)"},"LAHU02D06_A             AT%I16.6       :BOOL; (*空调机组NJ-2AP(KT)4-6-自动状态*)",null,"L14\\L14AHU02D06_A","空调机组NJ-2AP(KT)4-6-自动状态",10134]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-2AP(KT)4-6-风机压差",{"$nulls":16},"NJ-2AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-6","02D06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU02D06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU02D06_FPS AT%I16.7 :BOOL; (*空调机组NJ-2AP(KT)4-6-风机压差*)"},"LAHU02D06_FPS           AT%I16.7       :BOOL; (*空调机组NJ-2AP(KT)4-6-风机压差*)",null,"L14\\L14AHU02D06_FPS","空调机组NJ-2AP(KT)4-6-风机压差",10135]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-2AL4-1-运行状态",{"$nulls":16},"NJ-2AL4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-1","02D01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"LCB02D01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B26*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LLCB02D01_R AT%I17.0 :BOOL; (*照明控制箱NJ-2AL4-1-运行状态*)"},"LLCB02D01_R             AT%I17.0       :BOOL; (*照明控制箱NJ-2AL4-1-运行状态*)",null,"L14\\L14LCB02D01_R","照明控制箱NJ-2AL4-1-运行状态",10136]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-2AL4-1-自动状态",{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-2AL4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-1","02D01","自动状态",{"$f":"AH34&\"-\"&AK34","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"LCB02D01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B26*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LLCB02D01_A AT%I17.1 :BOOL; (*照明控制箱NJ-2AL4-1-自动状态*)"},"LLCB02D01_A             AT%I17.1       :BOOL; (*照明控制箱NJ-2AL4-1-自动状态*)",null,"L14\\L14LCB02D01_A",{"$f":"J34","v":"照明控制箱NJ-2AL4-1-自动状态"},10137]
[{"$nulls":5},11,null,21,22,"照明控制箱NJ-2AL4-2-运行状态",{"$nulls":16},"NJ-2AL4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-2","02D02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"LCB02D02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B26*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LLCB02D02_R AT%I17.2 :BOOL; (*照明控制箱NJ-2AL4-2-运行状态*)"},"LLCB02D02_R             AT%I17.2       :BOOL; (*照明控制箱NJ-2AL4-2-运行状态*)",null,"L14\\L14LCB02D02_R","照明控制箱NJ-2AL4-2-运行状态",10138]
[{"$nulls":5},12,null,23,24,"照明控制箱NJ-2AL4-2-自动状态",{"$nulls":16},"NJ-2AL4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-2","02D02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"LCB02D02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B26*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LLCB02D02_A AT%I17.3 :BOOL; (*照明控制箱NJ-2AL4-2-自动状态*)"},"LLCB02D02_A             AT%I17.3       :BOOL; (*照明控制箱NJ-2AL4-2-自动状态*)",null,"L14\\L14LCB02D02_A","照明控制箱NJ-2AL4-2-自动状态",10139]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-2AL4-3-运行状态",{"$nulls":16},"NJ-2AL4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-3","02D03","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"LCB02D03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B26*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LLCB02D03_R AT%I17.4 :BOOL; (*照明控制箱NJ-2AL4-3-运行状态*)"},"LLCB02D03_R             AT%I17.4       :BOOL; (*照明控制箱NJ-2AL4-3-运行状态*)",null,"L14\\L14LCB02D03_R","照明控制箱NJ-2AL4-3-运行状态",10140]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-2AL4-3-自动状态",{"$nulls":16},"NJ-2AL4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-3","02D03","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB02D03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B26*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB02D03_A AT%I17.5 :BOOL; (*照明控制箱NJ-2AL4-3-自动状态*)"},"LLCB02D03_A             AT%I17.5       :BOOL; (*照明控制箱NJ-2AL4-3-自动状态*)",null,"L14\\L14LCB02D03_A","照明控制箱NJ-2AL4-3-自动状态",10141]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-2AL4-4-运行状态",{"$nulls":16},"NJ-2AL4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-4","02D04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB02D04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B26*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB02D04_R AT%I17.6 :BOOL; (*照明控制箱NJ-2AL4-4-运行状态*)"},"LLCB02D04_R             AT%I17.6       :BOOL; (*照明控制箱NJ-2AL4-4-运行状态*)",null,"L14\\L14LCB02D04_R","照明控制箱NJ-2AL4-4-运行状态",10142]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-2AL4-4-自动状态",{"$nulls":16},"NJ-2AL4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-4","02D04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"LCB02D04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B26*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LLCB02D04_A AT%I17.7 :BOOL; (*照明控制箱NJ-2AL4-4-自动状态*)"},"LLCB02D04_A             AT%I17.7       :BOOL; (*照明控制箱NJ-2AL4-4-自动状态*)",null,"L14\\L14LCB02D04_A","照明控制箱NJ-2AL4-4-自动状态",10143]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B46&\"地址: \"&B43&\" *)\"","v":"(* IOM 0801R 地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH42&AA42&\"-\"&AK42","v":"照明控制箱NJ-2AL4-5-运行状态"},{"$nulls":16},{"$f":"IF(AI42=\"\",\"\",AI42)","v":"NJ-2AL4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-5","02D05","运行状态",{"$f":"AH42&\"-\"&AK42","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":"LCB02D05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%I\"&B43*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":"LLCB02D05_R AT%I32.0 :BOOL; (*照明控制箱NJ-2AL4-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42))),SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))))),\" \")","v":"LLCB02D05_R             AT%I32.0       :BOOL; (*照明控制箱NJ-2AL4-5-运行状态*)"},null,{"$f":"AM42","v":"LCB02D05_R"},{"$f":"J42","v":"照明控制箱NJ-2AL4-5-运行状态"},{"$f":"10000+($B43*16*8+F42-1)","v":10256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},2,null,2,"C",{"$f":"AH43&AA43&\"-\"&AK43","v":"照明控制箱NJ-2AL4-5-自动状态"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-2AL4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-5","02D05","自动状态",{"$f":"AH43&\"-\"&AK43","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"LCB02D05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B43*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LLCB02D05_A AT%I32.1 :BOOL; (*照明控制箱NJ-2AL4-5-自动状态*)"},"LLCB02D05_A             AT%I32.1       :BOOL; (*照明控制箱NJ-2AL4-5-自动状态*)",null,{"$f":"AM43","v":"LCB02D05_A"},{"$f":"J43","v":"照明控制箱NJ-2AL4-5-自动状态"},{"$f":"AS42+1","v":10257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":0},3,null,3,"C",{"$f":"AH44&AA44&\"-\"&AK44","v":"照明控制箱NJ-2AL4-6-运行状态"},{"$nulls":16},"NJ-2AL4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-6","02D06","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"LCB02D06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B43*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LLCB02D06_R AT%I32.2 :BOOL; (*照明控制箱NJ-2AL4-6-运行状态*)"},"LLCB02D06_R             AT%I32.2       :BOOL; (*照明控制箱NJ-2AL4-6-运行状态*)",null,"LCB02D06_R","照明控制箱NJ-2AL4-6-运行状态",{"$f":"AS43+1","v":10258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":0},4,null,4,"C",{"$f":"AH45&AA45&\"-\"&AK45","v":"照明控制箱NJ-2AL4-6-自动状态"},{"$nulls":16},"NJ-2AL4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-6","02D06","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"LCB02D06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B43*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LLCB02D06_A AT%I32.3 :BOOL; (*照明控制箱NJ-2AL4-6-自动状态*)"},"LLCB02D06_A             AT%I32.3       :BOOL; (*照明控制箱NJ-2AL4-6-自动状态*)",null,"LCB02D06_A","照明控制箱NJ-2AL4-6-自动状态",10259]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},5,null,5,"C","风机盘管NJ-2AP(KT)4-1-运行状态",{"$nulls":16},"NJ-2AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-2AP(KT)4-1","02D01","运行状态","风机盘管-运行状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"FCU02D01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B43*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LFCU02D01_R AT%I32.4 :BOOL; (*风机盘管NJ-2AP(KT)4-1-运行状态*)"},"LFCU02D01_R             AT%I32.4       :BOOL; (*风机盘管NJ-2AP(KT)4-1-运行状态*)",null,"FCU02D01_R","风机盘管NJ-2AP(KT)4-1-运行状态",10260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","风机盘管NJ-2AP(KT)4-1-自动状态",{"$nulls":16},"NJ-2AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-2AP(KT)4-1","02D01","自动状态","风机盘管-自动状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"FCU02D01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B43*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LFCU02D01_A AT%I32.5 :BOOL; (*风机盘管NJ-2AP(KT)4-1-自动状态*)"},"LFCU02D01_A             AT%I32.5       :BOOL; (*风机盘管NJ-2AP(KT)4-1-自动状态*)",null,"FCU02D01_A","风机盘管NJ-2AP(KT)4-1-自动状态",10261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","风机盘管NJ-2AP(KT)4-1-电磁阀开启状态",{"$nulls":16},"NJ-2AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-2AP(KT)4-1","02D01","电磁阀开启状态","风机盘管-电磁阀开启状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"FCU02D01_EVR"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B43*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LFCU02D01_EVR AT%I32.6 :BOOL; (*风机盘管NJ-2AP(KT)4-1-电磁阀开启状态*)"},"LFCU02D01_EVR           AT%I32.6       :BOOL; (*风机盘管NJ-2AP(KT)4-1-电磁阀开启状态*)",null,"FCU02D01_EVR","风机盘管NJ-2AP(KT)4-1-电磁阀开启状态",10262]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","风机盘管NJ-2AP(KT)4-1-电磁阀自动状态",{"$nulls":16},"NJ-2AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-2AP(KT)4-1","02D01","电磁阀自动状态","风机盘管-电磁阀自动状态",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"FCU02D01_EVA"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B43*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LFCU02D01_EVA AT%I32.7 :BOOL; (*风机盘管NJ-2AP(KT)4-1-电磁阀自动状态*)"},"LFCU02D01_EVA           AT%I32.7       :BOOL; (*风机盘管NJ-2AP(KT)4-1-电磁阀自动状态*)",null,"FCU02D01_EVA","风机盘管NJ-2AP(KT)4-1-电磁阀自动状态",10263]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B55&\"地址: \"&B52&\" *)\"","v":"(* IOM 1601D地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH51&AA51&\"-\"&AK51","v":"空调机组NJ-2AP(KT)4-1-启停控制"},{"$nulls":16},{"$f":"IF(AI51=\"\",\"\",AI51)","v":"NJ-2AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-1","02D01","启停控制",{"$f":"AH51&\"-\"&AK51","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"AHU02D01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%Q\"&B52*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LAHU02D01_C AT%Q48.0 :BOOL; (*空调机组NJ-2AP(KT)4-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN51,SEARCH(\"AT%\",AN51),,REPT(\" \",25-SEARCH(\"AT%\",AN51))),SEARCH(\":\",REPLACE(AN51,SEARCH(\"AT%\",AN51),,REPT(\" \",25-SEARCH(\"AT%\",AN51)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN51,SEARCH(\"AT%\",AN51),,REPT(\" \",25-SEARCH(\"AT%\",AN51)))))),\" \")","v":"LAHU02D01_C             AT%Q48.0       :BOOL; (*空调机组NJ-2AP(KT)4-1-启停控制*)"},null,{"$f":"AM51","v":"AHU02D01_C"},{"$f":"J51","v":"空调机组NJ-2AP(KT)4-1-启停控制"},{"$f":"($B52*16*8+F51-1)","v":384}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-2AP(KT)4-2-启停控制",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-2AP(KT)4-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-2","02D02","启停控制",{"$f":"AH52&\"-\"&AK52","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"AHU02D02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%Q\"&B52*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LAHU02D02_C AT%Q48.1 :BOOL; (*空调机组NJ-2AP(KT)4-2-启停控制*)"},"LAHU02D02_C             AT%Q48.1       :BOOL; (*空调机组NJ-2AP(KT)4-2-启停控制*)",null,"AHU02D02_C",{"$f":"J52","v":"空调机组NJ-2AP(KT)4-2-启停控制"},{"$f":"AS51+1","v":385}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","空调机组NJ-2AP(KT)4-3-启停控制",{"$nulls":16},"NJ-2AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-3","02D03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"AHU02D03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%Q\"&B52*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LAHU02D03_C AT%Q48.2 :BOOL; (*空调机组NJ-2AP(KT)4-3-启停控制*)"},"LAHU02D03_C             AT%Q48.2       :BOOL; (*空调机组NJ-2AP(KT)4-3-启停控制*)",null,"AHU02D03_C","空调机组NJ-2AP(KT)4-3-启停控制",{"$f":"AS52+1","v":386}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","空调机组NJ-2AP(KT)4-4-启停控制",{"$nulls":16},"NJ-2AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-4","02D04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"AHU02D04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%Q\"&B52*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LAHU02D04_C AT%Q48.3 :BOOL; (*空调机组NJ-2AP(KT)4-4-启停控制*)"},"LAHU02D04_C             AT%Q48.3       :BOOL; (*空调机组NJ-2AP(KT)4-4-启停控制*)",null,"AHU02D04_C","空调机组NJ-2AP(KT)4-4-启停控制",387]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-2AP(KT)4-5-启停控制",{"$nulls":16},"NJ-2AP(KT)4-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-5","02D05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"AHU02D05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%Q\"&B52*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LAHU02D05_C AT%Q48.4 :BOOL; (*空调机组NJ-2AP(KT)4-5-启停控制*)"},"LAHU02D05_C             AT%Q48.4       :BOOL; (*空调机组NJ-2AP(KT)4-5-启停控制*)",null,"AHU02D05_C","空调机组NJ-2AP(KT)4-5-启停控制",388]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-2AP(KT)4-6-启停控制",{"$nulls":16},"NJ-2AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-6","02D06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"AHU02D06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%Q\"&B52*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LAHU02D06_C AT%Q48.5 :BOOL; (*空调机组NJ-2AP(KT)4-6-启停控制*)"},"LAHU02D06_C             AT%Q48.5       :BOOL; (*空调机组NJ-2AP(KT)4-6-启停控制*)",null,"AHU02D06_C","空调机组NJ-2AP(KT)4-6-启停控制",389]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","照明控制箱NJ-2AL4-1-启停控制",{"$nulls":16},"NJ-2AL4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-1","02D01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"LCB02D01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%Q\"&B52*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LLCB02D01_C AT%Q48.6 :BOOL; (*照明控制箱NJ-2AL4-1-启停控制*)"},"LLCB02D01_C             AT%Q48.6       :BOOL; (*照明控制箱NJ-2AL4-1-启停控制*)",null,"LCB02D01_C","照明控制箱NJ-2AL4-1-启停控制",390]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-2AL4-2-启停控制",{"$nulls":16},"NJ-2AL4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-2","02D02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":"LCB02D02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%Q\"&B52*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":"LLCB02D02_C AT%Q48.7 :BOOL; (*照明控制箱NJ-2AL4-2-启停控制*)"},"LLCB02D02_C             AT%Q48.7       :BOOL; (*照明控制箱NJ-2AL4-2-启停控制*)",null,"LCB02D02_C","照明控制箱NJ-2AL4-2-启停控制",391]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-2AL4-3-启停控制",{"$nulls":16},"NJ-2AL4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-3","02D03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH59,List!$B$3:$D$445,2,FALSE)&AJ59&\"_\"&VLOOKUP(AK59,List!$K$2:$M$447,2,FALSE)","v":"LCB02D03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM59&\" \"&\"AT%Q\"&B52*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J59&\"*)\",\" \")","v":"LLCB02D03_C AT%Q49.0 :BOOL; (*照明控制箱NJ-2AL4-3-启停控制*)"},"LLCB02D03_C             AT%Q49.0       :BOOL; (*照明控制箱NJ-2AL4-3-启停控制*)",null,"LCB02D03_C","照明控制箱NJ-2AL4-3-启停控制",392]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-2AL4-4-启停控制",{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-2AL4-4"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-4","02D04","启停控制",{"$f":"AH60&\"-\"&AK60","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"LCB02D04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%Q\"&B52*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LLCB02D04_C AT%Q49.1 :BOOL; (*照明控制箱NJ-2AL4-4-启停控制*)"},"LLCB02D04_C             AT%Q49.1       :BOOL; (*照明控制箱NJ-2AL4-4-启停控制*)",null,"LCB02D04_C",{"$f":"J60","v":"照明控制箱NJ-2AL4-4-启停控制"},393]
[{"$nulls":5},11,null,"11+","11-","照明控制箱NJ-2AL4-5-启停控制",{"$nulls":16},"NJ-2AL4-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-5","02D05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"LCB02D05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%Q\"&B52*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LLCB02D05_C AT%Q49.2 :BOOL; (*照明控制箱NJ-2AL4-5-启停控制*)"},"LLCB02D05_C             AT%Q49.2       :BOOL; (*照明控制箱NJ-2AL4-5-启停控制*)",null,"LCB02D05_C","照明控制箱NJ-2AL4-5-启停控制",394]
[{"$nulls":5},12,null,"12+","12-","照明控制箱NJ-2AL4-6-启停控制",{"$nulls":16},"NJ-2AL4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL4-6","02D06","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"LCB02D06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%Q\"&B52*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LLCB02D06_C AT%Q49.3 :BOOL; (*照明控制箱NJ-2AL4-6-启停控制*)"},"LLCB02D06_C             AT%Q49.3       :BOOL; (*照明控制箱NJ-2AL4-6-启停控制*)",null,"LCB02D06_C","照明控制箱NJ-2AL4-6-启停控制",395]
[{"$nulls":5},13,null,"13+","13-","风机盘管NJ-2AP(KT)4-1-启停控制",{"$nulls":16},"NJ-2AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-2AP(KT)4-1","02D01","启停控制","风机盘管-启停控制",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"FCU02D01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%Q\"&B52*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LFCU02D01_C AT%Q49.4 :BOOL; (*风机盘管NJ-2AP(KT)4-1-启停控制*)"},"LFCU02D01_C             AT%Q49.4       :BOOL; (*风机盘管NJ-2AP(KT)4-1-启停控制*)",null,"FCU02D01_C","风机盘管NJ-2AP(KT)4-1-启停控制",396]
[{"$nulls":5},14,null,"14+","14-","风机盘管NJ-2AP(KT)4-1-电磁阀开关控制",{"$nulls":16},"NJ-2AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-2AP(KT)4-1","02D01","电磁阀开关控制","风机盘管-电磁阀开关控制",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"FCU02D01_EVC"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%Q\"&B52*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LFCU02D01_EVC AT%Q49.5 :BOOL; (*风机盘管NJ-2AP(KT)4-1-电磁阀开关控制*)"},"LFCU02D01_EVC           AT%Q49.5       :BOOL; (*风机盘管NJ-2AP(KT)4-1-电磁阀开关控制*)",null,"FCU02D01_EVC","风机盘管NJ-2AP(KT)4-1-电磁阀开关控制",397]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%Q\"&B52*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",398]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%Q\"&B52*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",399]
[null,{"$f":"B72","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B72&\"地址: \"&B69&\" *)\"","v":"(* IOM 0801U地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH68&AA68&\"-\"&AK68","v":"空调机组NJ-2AP(KT)4-1-回风温度"},{"$nulls":16},{"$f":"IF(AI68=\"\",\"\",AI68)","v":"NJ-2AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-1","02D01","回风温度",{"$f":"AH68&\"-\"&AK68","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"AHU02D01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%I\"&B69*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LAHU02D01_RT AT%I64.0 :INT ; (*空调机组NJ-2AP(KT)4-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68))),SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))))),\" \")","v":"LAHU02D01_RT            AT%I64.0       :INT ; (*空调机组NJ-2AP(KT)4-1-回风温度*)"},null,{"$f":"AM68","v":"AHU02D01_RT"},{"$f":"J68","v":"空调机组NJ-2AP(KT)4-1-回风温度"},{"$f":"30000+($B69*8+F68-1)","v":30032}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-2AP(KT)4-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-2AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-1","02D01","水阀反馈",{"$f":"AH69&\"-\"&AK69","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU02D01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%I\"&B69*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU02D01_WVB AT%I66.0 :INT ; (*空调机组NJ-2AP(KT)4-1-水阀反馈*)"},"LAHU02D01_WVB           AT%I66.0       :INT ; (*空调机组NJ-2AP(KT)4-1-水阀反馈*)",null,"AHU02D01_WVB",{"$f":"J69","v":"空调机组NJ-2AP(KT)4-1-水阀反馈"},{"$f":"AS68+1","v":30033}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-2AP(KT)4-2-回风温度",{"$nulls":16},"NJ-2AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-2","02D02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"AHU02D02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%I\"&B69*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LAHU02D02_RT AT%I68.0 :INT ; (*空调机组NJ-2AP(KT)4-2-回风温度*)"},"LAHU02D02_RT            AT%I68.0       :INT ; (*空调机组NJ-2AP(KT)4-2-回风温度*)",null,"AHU02D02_RT","空调机组NJ-2AP(KT)4-2-回风温度",{"$f":"AS69+1","v":30034}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-2AP(KT)4-2-水阀反馈",{"$nulls":16},"NJ-2AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-2","02D02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"AHU02D02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%I\"&B69*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LAHU02D02_WVB AT%I70.0 :INT ; (*空调机组NJ-2AP(KT)4-2-水阀反馈*)"},"LAHU02D02_WVB           AT%I70.0       :INT ; (*空调机组NJ-2AP(KT)4-2-水阀反馈*)",null,"AHU02D02_WVB","空调机组NJ-2AP(KT)4-2-水阀反馈",30035]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-2AP(KT)4-3-回风温度",{"$nulls":16},"NJ-2AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-3","02D03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"AHU02D03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%I\"&B69*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LAHU02D03_RT AT%I72.0 :INT ; (*空调机组NJ-2AP(KT)4-3-回风温度*)"},"LAHU02D03_RT            AT%I72.0       :INT ; (*空调机组NJ-2AP(KT)4-3-回风温度*)",null,"AHU02D03_RT","空调机组NJ-2AP(KT)4-3-回风温度",30036]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-2AP(KT)4-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI73=\"\",\"\",AI73)","v":"NJ-2AP(KT)4-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-3","02D03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"AHU02D03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%I\"&B69*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LAHU02D03_WVB AT%I74.0 :INT ; (*空调机组NJ-2AP(KT)4-3-水阀反馈*)"},"LAHU02D03_WVB           AT%I74.0       :INT ; (*空调机组NJ-2AP(KT)4-3-水阀反馈*)",null,"AHU02D03_WVB",{"$f":"J73","v":"空调机组NJ-2AP(KT)4-3-水阀反馈"},30037]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-2AP(KT)4-4-回风温度",{"$nulls":16},"NJ-2AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-4","02D04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":"AHU02D04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%I\"&B69*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":"LAHU02D04_RT AT%I76.0 :INT ; (*空调机组NJ-2AP(KT)4-4-回风温度*)"},"LAHU02D04_RT            AT%I76.0       :INT ; (*空调机组NJ-2AP(KT)4-4-回风温度*)",null,"AHU02D04_RT","空调机组NJ-2AP(KT)4-4-回风温度",30038]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-2AP(KT)4-4-水阀反馈",{"$nulls":16},"NJ-2AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-4","02D04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":"AHU02D04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%I\"&B69*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":"LAHU02D04_WVB AT%I78.0 :INT ; (*空调机组NJ-2AP(KT)4-4-水阀反馈*)"},"LAHU02D04_WVB           AT%I78.0       :INT ; (*空调机组NJ-2AP(KT)4-4-水阀反馈*)",null,"AHU02D04_WVB","空调机组NJ-2AP(KT)4-4-水阀反馈",30039]
[null,{"$f":"B81","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B81&\"地址: \"&B78&\" *)\"","v":"(* IOM 0801U地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH77&AA77&\"-\"&AK77","v":"空调机组NJ-2AP(KT)4-5-回风温度"},{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-2AP(KT)4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-5","02D05","回风温度",{"$f":"AH77&\"-\"&AK77","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"AHU02D05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%I\"&B78*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LAHU02D05_RT AT%I80.0 :INT ; (*空调机组NJ-2AP(KT)4-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77))),SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))))),\" \")","v":"LAHU02D05_RT            AT%I80.0       :INT ; (*空调机组NJ-2AP(KT)4-5-回风温度*)"},null,{"$f":"AM77","v":"AHU02D05_RT"},{"$f":"J77","v":"空调机组NJ-2AP(KT)4-5-回风温度"},{"$f":"30000+($B78*8+F77-1)","v":30040}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-2AP(KT)4-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-2AP(KT)4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-5","02D05","水阀反馈",{"$f":"AH78&\"-\"&AK78","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU02D05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%I\"&B78*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU02D05_WVB AT%I82.0 :INT ; (*空调机组NJ-2AP(KT)4-5-水阀反馈*)"},"LAHU02D05_WVB           AT%I82.0       :INT ; (*空调机组NJ-2AP(KT)4-5-水阀反馈*)",null,"AHU02D05_WVB",{"$f":"J78","v":"空调机组NJ-2AP(KT)4-5-水阀反馈"},{"$f":"AS77+1","v":30041}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-2AP(KT)4-6-回风温度",{"$nulls":16},"NJ-2AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-6","02D06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU02D06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%I\"&B78*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU02D06_RT AT%I84.0 :INT ; (*空调机组NJ-2AP(KT)4-6-回风温度*)"},"LAHU02D06_RT            AT%I84.0       :INT ; (*空调机组NJ-2AP(KT)4-6-回风温度*)",null,"AHU02D06_RT","空调机组NJ-2AP(KT)4-6-回风温度",{"$f":"AS78+1","v":30042}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-2AP(KT)4-6-水阀反馈",{"$nulls":16},"NJ-2AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-6","02D06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU02D06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%I\"&B78*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU02D06_WVB AT%I86.0 :INT ; (*空调机组NJ-2AP(KT)4-6-水阀反馈*)"},"LAHU02D06_WVB           AT%I86.0       :INT ; (*空调机组NJ-2AP(KT)4-6-水阀反馈*)",null,"AHU02D06_WVB","空调机组NJ-2AP(KT)4-6-水阀反馈",30043]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},5,null,5,"0V","风机盘管NJ-2AP(KT)4-1-温度状态",{"$nulls":16},"NJ-2AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-2AP(KT)4-1","02D01","温度状态","风机盘管-温度状态",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"FCU02D01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%I\"&B78*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LFCU02D01_T AT%I88.0 :INT ; (*风机盘管NJ-2AP(KT)4-1-温度状态*)"},"LFCU02D01_T             AT%I88.0       :INT ; (*风机盘管NJ-2AP(KT)4-1-温度状态*)",null,"FCU02D01_T","风机盘管NJ-2AP(KT)4-1-温度状态",30044]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","-",{"$nulls":16},{"$f":"IF(AI82=\"\",\"\",AI82)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%I\"&B78*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J82","v":"-"},30045]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%I\"&B78*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30046]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH84,List!$B$3:$D$445,2,FALSE)&AJ84&\"_\"&VLOOKUP(AK84,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM84&\" \"&\"AT%I\"&B78*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J84&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30047]
[null,{"$f":"B90","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B90&\"地址: \"&B87&\" *)\"","v":"(* IOM 0401A地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH86&AA86&\"-\"&AK86","v":"空调机组NJ-2AP(KT)4-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-2AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-1","02D01","水阀控制",{"$f":"AH86&\"-\"&AK86","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"AHU02D01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%Q\"&B87*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LAHU02D01_WVC AT%Q96.0 :INT ; (*空调机组NJ-2AP(KT)4-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86))),SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))))),\" \")","v":"LAHU02D01_WVC           AT%Q96.0       :INT ; (*空调机组NJ-2AP(KT)4-1-水阀控制*)"},null,{"$f":"AM86","v":"AHU02D01_WVC"},{"$f":"J86","v":"空调机组NJ-2AP(KT)4-1-水阀控制"},{"$f":"40000+($B87*8+F86-1)","v":40048}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH87&AA87&\"-\"&AK87","v":"空调机组NJ-2AP(KT)4-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI87=\"\",\"\",AI87)","v":"NJ-2AP(KT)4-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-2","02D02","水阀控制",{"$f":"AH87&\"-\"&AK87","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"AHU02D02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%Q\"&B87*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LAHU02D02_WVC AT%Q98.0 :INT ; (*空调机组NJ-2AP(KT)4-2-水阀控制*)"},"LAHU02D02_WVC           AT%Q98.0       :INT ; (*空调机组NJ-2AP(KT)4-2-水阀控制*)",null,"AHU02D02_WVC",{"$f":"J87","v":"空调机组NJ-2AP(KT)4-2-水阀控制"},{"$f":"AS86+1","v":40049}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH88&AA88&\"-\"&AK88","v":"空调机组NJ-2AP(KT)4-3-水阀控制"},{"$nulls":16},"NJ-2AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-3","02D03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"AHU02D03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%Q\"&B87*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LAHU02D03_WVC AT%Q100.0 :INT ; (*空调机组NJ-2AP(KT)4-3-水阀控制*)"},"LAHU02D03_WVC           AT%Q100.0      :INT ; (*空调机组NJ-2AP(KT)4-3-水阀控制*)",null,"AHU02D03_WVC","空调机组NJ-2AP(KT)4-3-水阀控制",{"$f":"AS87+1","v":40050}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH89&AA89&\"-\"&AK89","v":"空调机组NJ-2AP(KT)4-4-水阀控制"},{"$nulls":16},"NJ-2AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-4","02D04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"AHU02D04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%Q\"&B87*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LAHU02D04_WVC AT%Q102.0 :INT ; (*空调机组NJ-2AP(KT)4-4-水阀控制*)"},"LAHU02D04_WVC           AT%Q102.0      :INT ; (*空调机组NJ-2AP(KT)4-4-水阀控制*)",null,"AHU02D04_WVC","空调机组NJ-2AP(KT)4-4-水阀控制",40051]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B99","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B99&\"地址: \"&B96&\" *)\"","v":"(* IOM 0401A地址: 7 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH95&AA95&\"-\"&AK95","v":"空调机组NJ-2AP(KT)4-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-2AP(KT)4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-5","02D05","水阀控制",{"$f":"AH95&\"-\"&AK95","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"AHU02D05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%Q\"&B96*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LAHU02D05_WVC AT%Q112.0 :INT ; (*空调机组NJ-2AP(KT)4-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95))),SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))))),\" \")","v":"LAHU02D05_WVC           AT%Q112.0      :INT ; (*空调机组NJ-2AP(KT)4-5-水阀控制*)"},null,{"$f":"AM95","v":"AHU02D05_WVC"},{"$f":"J95","v":"空调机组NJ-2AP(KT)4-5-水阀控制"},{"$f":"40000+($B96*8+F95-1)","v":40056}]
[null,7,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH96&AA96&\"-\"&AK96","v":"空调机组NJ-2AP(KT)4-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI96=\"\",\"\",AI96)","v":"NJ-2AP(KT)4-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)4-6","02D06","水阀控制",{"$f":"AH96&\"-\"&AK96","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"AHU02D06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%Q\"&B96*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LAHU02D06_WVC AT%Q114.0 :INT ; (*空调机组NJ-2AP(KT)4-6-水阀控制*)"},"LAHU02D06_WVC           AT%Q114.0      :INT ; (*空调机组NJ-2AP(KT)4-6-水阀控制*)",null,"AHU02D06_WVC",{"$f":"J96","v":"空调机组NJ-2AP(KT)4-6-水阀控制"},{"$f":"AS95+1","v":40057}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH97&AA97&\"-\"&AK97","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%Q\"&B96*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS96+1","v":40058}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH98&AA98&\"-\"&AK98","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%Q\"&B96*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40059]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L104","index":12,"n_rows":102,"n_cols":45,"rows_kept":102,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[41,5,41,6],[41,9,41,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[92,5,92,6],[92,9,92,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[101,5,101,6],[101,9,101,25],[4,1,5,1],[11,1,22,1],[28,1,39,1],[45,1,48,1],[54,1,65,1],[71,1,74,1],[80,1,83,1],[89,1,92,1],[98,1,101,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4],[32,2,39,4],[58,2,65,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L14",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 8 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH8&AA8&\"-\"&AK8","v":"空调机组NJ-1AP(KT)4-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-1AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-1","01D01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH8,List!$B$3:$D$445,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,List!$K$2:$M$447,2,FALSE)","v":"AHU01D01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LAHU01D01_R AT%I128.0 :BOOL; (*空调机组NJ-1AP(KT)4-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LAHU01D01_R             AT%I128.0      :BOOL; (*空调机组NJ-1AP(KT)4-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L14\\L14AHU01D01_R"},{"$f":"J8","v":"空调机组NJ-1AP(KT)4-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":11024}]
[null,8,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-1AP(KT)4-1-故障状态",{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-1AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-1","01D01","故障状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU01D01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU01D01_F AT%I128.1 :BOOL; (*空调机组NJ-1AP(KT)4-1-故障状态*)"},"LAHU01D01_F             AT%I128.1      :BOOL; (*空调机组NJ-1AP(KT)4-1-故障状态*)",null,"L14\\L14AHU01D01_F",{"$f":"J9","v":"空调机组NJ-1AP(KT)4-1-故障状态"},{"$f":"AS8+1","v":11025}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-1AP(KT)4-1-自动状态",{"$nulls":16},"NJ-1AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-1","01D01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU01D01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU01D01_A AT%I128.2 :BOOL; (*空调机组NJ-1AP(KT)4-1-自动状态*)"},"LAHU01D01_A             AT%I128.2      :BOOL; (*空调机组NJ-1AP(KT)4-1-自动状态*)",null,"L14\\L14AHU01D01_A","空调机组NJ-1AP(KT)4-1-自动状态",{"$f":"AS9+1","v":11026}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-1AP(KT)4-1-风机压差",{"$nulls":16},"NJ-1AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-1","01D01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU01D01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU01D01_FPS AT%I128.3 :BOOL; (*空调机组NJ-1AP(KT)4-1-风机压差*)"},"LAHU01D01_FPS           AT%I128.3      :BOOL; (*空调机组NJ-1AP(KT)4-1-风机压差*)",null,"L14\\L14AHU01D01_FPS","空调机组NJ-1AP(KT)4-1-风机压差",11027]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-1AP(KT)4-1-运行状态",{"$nulls":16},"NJ-1AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-1","01D02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU01D02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU01D02_R AT%I128.4 :BOOL; (*空调机组NJ-1AP(KT)4-1-运行状态*)"},"LAHU01D02_R             AT%I128.4      :BOOL; (*空调机组NJ-1AP(KT)4-1-运行状态*)",null,"L14\\L14AHU01D02_R","空调机组NJ-1AP(KT)4-1-运行状态",11028]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-1AP(KT)4-2-故障状态",{"$nulls":16},"NJ-1AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-2","01D02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU01D02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU01D02_F AT%I128.5 :BOOL; (*空调机组NJ-1AP(KT)4-2-故障状态*)"},"LAHU01D02_F             AT%I128.5      :BOOL; (*空调机组NJ-1AP(KT)4-2-故障状态*)",null,"L14\\L14AHU01D02_F","空调机组NJ-1AP(KT)4-2-故障状态",11029]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-1AP(KT)4-2-自动状态",{"$nulls":16},"NJ-1AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-2","01D02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU01D02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU01D02_A AT%I128.6 :BOOL; (*空调机组NJ-1AP(KT)4-2-自动状态*)"},"LAHU01D02_A             AT%I128.6      :BOOL; (*空调机组NJ-1AP(KT)4-2-自动状态*)",null,"L14\\L14AHU01D02_A","空调机组NJ-1AP(KT)4-2-自动状态",11030]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-1AP(KT)4-2-风机压差",{"$nulls":16},"NJ-1AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-2","01D02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU01D02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU01D02_FPS AT%I128.7 :BOOL; (*空调机组NJ-1AP(KT)4-2-风机压差*)"},"LAHU01D02_FPS           AT%I128.7      :BOOL; (*空调机组NJ-1AP(KT)4-2-风机压差*)",null,"L14\\L14AHU01D02_FPS","空调机组NJ-1AP(KT)4-2-风机压差",11031]
[{"$nulls":5},9,null,17,18,"空调机组NJ-1AP(KT)4-2-运行状态",{"$nulls":16},"NJ-1AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-2","01D03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU01D03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU01D03_R AT%I129.0 :BOOL; (*空调机组NJ-1AP(KT)4-2-运行状态*)"},"LAHU01D03_R             AT%I129.0      :BOOL; (*空调机组NJ-1AP(KT)4-2-运行状态*)",null,"L14\\L14AHU01D03_R","空调机组NJ-1AP(KT)4-2-运行状态",11032]
[{"$nulls":5},10,null,19,20,"空调机组NJ-1AP(KT)4-3-故障状态",{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-1AP(KT)4-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-3","01D03","故障状态",{"$f":"AH17&\"-\"&AK17","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU01D03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU01D03_F AT%I129.1 :BOOL; (*空调机组NJ-1AP(KT)4-3-故障状态*)"},"LAHU01D03_F             AT%I129.1      :BOOL; (*空调机组NJ-1AP(KT)4-3-故障状态*)",null,"L14\\L14AHU01D03_F","空调机组NJ-1AP(KT)4-3-故障状态",11033]
[{"$nulls":5},11,null,21,22,"空调机组NJ-1AP(KT)4-3-自动状态",{"$nulls":16},"NJ-1AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-3","01D03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU01D03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU01D03_A AT%I129.2 :BOOL; (*空调机组NJ-1AP(KT)4-3-自动状态*)"},"LAHU01D03_A             AT%I129.2      :BOOL; (*空调机组NJ-1AP(KT)4-3-自动状态*)",null,"L14\\L14AHU01D03_A","空调机组NJ-1AP(KT)4-3-自动状态",11034]
[{"$nulls":5},12,null,23,24,"空调机组NJ-1AP(KT)4-3-风机压差",{"$nulls":16},"NJ-1AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-3","01D03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU01D03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU01D03_FPS AT%I129.3 :BOOL; (*空调机组NJ-1AP(KT)4-3-风机压差*)"},"LAHU01D03_FPS           AT%I129.3      :BOOL; (*空调机组NJ-1AP(KT)4-3-风机压差*)",null,"L14\\L14AHU01D03_FPS","空调机组NJ-1AP(KT)4-3-风机压差",11035]
[{"$nulls":5},13,null,25,26,"空调机组NJ-1AP(KT)4-4-运行状态",{"$nulls":16},"NJ-1AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-4","01D04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU01D04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU01D04_R AT%I129.4 :BOOL; (*空调机组NJ-1AP(KT)4-4-运行状态*)"},"LAHU01D04_R             AT%I129.4      :BOOL; (*空调机组NJ-1AP(KT)4-4-运行状态*)",null,"L14\\L14AHU01D04_R","空调机组NJ-1AP(KT)4-4-运行状态",11036]
[{"$nulls":5},14,null,27,28,"空调机组NJ-1AP(KT)4-4-故障状态",{"$nulls":16},"NJ-1AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-4","01D04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU01D04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU01D04_F AT%I129.5 :BOOL; (*空调机组NJ-1AP(KT)4-4-故障状态*)"},"LAHU01D04_F             AT%I129.5      :BOOL; (*空调机组NJ-1AP(KT)4-4-故障状态*)",null,"L14\\L14AHU01D04_F","空调机组NJ-1AP(KT)4-4-故障状态",11037]
[{"$nulls":5},15,null,29,30,"空调机组NJ-1AP(KT)4-4-自动状态",{"$nulls":16},"NJ-1AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-4","01D04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU01D04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU01D04_A AT%I129.6 :BOOL; (*空调机组NJ-1AP(KT)4-4-自动状态*)"},"LAHU01D04_A             AT%I129.6      :BOOL; (*空调机组NJ-1AP(KT)4-4-自动状态*)",null,"L14\\L14AHU01D04_A","空调机组NJ-1AP(KT)4-4-自动状态",11038]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-1AP(KT)4-4-风机压差",{"$nulls":16},"NJ-1AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-4","01D04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU01D04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU01D04_FPS AT%I129.7 :BOOL; (*空调机组NJ-1AP(KT)4-4-风机压差*)"},"LAHU01D04_FPS           AT%I129.7      :BOOL; (*空调机组NJ-1AP(KT)4-4-风机压差*)",null,"L14\\L14AHU01D04_FPS","空调机组NJ-1AP(KT)4-4-风机压差",11039]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 1601R地址: 9 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH25&AA25&\"-\"&AK25","v":"空调机组NJ-1AP(KT)4-5-运行状态"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-1AP(KT)4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-5","01D05","运行状态",{"$f":"AH25&\"-\"&AK25","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"AHU01D05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LAHU01D05_R AT%I144.0 :BOOL; (*空调机组NJ-1AP(KT)4-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LAHU01D05_R             AT%I144.0      :BOOL; (*空调机组NJ-1AP(KT)4-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L14\\L14AHU01D05_R"},{"$f":"J25","v":"空调机组NJ-1AP(KT)4-5-运行状态"},{"$f":"10000+($B26*16*8+F25-1)","v":11152}]
[null,9,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-1AP(KT)4-5-故障状态",{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-1AP(KT)4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-5","01D05","故障状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU01D05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU01D05_F AT%I144.1 :BOOL; (*空调机组NJ-1AP(KT)4-5-故障状态*)"},"LAHU01D05_F             AT%I144.1      :BOOL; (*空调机组NJ-1AP(KT)4-5-故障状态*)",null,"L14\\L14AHU01D05_F",{"$f":"J26","v":"空调机组NJ-1AP(KT)4-5-故障状态"},{"$f":"AS25+1","v":11153}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-1AP(KT)4-5-自动状态",{"$nulls":16},"NJ-1AP(KT)4-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-5","01D05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU01D05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU01D05_A AT%I144.2 :BOOL; (*空调机组NJ-1AP(KT)4-5-自动状态*)"},"LAHU01D05_A             AT%I144.2      :BOOL; (*空调机组NJ-1AP(KT)4-5-自动状态*)",null,"L14\\L14AHU01D05_A","空调机组NJ-1AP(KT)4-5-自动状态",{"$f":"AS26+1","v":11154}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-1AP(KT)4-5-风机压差",{"$nulls":16},"NJ-1AP(KT)4-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-5","01D05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU01D05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU01D05_FPS AT%I144.3 :BOOL; (*空调机组NJ-1AP(KT)4-5-风机压差*)"},"LAHU01D05_FPS           AT%I144.3      :BOOL; (*空调机组NJ-1AP(KT)4-5-风机压差*)",null,"L14\\L14AHU01D05_FPS","空调机组NJ-1AP(KT)4-5-风机压差",11155]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-1AP(KT)4-6-运行状态",{"$nulls":16},"NJ-1AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-6","01D06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU01D06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU01D06_R AT%I144.4 :BOOL; (*空调机组NJ-1AP(KT)4-6-运行状态*)"},"LAHU01D06_R             AT%I144.4      :BOOL; (*空调机组NJ-1AP(KT)4-6-运行状态*)",null,"L14\\L14AHU01D06_R","空调机组NJ-1AP(KT)4-6-运行状态",11156]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-1AP(KT)4-6-故障状态",{"$nulls":16},"NJ-1AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-6","01D06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU01D06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU01D06_F AT%I144.5 :BOOL; (*空调机组NJ-1AP(KT)4-6-故障状态*)"},"LAHU01D06_F             AT%I144.5      :BOOL; (*空调机组NJ-1AP(KT)4-6-故障状态*)",null,"L14\\L14AHU01D06_F","空调机组NJ-1AP(KT)4-6-故障状态",11157]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-1AP(KT)4-6-自动状态",{"$nulls":16},"NJ-1AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-6","01D06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU01D06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU01D06_A AT%I144.6 :BOOL; (*空调机组NJ-1AP(KT)4-6-自动状态*)"},"LAHU01D06_A             AT%I144.6      :BOOL; (*空调机组NJ-1AP(KT)4-6-自动状态*)",null,"L14\\L14AHU01D06_A","空调机组NJ-1AP(KT)4-6-自动状态",11158]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-1AP(KT)4-6-风机压差",{"$nulls":16},"NJ-1AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-6","01D06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU01D06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU01D06_FPS AT%I144.7 :BOOL; (*空调机组NJ-1AP(KT)4-6-风机压差*)"},"LAHU01D06_FPS           AT%I144.7      :BOOL; (*空调机组NJ-1AP(KT)4-6-风机压差*)",null,"L14\\L14AHU01D06_FPS","空调机组NJ-1AP(KT)4-6-风机压差",11159]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-1AL4-1-运行状态",{"$nulls":16},"NJ-1AL4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL4-1","01D01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"LCB01D01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B26*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LLCB01D01_R AT%I145.0 :BOOL; (*照明控制箱NJ-1AL4-1-运行状态*)"},"LLCB01D01_R             AT%I145.0      :BOOL; (*照明控制箱NJ-1AL4-1-运行状态*)",null,"L14\\L14LCB01D01_R","照明控制箱NJ-1AL4-1-运行状态",11160]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-1AL4-1-自动状态",{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-1AL4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL4-1","01D01","自动状态",{"$f":"AH34&\"-\"&AK34","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"LCB01D01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B26*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LLCB01D01_A AT%I145.1 :BOOL; (*照明控制箱NJ-1AL4-1-自动状态*)"},"LLCB01D01_A             AT%I145.1      :BOOL; (*照明控制箱NJ-1AL4-1-自动状态*)",null,"L14\\L14LCB01D01_A","照明控制箱NJ-1AL4-1-自动状态",11161]
[{"$nulls":5},11,null,21,22,"照明控制箱NJ-1AL4-2-运行状态",{"$nulls":16},"NJ-1AL4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL4-2","01D02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"LCB01D02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B26*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LLCB01D02_R AT%I145.2 :BOOL; (*照明控制箱NJ-1AL4-2-运行状态*)"},"LLCB01D02_R             AT%I145.2      :BOOL; (*照明控制箱NJ-1AL4-2-运行状态*)",null,"L14\\L14LCB01D02_R","照明控制箱NJ-1AL4-2-运行状态",11162]
[{"$nulls":5},12,null,23,24,"照明控制箱NJ-1AL4-2-自动状态",{"$nulls":16},"NJ-1AL4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL4-2","01D02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"LCB01D02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B26*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LLCB01D02_A AT%I145.3 :BOOL; (*照明控制箱NJ-1AL4-2-自动状态*)"},"LLCB01D02_A             AT%I145.3      :BOOL; (*照明控制箱NJ-1AL4-2-自动状态*)",null,"L14\\L14LCB01D02_A","照明控制箱NJ-1AL4-2-自动状态",11163]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-1AL4-3-运行状态",{"$nulls":16},"NJ-1AL4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL4-3","01D03","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"LCB01D03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B26*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LLCB01D03_R AT%I145.4 :BOOL; (*照明控制箱NJ-1AL4-3-运行状态*)"},"LLCB01D03_R             AT%I145.4      :BOOL; (*照明控制箱NJ-1AL4-3-运行状态*)",null,"L14\\L14LCB01D03_R","照明控制箱NJ-1AL4-3-运行状态",11164]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-1AL4-3-自动状态",{"$nulls":16},"NJ-1AL4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL4-3","01D03","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB01D03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B26*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB01D03_A AT%I145.5 :BOOL; (*照明控制箱NJ-1AL4-3-自动状态*)"},"LLCB01D03_A             AT%I145.5      :BOOL; (*照明控制箱NJ-1AL4-3-自动状态*)",null,"L14\\L14LCB01D03_A","照明控制箱NJ-1AL4-3-自动状态",11165]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-1AL4-4-运行状态",{"$nulls":16},"NJ-1AL4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL4-4","01D04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB01D04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B26*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB01D04_R AT%I145.6 :BOOL; (*照明控制箱NJ-1AL4-4-运行状态*)"},"LLCB01D04_R             AT%I145.6      :BOOL; (*照明控制箱NJ-1AL4-4-运行状态*)",null,"L14\\L14LCB01D04_R","照明控制箱NJ-1AL4-4-运行状态",11166]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-1AL4-4-自动状态",{"$nulls":16},"NJ-1AL4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL4-4","01D04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"LCB01D04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B26*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LLCB01D04_A AT%I145.7 :BOOL; (*照明控制箱NJ-1AL4-4-自动状态*)"},"LLCB01D04_A             AT%I145.7      :BOOL; (*照明控制箱NJ-1AL4-4-自动状态*)",null,"L14\\L14LCB01D04_A","照明控制箱NJ-1AL4-4-自动状态",11167]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B46&\"地址: \"&B43&\" *)\"","v":"(* IOM 0801R 地址: 10 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH42&AA42&\"-\"&AK42","v":"水幕机NJ-1AP(KT)4-1-运行状态"},{"$nulls":16},{"$f":"IF(AI42=\"\",\"\",AI42)","v":"NJ-1AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)4-1","01D01","运行状态",{"$f":"AH42&\"-\"&AK42","v":"水幕机-运行状态"},{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":"WAC01D01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%I\"&B43*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":"LWAC01D01_R AT%I160.0 :BOOL; (*水幕机NJ-1AP(KT)4-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42))),SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))))),\" \")","v":"LWAC01D01_R             AT%I160.0      :BOOL; (*水幕机NJ-1AP(KT)4-1-运行状态*)"},null,{"$f":"AM42","v":"WAC01D01_R"},{"$f":"J42","v":"水幕机NJ-1AP(KT)4-1-运行状态"},{"$f":"10000+($B43*16*8+F42-1)","v":11280}]
[null,10,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},2,null,2,"C",{"$f":"AH43&AA43&\"-\"&AK43","v":"水幕机NJ-1AP(KT)4-1-故障状态"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-1AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)4-1","01D01","故障状态",{"$f":"AH43&\"-\"&AK43","v":"水幕机-故障状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"WAC01D01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B43*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LWAC01D01_F AT%I160.1 :BOOL; (*水幕机NJ-1AP(KT)4-1-故障状态*)"},"LWAC01D01_F             AT%I160.1      :BOOL; (*水幕机NJ-1AP(KT)4-1-故障状态*)",null,{"$f":"AM43","v":"WAC01D01_F"},{"$f":"J43","v":"水幕机NJ-1AP(KT)4-1-故障状态"},{"$f":"AS42+1","v":11281}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":0},3,null,3,"C",{"$f":"AH44&AA44&\"-\"&AK44","v":"水幕机NJ-1AP(KT)4-1-自动状态"},{"$nulls":16},"NJ-1AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)4-1","01D01","自动状态","水幕机-自动状态",{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"WAC01D01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B43*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LWAC01D01_A AT%I160.2 :BOOL; (*水幕机NJ-1AP(KT)4-1-自动状态*)"},"LWAC01D01_A             AT%I160.2      :BOOL; (*水幕机NJ-1AP(KT)4-1-自动状态*)",null,"WAC01D01_A","水幕机NJ-1AP(KT)4-1-自动状态",{"$f":"AS43+1","v":11282}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},4,null,4,"C",{"$f":"AH45&AA45&\"-\"&AK45","v":"水幕机NJ-1AP(KT)4-2-运行状态"},{"$nulls":16},"NJ-1AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)4-2","01D02","运行状态","水幕机-运行状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"WAC01D02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B43*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LWAC01D02_R AT%I160.3 :BOOL; (*水幕机NJ-1AP(KT)4-2-运行状态*)"},"LWAC01D02_R             AT%I160.3      :BOOL; (*水幕机NJ-1AP(KT)4-2-运行状态*)",null,"WAC01D02_R","水幕机NJ-1AP(KT)4-2-运行状态",11283]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},5,null,5,"C","水幕机NJ-1AP(KT)4-2-故障状态",{"$nulls":16},"NJ-1AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)4-2","01D02","故障状态","水幕机-故障状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"WAC01D02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B43*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LWAC01D02_F AT%I160.4 :BOOL; (*水幕机NJ-1AP(KT)4-2-故障状态*)"},"LWAC01D02_F             AT%I160.4      :BOOL; (*水幕机NJ-1AP(KT)4-2-故障状态*)",null,"WAC01D02_F","水幕机NJ-1AP(KT)4-2-故障状态",11284]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","水幕机NJ-1AP(KT)4-2-自动状态",{"$nulls":16},"NJ-1AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)4-2","01D02","自动状态","水幕机-自动状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"WAC01D02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B43*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LWAC01D02_A AT%I160.5 :BOOL; (*水幕机NJ-1AP(KT)4-2-自动状态*)"},"LWAC01D02_A             AT%I160.5      :BOOL; (*水幕机NJ-1AP(KT)4-2-自动状态*)",null,"WAC01D02_A","水幕机NJ-1AP(KT)4-2-自动状态",11285]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","水幕机NJ-1AP(KT)4-1-水阀开反馈",{"$nulls":16},"NJ-1AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)4-1","01D01","水阀开反馈","水幕机-水阀开反馈",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"WAC01D01_WVOB"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B43*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LWAC01D01_WVOB AT%I160.6 :BOOL; (*水幕机NJ-1AP(KT)4-1-水阀开反馈*)"},"LWAC01D01_WVOB          AT%I160.6      :BOOL; (*水幕机NJ-1AP(KT)4-1-水阀开反馈*)",null,"WAC01D01_WVOB","水幕机NJ-1AP(KT)4-1-水阀开反馈",11286]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","水幕机NJ-1AP(KT)4-1-水阀关反馈",{"$nulls":16},"NJ-1AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)4-1","01D01","水阀关反馈","水幕机-水阀关反馈",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"WAC01D01_WVSB"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B43*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LWAC01D01_WVSB AT%I160.7 :BOOL; (*水幕机NJ-1AP(KT)4-1-水阀关反馈*)"},"LWAC01D01_WVSB          AT%I160.7      :BOOL; (*水幕机NJ-1AP(KT)4-1-水阀关反馈*)",null,"WAC01D01_WVSB","水幕机NJ-1AP(KT)4-1-水阀关反馈",11287]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B55&\"地址: \"&B52&\" *)\"","v":"(* IOM 1601D地址: 11 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH51&AA51&\"-\"&AK51","v":"空调机组NJ-1AP(KT)4-1-启停控制"},{"$nulls":16},{"$f":"IF(AI51=\"\",\"\",AI51)","v":"NJ-1AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-1","01D01","启停控制",{"$f":"AH51&\"-\"&AK51","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"AHU01D01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%Q\"&B52*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LAHU01D01_C AT%Q176.0 :BOOL; (*空调机组NJ-1AP(KT)4-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN51,SEARCH(\"AT%\",AN51),,REPT(\" \",25-SEARCH(\"AT%\",AN51))),SEARCH(\":\",REPLACE(AN51,SEARCH(\"AT%\",AN51),,REPT(\" \",25-SEARCH(\"AT%\",AN51)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN51,SEARCH(\"AT%\",AN51),,REPT(\" \",25-SEARCH(\"AT%\",AN51)))))),\" \")","v":"LAHU01D01_C             AT%Q176.0      :BOOL; (*空调机组NJ-1AP(KT)4-1-启停控制*)"},null,{"$f":"AM51","v":"AHU01D01_C"},{"$f":"J51","v":"空调机组NJ-1AP(KT)4-1-启停控制"},{"$f":"($B52*16*8+F51-1)","v":1408}]
[null,11,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-1AP(KT)4-2-启停控制",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-1AP(KT)4-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-2","01D02","启停控制",{"$f":"AH52&\"-\"&AK52","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"AHU01D02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%Q\"&B52*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LAHU01D02_C AT%Q176.1 :BOOL; (*空调机组NJ-1AP(KT)4-2-启停控制*)"},"LAHU01D02_C             AT%Q176.1      :BOOL; (*空调机组NJ-1AP(KT)4-2-启停控制*)",null,"AHU01D02_C",{"$f":"J52","v":"空调机组NJ-1AP(KT)4-2-启停控制"},{"$f":"AS51+1","v":1409}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","空调机组NJ-1AP(KT)4-3-启停控制",{"$nulls":16},"NJ-1AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-3","01D03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"AHU01D03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%Q\"&B52*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LAHU01D03_C AT%Q176.2 :BOOL; (*空调机组NJ-1AP(KT)4-3-启停控制*)"},"LAHU01D03_C             AT%Q176.2      :BOOL; (*空调机组NJ-1AP(KT)4-3-启停控制*)",null,"AHU01D03_C","空调机组NJ-1AP(KT)4-3-启停控制",{"$f":"AS52+1","v":1410}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","空调机组NJ-1AP(KT)4-4-启停控制",{"$nulls":16},"NJ-1AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-4","01D04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"AHU01D04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%Q\"&B52*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LAHU01D04_C AT%Q176.3 :BOOL; (*空调机组NJ-1AP(KT)4-4-启停控制*)"},"LAHU01D04_C             AT%Q176.3      :BOOL; (*空调机组NJ-1AP(KT)4-4-启停控制*)",null,"AHU01D04_C","空调机组NJ-1AP(KT)4-4-启停控制",1411]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-1AP(KT)4-5-启停控制",{"$nulls":16},"NJ-1AP(KT)4-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-5","01D05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"AHU01D05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%Q\"&B52*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LAHU01D05_C AT%Q176.4 :BOOL; (*空调机组NJ-1AP(KT)4-5-启停控制*)"},"LAHU01D05_C             AT%Q176.4      :BOOL; (*空调机组NJ-1AP(KT)4-5-启停控制*)",null,"AHU01D05_C","空调机组NJ-1AP(KT)4-5-启停控制",1412]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-1AP(KT)4-6-启停控制",{"$nulls":16},"NJ-1AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-6","01D06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"AHU01D06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%Q\"&B52*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LAHU01D06_C AT%Q176.5 :BOOL; (*空调机组NJ-1AP(KT)4-6-启停控制*)"},"LAHU01D06_C             AT%Q176.5      :BOOL; (*空调机组NJ-1AP(KT)4-6-启停控制*)",null,"AHU01D06_C","空调机组NJ-1AP(KT)4-6-启停控制",1413]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","照明控制箱NJ-1AL4-1-启停控制",{"$nulls":16},"NJ-1AL4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL4-1","01D01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"LCB01D01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%Q\"&B52*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LLCB01D01_C AT%Q176.6 :BOOL; (*照明控制箱NJ-1AL4-1-启停控制*)"},"LLCB01D01_C             AT%Q176.6      :BOOL; (*照明控制箱NJ-1AL4-1-启停控制*)",null,"LCB01D01_C","照明控制箱NJ-1AL4-1-启停控制",1414]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-1AL4-2-启停控制",{"$nulls":16},"NJ-1AL4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL4-2","01D02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":"LCB01D02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%Q\"&B52*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":"LLCB01D02_C AT%Q176.7 :BOOL; (*照明控制箱NJ-1AL4-2-启停控制*)"},"LLCB01D02_C             AT%Q176.7      :BOOL; (*照明控制箱NJ-1AL4-2-启停控制*)",null,"LCB01D02_C","照明控制箱NJ-1AL4-2-启停控制",1415]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-1AL4-3-启停控制",{"$nulls":16},"NJ-1AL4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL4-3","01D03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH59,List!$B$3:$D$445,2,FALSE)&AJ59&\"_\"&VLOOKUP(AK59,List!$K$2:$M$447,2,FALSE)","v":"LCB01D03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM59&\" \"&\"AT%Q\"&B52*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J59&\"*)\",\" \")","v":"LLCB01D03_C AT%Q177.0 :BOOL; (*照明控制箱NJ-1AL4-3-启停控制*)"},"LLCB01D03_C             AT%Q177.0      :BOOL; (*照明控制箱NJ-1AL4-3-启停控制*)",null,"LCB01D03_C","照明控制箱NJ-1AL4-3-启停控制",1416]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-1AL4-4-启停控制",{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-1AL4-4"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL4-4","01D04","启停控制",{"$f":"AH60&\"-\"&AK60","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"LCB01D04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%Q\"&B52*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LLCB01D04_C AT%Q177.1 :BOOL; (*照明控制箱NJ-1AL4-4-启停控制*)"},"LLCB01D04_C             AT%Q177.1      :BOOL; (*照明控制箱NJ-1AL4-4-启停控制*)",null,"LCB01D04_C",{"$f":"J60","v":"照明控制箱NJ-1AL4-4-启停控制"},1417]
[{"$nulls":5},11,null,"11+","11-","水幕机NJ-1AP(KT)4-1-启停控制",{"$nulls":16},"NJ-1AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)4-1","01D01","启停控制","水幕机-启停控制",{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"WAC01D01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%Q\"&B52*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LWAC01D01_C AT%Q177.2 :BOOL; (*水幕机NJ-1AP(KT)4-1-启停控制*)"},"LWAC01D01_C             AT%Q177.2      :BOOL; (*水幕机NJ-1AP(KT)4-1-启停控制*)",null,"WAC01D01_C","水幕机NJ-1AP(KT)4-1-启停控制",1418]
[{"$nulls":5},12,null,"12+","12-","水幕机NJ-1AP(KT)4-2-启停控制",{"$nulls":16},"NJ-1AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)4-2","01D02","启停控制","水幕机-启停控制",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"WAC01D02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%Q\"&B52*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LWAC01D02_C AT%Q177.3 :BOOL; (*水幕机NJ-1AP(KT)4-2-启停控制*)"},"LWAC01D02_C             AT%Q177.3      :BOOL; (*水幕机NJ-1AP(KT)4-2-启停控制*)",null,"WAC01D02_C","水幕机NJ-1AP(KT)4-2-启停控制",1419]
[{"$nulls":5},13,null,"13+","13-","水幕机NJ-1AP(KT)4-1-水阀控制",{"$nulls":16},"NJ-1AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)4-1","01D01","水阀控制","水幕机-水阀控制",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"WAC01D01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%Q\"&B52*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LWAC01D01_WVC AT%Q177.4 :BOOL; (*水幕机NJ-1AP(KT)4-1-水阀控制*)"},"LWAC01D01_WVC           AT%Q177.4      :BOOL; (*水幕机NJ-1AP(KT)4-1-水阀控制*)",null,"WAC01D01_WVC","水幕机NJ-1AP(KT)4-1-水阀控制",1420]
[{"$nulls":5},14,null,"14+","14-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%Q\"&B52*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1421]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%Q\"&B52*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1422]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%Q\"&B52*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1423]
[null,{"$f":"B72","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B72&\"地址: \"&B69&\" *)\"","v":"(* IOM 0801U地址: 12 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH68&AA68&\"-\"&AK68","v":"空调机组NJ-1AP(KT)4-1-回风温度"},{"$nulls":16},{"$f":"IF(AI68=\"\",\"\",AI68)","v":"NJ-1AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-1","01D01","回风温度",{"$f":"AH68&\"-\"&AK68","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"AHU01D01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%I\"&B69*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LAHU01D01_RT AT%I192.0 :INT ; (*空调机组NJ-1AP(KT)4-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68))),SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))))),\" \")","v":"LAHU01D01_RT            AT%I192.0      :INT ; (*空调机组NJ-1AP(KT)4-1-回风温度*)"},null,{"$f":"AM68","v":"AHU01D01_RT"},{"$f":"J68","v":"空调机组NJ-1AP(KT)4-1-回风温度"},{"$f":"30000+($B69*8+F68-1)","v":30096}]
[null,12,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-1AP(KT)4-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-1AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-1","01D01","水阀反馈",{"$f":"AH69&\"-\"&AK69","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU01D01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%I\"&B69*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU01D01_WVB AT%I194.0 :INT ; (*空调机组NJ-1AP(KT)4-1-水阀反馈*)"},"LAHU01D01_WVB           AT%I194.0      :INT ; (*空调机组NJ-1AP(KT)4-1-水阀反馈*)",null,"AHU01D01_WVB",{"$f":"J69","v":"空调机组NJ-1AP(KT)4-1-水阀反馈"},{"$f":"AS68+1","v":30097}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-1AP(KT)4-2-回风温度",{"$nulls":16},"NJ-1AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-2","01D02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"AHU01D02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%I\"&B69*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LAHU01D02_RT AT%I196.0 :INT ; (*空调机组NJ-1AP(KT)4-2-回风温度*)"},"LAHU01D02_RT            AT%I196.0      :INT ; (*空调机组NJ-1AP(KT)4-2-回风温度*)",null,"AHU01D02_RT","空调机组NJ-1AP(KT)4-2-回风温度",{"$f":"AS69+1","v":30098}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-1AP(KT)4-2-水阀反馈",{"$nulls":16},"NJ-1AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-2","01D02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"AHU01D02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%I\"&B69*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LAHU01D02_WVB AT%I198.0 :INT ; (*空调机组NJ-1AP(KT)4-2-水阀反馈*)"},"LAHU01D02_WVB           AT%I198.0      :INT ; (*空调机组NJ-1AP(KT)4-2-水阀反馈*)",null,"AHU01D02_WVB","空调机组NJ-1AP(KT)4-2-水阀反馈",30099]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-1AP(KT)4-3-回风温度",{"$nulls":16},"NJ-1AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-3","01D03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"AHU01D03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%I\"&B69*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LAHU01D03_RT AT%I200.0 :INT ; (*空调机组NJ-1AP(KT)4-3-回风温度*)"},"LAHU01D03_RT            AT%I200.0      :INT ; (*空调机组NJ-1AP(KT)4-3-回风温度*)",null,"AHU01D03_RT","空调机组NJ-1AP(KT)4-3-回风温度",30100]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-1AP(KT)4-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI73=\"\",\"\",AI73)","v":"NJ-1AP(KT)4-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-3","01D03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"AHU01D03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%I\"&B69*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LAHU01D03_WVB AT%I202.0 :INT ; (*空调机组NJ-1AP(KT)4-3-水阀反馈*)"},"LAHU01D03_WVB           AT%I202.0      :INT ; (*空调机组NJ-1AP(KT)4-3-水阀反馈*)",null,"AHU01D03_WVB",{"$f":"J73","v":"空调机组NJ-1AP(KT)4-3-水阀反馈"},30101]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-1AP(KT)4-4-回风温度",{"$nulls":16},"NJ-1AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-4","01D04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":"AHU01D04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%I\"&B69*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":"LAHU01D04_RT AT%I204.0 :INT ; (*空调机组NJ-1AP(KT)4-4-回风温度*)"},"LAHU01D04_RT            AT%I204.0      :INT ; (*空调机组NJ-1AP(KT)4-4-回风温度*)",null,"AHU01D04_RT","空调机组NJ-1AP(KT)4-4-回风温度",30102]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-1AP(KT)4-4-水阀反馈",{"$nulls":16},"NJ-1AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-4","01D04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":"AHU01D04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%I\"&B69*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":"LAHU01D04_WVB AT%I206.0 :INT ; (*空调机组NJ-1AP(KT)4-4-水阀反馈*)"},"LAHU01D04_WVB           AT%I206.0      :INT ; (*空调机组NJ-1AP(KT)4-4-水阀反馈*)",null,"AHU01D04_WVB","空调机组NJ-1AP(KT)4-4-水阀反馈",30103]
[null,{"$f":"B81","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B81&\"地址: \"&B78&\" *)\"","v":"(* IOM 0401U地址: 13 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH77&AA77&\"-\"&AK77","v":"空调机组NJ-1AP(KT)4-5-回风温度"},{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-1AP(KT)4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-5","01D05","回风温度",{"$f":"AH77&\"-\"&AK77","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"AHU01D05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%I\"&B78*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LAHU01D05_RT AT%I208.0 :INT ; (*空调机组NJ-1AP(KT)4-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77))),SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))))),\" \")","v":"LAHU01D05_RT            AT%I208.0      :INT ; (*空调机组NJ-1AP(KT)4-5-回风温度*)"},null,"AHU01D05_RT",{"$f":"J77","v":"空调机组NJ-1AP(KT)4-5-回风温度"},{"$f":"30000+($B78*8+F77-1)","v":30104}]
[null,13,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-1AP(KT)4-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-1AP(KT)4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-5","01D05","水阀反馈",{"$f":"AH78&\"-\"&AK78","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU01D05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%I\"&B78*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU01D05_WVB AT%I210.0 :INT ; (*空调机组NJ-1AP(KT)4-5-水阀反馈*)"},"LAHU01D05_WVB           AT%I210.0      :INT ; (*空调机组NJ-1AP(KT)4-5-水阀反馈*)",null,"AHU01D05_WVB",{"$f":"J78","v":"空调机组NJ-1AP(KT)4-5-水阀反馈"},{"$f":"AS77+1","v":30105}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-1AP(KT)4-6-回风温度",{"$nulls":16},"NJ-1AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-6","01D06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU01D06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%I\"&B78*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU01D06_RT AT%I212.0 :INT ; (*空调机组NJ-1AP(KT)4-6-回风温度*)"},"LAHU01D06_RT            AT%I212.0      :INT ; (*空调机组NJ-1AP(KT)4-6-回风温度*)",null,"AHU01D06_RT","空调机组NJ-1AP(KT)4-6-回风温度",{"$f":"AS78+1","v":30106}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-1AP(KT)4-6-水阀反馈",{"$nulls":16},"NJ-1AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-6","01D06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU01D06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%I\"&B78*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU01D06_WVB AT%I214.0 :INT ; (*空调机组NJ-1AP(KT)4-6-水阀反馈*)"},"LAHU01D06_WVB           AT%I214.0      :INT ; (*空调机组NJ-1AP(KT)4-6-水阀反馈*)",null,"AHU01D06_WVB","空调机组NJ-1AP(KT)4-6-水阀反馈",30107]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B90","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B90&\"地址: \"&B87&\" *)\"","v":"(* IOM 0401A地址: 14 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH86&AA86&\"-\"&AK86","v":"空调机组NJ-1AP(KT)4-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-1AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-1","01D01","水阀控制",{"$f":"AH86&\"-\"&AK86","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"AHU01D01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%Q\"&B87*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LAHU01D01_WVC AT%Q224.0 :INT ; (*空调机组NJ-1AP(KT)4-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86))),SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))))),\" \")","v":"LAHU01D01_WVC           AT%Q224.0      :INT ; (*空调机组NJ-1AP(KT)4-1-水阀控制*)"},null,{"$f":"AM86","v":"AHU01D01_WVC"},{"$f":"J86","v":"空调机组NJ-1AP(KT)4-1-水阀控制"},{"$f":"40000+($B87*8+F86-1)","v":40112}]
[null,14,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH87&AA87&\"-\"&AK87","v":"空调机组NJ-1AP(KT)4-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI87=\"\",\"\",AI87)","v":"NJ-1AP(KT)4-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-2","01D02","水阀控制",{"$f":"AH87&\"-\"&AK87","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"AHU01D02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%Q\"&B87*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LAHU01D02_WVC AT%Q226.0 :INT ; (*空调机组NJ-1AP(KT)4-2-水阀控制*)"},"LAHU01D02_WVC           AT%Q226.0      :INT ; (*空调机组NJ-1AP(KT)4-2-水阀控制*)",null,"AHU01D02_WVC",{"$f":"J87","v":"空调机组NJ-1AP(KT)4-2-水阀控制"},{"$f":"AS86+1","v":40113}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH88&AA88&\"-\"&AK88","v":"空调机组NJ-1AP(KT)4-3-水阀控制"},{"$nulls":16},"NJ-1AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-3","01D03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"AHU01D03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%Q\"&B87*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LAHU01D03_WVC AT%Q228.0 :INT ; (*空调机组NJ-1AP(KT)4-3-水阀控制*)"},"LAHU01D03_WVC           AT%Q228.0      :INT ; (*空调机组NJ-1AP(KT)4-3-水阀控制*)",null,"AHU01D03_WVC","空调机组NJ-1AP(KT)4-3-水阀控制",{"$f":"AS87+1","v":40114}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH89&AA89&\"-\"&AK89","v":"空调机组NJ-1AP(KT)4-4-水阀控制"},{"$nulls":16},"NJ-1AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-4","01D04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"AHU01D04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%Q\"&B87*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LAHU01D04_WVC AT%Q230.0 :INT ; (*空调机组NJ-1AP(KT)4-4-水阀控制*)"},"LAHU01D04_WVC           AT%Q230.0      :INT ; (*空调机组NJ-1AP(KT)4-4-水阀控制*)",null,"AHU01D04_WVC","空调机组NJ-1AP(KT)4-4-水阀控制",40115]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B99","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B99&\"地址: \"&B96&\" *)\"","v":"(* IOM 0401A地址: 15 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH95&AA95&\"-\"&AK95","v":"空调机组NJ-1AP(KT)4-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-1AP(KT)4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-5","01D05","水阀控制",{"$f":"AH95&\"-\"&AK95","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"AHU01D05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%Q\"&B96*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LAHU01D05_WVC AT%Q240.0 :INT ; (*空调机组NJ-1AP(KT)4-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95))),SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))))),\" \")","v":"LAHU01D05_WVC           AT%Q240.0      :INT ; (*空调机组NJ-1AP(KT)4-5-水阀控制*)"},null,{"$f":"AM95","v":"AHU01D05_WVC"},{"$f":"J95","v":"空调机组NJ-1AP(KT)4-5-水阀控制"},{"$f":"40000+($B96*8+F95-1)","v":40120}]
[null,15,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH96&AA96&\"-\"&AK96","v":"空调机组NJ-1AP(KT)4-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI96=\"\",\"\",AI96)","v":"NJ-1AP(KT)4-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)4-6","01D06","水阀控制",{"$f":"AH96&\"-\"&AK96","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"AHU01D06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%Q\"&B96*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LAHU01D06_WVC AT%Q242.0 :INT ; (*空调机组NJ-1AP(KT)4-6-水阀控制*)"},"LAHU01D06_WVC           AT%Q242.0      :INT ; (*空调机组NJ-1AP(KT)4-6-水阀控制*)",null,"AHU01D06_WVC",{"$f":"J96","v":"空调机组NJ-1AP(KT)4-6-水阀控制"},{"$f":"AS95+1","v":40121}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH97&AA97&\"-\"&AK97","v":"-"},{"$nulls":16},{"$f":"IF(AI97=\"\",\"\",AI97)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},{"$f":"AH97&\"-\"&AK97","v":"-"},{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%Q\"&B96*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS96+1","v":40122}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH98&AA98&\"-\"&AK98","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%Q\"&B96*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40123]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L205","index":13,"n_rows":94,"n_cols":45,"rows_kept":94,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[6,1,6,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[75,5,75,6],[75,9,75,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[84,5,84,6],[84,9,84,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[92,5,92,6],[92,9,92,25],[93,5,93,6],[93,9,93,25],[4,1,5,1],[12,1,23,1],[29,1,40,1],[46,1,57,1],[63,1,66,1],[72,1,75,1],[81,1,84,1],[90,1,93,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[16,2,23,4],[33,2,40,4],[50,2,57,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L15",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"EXC-1000"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B13&\"地址: \"&B10&\" *)\"","v":"(* IOM 1601R地址: 0 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH9&AA9&\"-\"&AK9","v":"空调机组NJ-2AP(KT)5-1-运行状态"},{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-2AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-1","02E01","运行状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU02E01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B10*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU02E01_R AT%I0.0 :BOOL; (*空调机组NJ-2AP(KT)5-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9))),SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))))),\" \")","v":"LAHU02E01_R             AT%I0.0        :BOOL; (*空调机组NJ-2AP(KT)5-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM9","v":"L15\\L15AHU02E01_R"},{"$f":"J9","v":"空调机组NJ-2AP(KT)5-1-运行状态"},{"$f":"10000+($B10*16*8+F9-1)","v":10000}]
[null,0,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-2AP(KT)5-1-故障状态",{"$nulls":16},{"$f":"IF(AI10=\"\",\"\",AI10)","v":"NJ-2AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-1","02E01","故障状态",{"$f":"AH10&\"-\"&AK10","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU02E01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B10*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU02E01_F AT%I0.1 :BOOL; (*空调机组NJ-2AP(KT)5-1-故障状态*)"},"LAHU02E01_F             AT%I0.1        :BOOL; (*空调机组NJ-2AP(KT)5-1-故障状态*)",null,"L15\\L15AHU02E01_F",{"$f":"J10","v":"空调机组NJ-2AP(KT)5-1-故障状态"},{"$f":"AS9+1","v":10001}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-2AP(KT)5-1-自动状态",{"$nulls":16},"NJ-2AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-1","02E01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU02E01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B10*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU02E01_A AT%I0.2 :BOOL; (*空调机组NJ-2AP(KT)5-1-自动状态*)"},"LAHU02E01_A             AT%I0.2        :BOOL; (*空调机组NJ-2AP(KT)5-1-自动状态*)",null,"L15\\L15AHU02E01_A","空调机组NJ-2AP(KT)5-1-自动状态",{"$f":"AS10+1","v":10002}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-2AP(KT)5-1-风机压差",{"$nulls":16},"NJ-2AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-1","02E01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU02E01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B10*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU02E01_FPS AT%I0.3 :BOOL; (*空调机组NJ-2AP(KT)5-1-风机压差*)"},"LAHU02E01_FPS           AT%I0.3        :BOOL; (*空调机组NJ-2AP(KT)5-1-风机压差*)",null,"L15\\L15AHU02E01_FPS","空调机组NJ-2AP(KT)5-1-风机压差",10003]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-2AP(KT)5-2-运行状态",{"$nulls":16},"NJ-2AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-2","02E02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU02E02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B10*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU02E02_R AT%I0.4 :BOOL; (*空调机组NJ-2AP(KT)5-2-运行状态*)"},"LAHU02E02_R             AT%I0.4        :BOOL; (*空调机组NJ-2AP(KT)5-2-运行状态*)",null,"L15\\L15AHU02E02_R","空调机组NJ-2AP(KT)5-2-运行状态",10004]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-2AP(KT)5-2-故障状态",{"$nulls":16},"NJ-2AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-2","02E02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU02E02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B10*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU02E02_F AT%I0.5 :BOOL; (*空调机组NJ-2AP(KT)5-2-故障状态*)"},"LAHU02E02_F             AT%I0.5        :BOOL; (*空调机组NJ-2AP(KT)5-2-故障状态*)",null,"L15\\L15AHU02E02_F","空调机组NJ-2AP(KT)5-2-故障状态",10005]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-2AP(KT)5-2-自动状态",{"$nulls":16},"NJ-2AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-2","02E02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU02E02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B10*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU02E02_A AT%I0.6 :BOOL; (*空调机组NJ-2AP(KT)5-2-自动状态*)"},"LAHU02E02_A             AT%I0.6        :BOOL; (*空调机组NJ-2AP(KT)5-2-自动状态*)",null,"L15\\L15AHU02E02_A","空调机组NJ-2AP(KT)5-2-自动状态",10006]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-2AP(KT)5-2-风机压差",{"$nulls":16},"NJ-2AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-2","02E02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU02E02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B10*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU02E02_FPS AT%I0.7 :BOOL; (*空调机组NJ-2AP(KT)5-2-风机压差*)"},"LAHU02E02_FPS           AT%I0.7        :BOOL; (*空调机组NJ-2AP(KT)5-2-风机压差*)",null,"L15\\L15AHU02E02_FPS","空调机组NJ-2AP(KT)5-2-风机压差",10007]
[{"$nulls":5},9,null,17,18,"空调机组NJ-2AP(KT)5-3-运行状态",{"$nulls":16},"NJ-2AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-3","02E03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU02E03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B10*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU02E03_R AT%I1.0 :BOOL; (*空调机组NJ-2AP(KT)5-3-运行状态*)"},"LAHU02E03_R             AT%I1.0        :BOOL; (*空调机组NJ-2AP(KT)5-3-运行状态*)",null,"L15\\L15AHU02E03_R","空调机组NJ-2AP(KT)5-3-运行状态",10008]
[{"$nulls":5},10,null,19,20,"空调机组NJ-2AP(KT)5-3-故障状态",{"$nulls":16},{"$f":"IF(AI18=\"\",\"\",AI18)","v":"NJ-2AP(KT)5-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-3","02E03","故障状态",{"$f":"AH18&\"-\"&AK18","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU02E03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B10*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU02E03_F AT%I1.1 :BOOL; (*空调机组NJ-2AP(KT)5-3-故障状态*)"},"LAHU02E03_F             AT%I1.1        :BOOL; (*空调机组NJ-2AP(KT)5-3-故障状态*)",null,"L15\\L15AHU02E03_F","空调机组NJ-2AP(KT)5-3-故障状态",10009]
[{"$nulls":5},11,null,21,22,"空调机组NJ-2AP(KT)5-3-自动状态",{"$nulls":16},"NJ-2AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-3","02E03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU02E03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B10*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU02E03_A AT%I1.2 :BOOL; (*空调机组NJ-2AP(KT)5-3-自动状态*)"},"LAHU02E03_A             AT%I1.2        :BOOL; (*空调机组NJ-2AP(KT)5-3-自动状态*)",null,"L15\\L15AHU02E03_A","空调机组NJ-2AP(KT)5-3-自动状态",10010]
[{"$nulls":5},12,null,23,24,"空调机组NJ-2AP(KT)5-3-风机压差",{"$nulls":16},"NJ-2AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-3","02E03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU02E03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B10*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU02E03_FPS AT%I1.3 :BOOL; (*空调机组NJ-2AP(KT)5-3-风机压差*)"},"LAHU02E03_FPS           AT%I1.3        :BOOL; (*空调机组NJ-2AP(KT)5-3-风机压差*)",null,"L15\\L15AHU02E03_FPS","空调机组NJ-2AP(KT)5-3-风机压差",10011]
[{"$nulls":5},13,null,25,26,"空调机组NJ-2AP(KT)5-4-运行状态",{"$nulls":16},"NJ-2AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-4","02E04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU02E04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B10*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU02E04_R AT%I1.4 :BOOL; (*空调机组NJ-2AP(KT)5-4-运行状态*)"},"LAHU02E04_R             AT%I1.4        :BOOL; (*空调机组NJ-2AP(KT)5-4-运行状态*)",null,"L15\\L15AHU02E04_R","空调机组NJ-2AP(KT)5-4-运行状态",10012]
[{"$nulls":5},14,null,27,28,"空调机组NJ-2AP(KT)5-4-故障状态",{"$nulls":16},"NJ-2AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-4","02E04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU02E04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B10*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU02E04_F AT%I1.5 :BOOL; (*空调机组NJ-2AP(KT)5-4-故障状态*)"},"LAHU02E04_F             AT%I1.5        :BOOL; (*空调机组NJ-2AP(KT)5-4-故障状态*)",null,"L15\\L15AHU02E04_F","空调机组NJ-2AP(KT)5-4-故障状态",10013]
[{"$nulls":5},15,null,29,30,"空调机组NJ-2AP(KT)5-4-自动状态",{"$nulls":16},"NJ-2AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-4","02E04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU02E04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B10*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU02E04_A AT%I1.6 :BOOL; (*空调机组NJ-2AP(KT)5-4-自动状态*)"},"LAHU02E04_A             AT%I1.6        :BOOL; (*空调机组NJ-2AP(KT)5-4-自动状态*)",null,"L15\\L15AHU02E04_A","空调机组NJ-2AP(KT)5-4-自动状态",10014]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-2AP(KT)5-4-风机压差",{"$nulls":16},"NJ-2AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-4","02E04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH24,List!$B$3:$D$445,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,List!$K$2:$M$447,2,FALSE)","v":"AHU02E04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%I\"&B10*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":"LAHU02E04_FPS AT%I1.7 :BOOL; (*空调机组NJ-2AP(KT)5-4-风机压差*)"},"LAHU02E04_FPS           AT%I1.7        :BOOL; (*空调机组NJ-2AP(KT)5-4-风机压差*)",null,"L15\\L15AHU02E04_FPS","空调机组NJ-2AP(KT)5-4-风机压差",10015]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 1601R地址: 1 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH26&AA26&\"-\"&AK26","v":"空调机组NJ-2AP(KT)5-5-运行状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-2AP(KT)5-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-5","02E05","运行状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU02E05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU02E05_R AT%I16.0 :BOOL; (*空调机组NJ-2AP(KT)5-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LAHU02E05_R             AT%I16.0       :BOOL; (*空调机组NJ-2AP(KT)5-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L15\\L15AHU02E05_R"},{"$f":"J26","v":"空调机组NJ-2AP(KT)5-5-运行状态"},{"$f":"10000+($B27*16*8+F26-1)","v":10128}]
[null,1,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-2AP(KT)5-5-故障状态",{"$nulls":16},{"$f":"IF(AI27=\"\",\"\",AI27)","v":"NJ-2AP(KT)5-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-5","02E05","故障状态",{"$f":"AH27&\"-\"&AK27","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU02E05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU02E05_F AT%I16.1 :BOOL; (*空调机组NJ-2AP(KT)5-5-故障状态*)"},"LAHU02E05_F             AT%I16.1       :BOOL; (*空调机组NJ-2AP(KT)5-5-故障状态*)",null,"L15\\L15AHU02E05_F",{"$f":"J27","v":"空调机组NJ-2AP(KT)5-5-故障状态"},{"$f":"AS26+1","v":10129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-2AP(KT)5-5-自动状态",{"$nulls":16},"NJ-2AP(KT)5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-5","02E05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU02E05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU02E05_A AT%I16.2 :BOOL; (*空调机组NJ-2AP(KT)5-5-自动状态*)"},"LAHU02E05_A             AT%I16.2       :BOOL; (*空调机组NJ-2AP(KT)5-5-自动状态*)",null,"L15\\L15AHU02E05_A","空调机组NJ-2AP(KT)5-5-自动状态",{"$f":"AS27+1","v":10130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-2AP(KT)5-5-风机压差",{"$nulls":16},"NJ-2AP(KT)5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-5","02E05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU02E05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU02E05_FPS AT%I16.3 :BOOL; (*空调机组NJ-2AP(KT)5-5-风机压差*)"},"LAHU02E05_FPS           AT%I16.3       :BOOL; (*空调机组NJ-2AP(KT)5-5-风机压差*)",null,"L15\\L15AHU02E05_FPS","空调机组NJ-2AP(KT)5-5-风机压差",10131]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-2AL5-1-运行状态",{"$nulls":16},"NJ-2AL5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL5-1","02E01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"LCB02E01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B27*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LLCB02E01_R AT%I16.4 :BOOL; (*照明控制箱NJ-2AL5-1-运行状态*)"},"LLCB02E01_R             AT%I16.4       :BOOL; (*照明控制箱NJ-2AL5-1-运行状态*)",null,"L15\\L15LCB02E01_R","照明控制箱NJ-2AL5-1-运行状态",10132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-2AL5-1-自动状态",{"$nulls":16},"NJ-2AL5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-2AL5-1","02E01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"LCB02E01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B27*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LLCB02E01_A AT%I16.5 :BOOL; (*照明控制箱NJ-2AL5-1-自动状态*)"},"LLCB02E01_A             AT%I16.5       :BOOL; (*照明控制箱NJ-2AL5-1-自动状态*)",null,"L15\\L15LCB02E01_A","照明控制箱NJ-2AL5-1-自动状态",10133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"照明控制箱NJ-2AL5-2-运行状态",{"$nulls":16},"NJ-2AL5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL5-2","02E02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"LCB02E02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B27*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LLCB02E02_R AT%I16.6 :BOOL; (*照明控制箱NJ-2AL5-2-运行状态*)"},"LLCB02E02_R             AT%I16.6       :BOOL; (*照明控制箱NJ-2AL5-2-运行状态*)",null,"L15\\L15LCB02E02_R","照明控制箱NJ-2AL5-2-运行状态",10134]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"照明控制箱NJ-2AL5-2-自动状态",{"$nulls":16},"NJ-2AL5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-2AL5-2","02E02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"LCB02E02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B27*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LLCB02E02_A AT%I16.7 :BOOL; (*照明控制箱NJ-2AL5-2-自动状态*)"},"LLCB02E02_A             AT%I16.7       :BOOL; (*照明控制箱NJ-2AL5-2-自动状态*)",null,"L15\\L15LCB02E02_A","照明控制箱NJ-2AL5-2-自动状态",10135]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-2AL5-3-运行状态",{"$nulls":16},"NJ-2AL5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL5-3","02E03","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"LCB02E03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B27*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LLCB02E03_R AT%I17.0 :BOOL; (*照明控制箱NJ-2AL5-3-运行状态*)"},"LLCB02E03_R             AT%I17.0       :BOOL; (*照明控制箱NJ-2AL5-3-运行状态*)",null,"L15\\L15LCB02E03_R","照明控制箱NJ-2AL5-3-运行状态",10136]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-2AL5-3-自动状态",{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-2AL5-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-2AL5-3","02E03","自动状态",{"$f":"AH35&\"-\"&AK35","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"LCB02E03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B27*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LLCB02E03_A AT%I17.1 :BOOL; (*照明控制箱NJ-2AL5-3-自动状态*)"},"LLCB02E03_A             AT%I17.1       :BOOL; (*照明控制箱NJ-2AL5-3-自动状态*)",null,"L15\\L15LCB02E03_A",{"$f":"J35","v":"照明控制箱NJ-2AL5-3-自动状态"},10137]
[{"$nulls":5},11,null,21,22,"照明控制箱NJ-2AL5-4-运行状态",{"$nulls":16},"NJ-2AL5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL5-4","02E04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"LCB02E04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B27*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LLCB02E04_R AT%I17.2 :BOOL; (*照明控制箱NJ-2AL5-4-运行状态*)"},"LLCB02E04_R             AT%I17.2       :BOOL; (*照明控制箱NJ-2AL5-4-运行状态*)",null,"L15\\L15LCB02E04_R","照明控制箱NJ-2AL5-4-运行状态",10138]
[{"$nulls":5},12,null,23,24,"照明控制箱NJ-2AL5-4-自动状态",{"$nulls":16},"NJ-2AL5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-2AL5-4","02E04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"LCB02E04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B27*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LLCB02E04_A AT%I17.3 :BOOL; (*照明控制箱NJ-2AL5-4-自动状态*)"},"LLCB02E04_A             AT%I17.3       :BOOL; (*照明控制箱NJ-2AL5-4-自动状态*)",null,"L15\\L15LCB02E04_A","照明控制箱NJ-2AL5-4-自动状态",10139]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-2AL5-5-运行状态",{"$nulls":16},"NJ-2AL5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL5-5","02E05","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB02E05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B27*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB02E05_R AT%I17.4 :BOOL; (*照明控制箱NJ-2AL5-5-运行状态*)"},"LLCB02E05_R             AT%I17.4       :BOOL; (*照明控制箱NJ-2AL5-5-运行状态*)",null,"L15\\L15LCB02E05_R","照明控制箱NJ-2AL5-5-运行状态",10140]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-2AL5-5-自动状态",{"$nulls":16},"NJ-2AL5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-2AL5-5","02E05","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB02E05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B27*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB02E05_A AT%I17.5 :BOOL; (*照明控制箱NJ-2AL5-5-自动状态*)"},"LLCB02E05_A             AT%I17.5       :BOOL; (*照明控制箱NJ-2AL5-5-自动状态*)",null,"L15\\L15LCB02E05_A","照明控制箱NJ-2AL5-5-自动状态",10141]
[{"$nulls":5},15,null,29,30,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B27*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10142]
[".",{"$nulls":4},16,null,31,32,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%I\"&B27*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10143]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 1601D地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH43&AA43&\"-\"&AK43","v":"空调机组NJ-2AP(KT)5-1-启停控制"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-2AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-1","02E01","启停控制",{"$f":"AH43&\"-\"&AK43","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"AHU02E01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%Q\"&B44*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LAHU02E01_C AT%Q32.0 :BOOL; (*空调机组NJ-2AP(KT)5-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LAHU02E01_C             AT%Q32.0       :BOOL; (*空调机组NJ-2AP(KT)5-1-启停控制*)"},null,{"$f":"AM43","v":"AHU02E01_C"},{"$f":"J43","v":"空调机组NJ-2AP(KT)5-1-启停控制"},{"$f":"($B44*16*8+F43-1)","v":256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-2AP(KT)5-2-启停控制",{"$nulls":16},{"$f":"IF(AI44=\"\",\"\",AI44)","v":"NJ-2AP(KT)5-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-2","02E02","启停控制",{"$f":"AH44&\"-\"&AK44","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"AHU02E02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%Q\"&B44*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LAHU02E02_C AT%Q32.1 :BOOL; (*空调机组NJ-2AP(KT)5-2-启停控制*)"},"LAHU02E02_C             AT%Q32.1       :BOOL; (*空调机组NJ-2AP(KT)5-2-启停控制*)",null,"AHU02E02_C",{"$f":"J44","v":"空调机组NJ-2AP(KT)5-2-启停控制"},{"$f":"AS43+1","v":257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","空调机组NJ-2AP(KT)5-3-启停控制",{"$nulls":16},"NJ-2AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-3","02E03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"AHU02E03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%Q\"&B44*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LAHU02E03_C AT%Q32.2 :BOOL; (*空调机组NJ-2AP(KT)5-3-启停控制*)"},"LAHU02E03_C             AT%Q32.2       :BOOL; (*空调机组NJ-2AP(KT)5-3-启停控制*)",null,"AHU02E03_C","空调机组NJ-2AP(KT)5-3-启停控制",{"$f":"AS44+1","v":258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","空调机组NJ-2AP(KT)5-4-启停控制",{"$nulls":16},"NJ-2AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-4","02E04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"AHU02E04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%Q\"&B44*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LAHU02E04_C AT%Q32.3 :BOOL; (*空调机组NJ-2AP(KT)5-4-启停控制*)"},"LAHU02E04_C             AT%Q32.3       :BOOL; (*空调机组NJ-2AP(KT)5-4-启停控制*)",null,"AHU02E04_C","空调机组NJ-2AP(KT)5-4-启停控制",259]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-2AP(KT)5-5-启停控制",{"$nulls":16},"NJ-2AP(KT)5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-5","02E05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"AHU02E05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%Q\"&B44*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LAHU02E05_C AT%Q32.4 :BOOL; (*空调机组NJ-2AP(KT)5-5-启停控制*)"},"LAHU02E05_C             AT%Q32.4       :BOOL; (*空调机组NJ-2AP(KT)5-5-启停控制*)",null,"AHU02E05_C","空调机组NJ-2AP(KT)5-5-启停控制",260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","照明控制箱NJ-2AL5-1-启停控制",{"$nulls":16},"NJ-2AL5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL5-1","02E01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"LCB02E01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%Q\"&B44*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LLCB02E01_C AT%Q32.5 :BOOL; (*照明控制箱NJ-2AL5-1-启停控制*)"},"LLCB02E01_C             AT%Q32.5       :BOOL; (*照明控制箱NJ-2AL5-1-启停控制*)",null,"LCB02E01_C","照明控制箱NJ-2AL5-1-启停控制",261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","照明控制箱NJ-2AL5-2-启停控制",{"$nulls":16},"NJ-2AL5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL5-2","02E02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"LCB02E02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%Q\"&B44*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LLCB02E02_C AT%Q32.6 :BOOL; (*照明控制箱NJ-2AL5-2-启停控制*)"},"LLCB02E02_C             AT%Q32.6       :BOOL; (*照明控制箱NJ-2AL5-2-启停控制*)",null,"LCB02E02_C","照明控制箱NJ-2AL5-2-启停控制",262]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-2AL5-3-启停控制",{"$nulls":16},"NJ-2AL5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL5-3","02E03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"LCB02E03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%Q\"&B44*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LLCB02E03_C AT%Q32.7 :BOOL; (*照明控制箱NJ-2AL5-3-启停控制*)"},"LLCB02E03_C             AT%Q32.7       :BOOL; (*照明控制箱NJ-2AL5-3-启停控制*)",null,"LCB02E03_C","照明控制箱NJ-2AL5-3-启停控制",263]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-2AL5-4-启停控制",{"$nulls":16},"NJ-2AL5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL5-4","02E04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"LCB02E04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%Q\"&B44*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LLCB02E04_C AT%Q33.0 :BOOL; (*照明控制箱NJ-2AL5-4-启停控制*)"},"LLCB02E04_C             AT%Q33.0       :BOOL; (*照明控制箱NJ-2AL5-4-启停控制*)",null,"LCB02E04_C","照明控制箱NJ-2AL5-4-启停控制",264]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-2AL5-5-启停控制",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-2AL5-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL5-5","02E05","启停控制",{"$f":"AH52&\"-\"&AK52","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"LCB02E05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%Q\"&B44*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LLCB02E05_C AT%Q33.1 :BOOL; (*照明控制箱NJ-2AL5-5-启停控制*)"},"LLCB02E05_C             AT%Q33.1       :BOOL; (*照明控制箱NJ-2AL5-5-启停控制*)",null,"LCB02E05_C",{"$f":"J52","v":"照明控制箱NJ-2AL5-5-启停控制"},265]
[{"$nulls":5},11,null,"11+","11-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%Q\"&B44*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",266]
[{"$nulls":5},12,null,"12+","12-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%Q\"&B44*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",267]
[{"$nulls":5},13,null,"13+","13-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%Q\"&B44*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",268]
[{"$nulls":5},14,null,"14+","14-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%Q\"&B44*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",269]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%Q\"&B44*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",270]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%Q\"&B44*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",271]
[null,{"$f":"B64","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B64&\"地址: \"&B61&\" *)\"","v":"(* IOM 0801U地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH60&AA60&\"-\"&AK60","v":"空调机组NJ-2AP(KT)5-1-回风温度"},{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-2AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-1","02E01","回风温度",{"$f":"AH60&\"-\"&AK60","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"AHU02E01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%I\"&B61*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LAHU02E01_RT AT%I48.0 :INT ; (*空调机组NJ-2AP(KT)5-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60))),SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))))),\" \")","v":"LAHU02E01_RT            AT%I48.0       :INT ; (*空调机组NJ-2AP(KT)5-1-回风温度*)"},null,{"$f":"AM60","v":"AHU02E01_RT"},{"$f":"J60","v":"空调机组NJ-2AP(KT)5-1-回风温度"},{"$f":"30000+($B61*8+F60-1)","v":30024}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-2AP(KT)5-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI61=\"\",\"\",AI61)","v":"NJ-2AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-1","02E01","水阀反馈",{"$f":"AH61&\"-\"&AK61","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"AHU02E01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%I\"&B61*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LAHU02E01_WVB AT%I50.0 :INT ; (*空调机组NJ-2AP(KT)5-1-水阀反馈*)"},"LAHU02E01_WVB           AT%I50.0       :INT ; (*空调机组NJ-2AP(KT)5-1-水阀反馈*)",null,"AHU02E01_WVB",{"$f":"J61","v":"空调机组NJ-2AP(KT)5-1-水阀反馈"},{"$f":"AS60+1","v":30025}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-2AP(KT)5-2-回风温度",{"$nulls":16},"NJ-2AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-2","02E02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"AHU02E02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B61*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LAHU02E02_RT AT%I52.0 :INT ; (*空调机组NJ-2AP(KT)5-2-回风温度*)"},"LAHU02E02_RT            AT%I52.0       :INT ; (*空调机组NJ-2AP(KT)5-2-回风温度*)",null,"AHU02E02_RT","空调机组NJ-2AP(KT)5-2-回风温度",{"$f":"AS61+1","v":30026}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-2AP(KT)5-2-水阀反馈",{"$nulls":16},"NJ-2AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-2","02E02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"AHU02E02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B61*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LAHU02E02_WVB AT%I54.0 :INT ; (*空调机组NJ-2AP(KT)5-2-水阀反馈*)"},"LAHU02E02_WVB           AT%I54.0       :INT ; (*空调机组NJ-2AP(KT)5-2-水阀反馈*)",null,"AHU02E02_WVB","空调机组NJ-2AP(KT)5-2-水阀反馈",30027]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-2AP(KT)5-3-回风温度",{"$nulls":16},"NJ-2AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-3","02E03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"AHU02E03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B61*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LAHU02E03_RT AT%I56.0 :INT ; (*空调机组NJ-2AP(KT)5-3-回风温度*)"},"LAHU02E03_RT            AT%I56.0       :INT ; (*空调机组NJ-2AP(KT)5-3-回风温度*)",null,"AHU02E03_RT","空调机组NJ-2AP(KT)5-3-回风温度",30028]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-2AP(KT)5-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI65=\"\",\"\",AI65)","v":"NJ-2AP(KT)5-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-3","02E03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":"AHU02E03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B61*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":"LAHU02E03_WVB AT%I58.0 :INT ; (*空调机组NJ-2AP(KT)5-3-水阀反馈*)"},"LAHU02E03_WVB           AT%I58.0       :INT ; (*空调机组NJ-2AP(KT)5-3-水阀反馈*)",null,"AHU02E03_WVB",{"$f":"J65","v":"空调机组NJ-2AP(KT)5-3-水阀反馈"},30029]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-2AP(KT)5-4-回风温度",{"$nulls":16},"NJ-2AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-4","02E04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":"AHU02E04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B61*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":"LAHU02E04_RT AT%I60.0 :INT ; (*空调机组NJ-2AP(KT)5-4-回风温度*)"},"LAHU02E04_RT            AT%I60.0       :INT ; (*空调机组NJ-2AP(KT)5-4-回风温度*)",null,"AHU02E04_RT","空调机组NJ-2AP(KT)5-4-回风温度",30030]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-2AP(KT)5-4-水阀反馈",{"$nulls":16},"NJ-2AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-4","02E04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":"AHU02E04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%I\"&B61*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":"LAHU02E04_WVB AT%I62.0 :INT ; (*空调机组NJ-2AP(KT)5-4-水阀反馈*)"},"LAHU02E04_WVB           AT%I62.0       :INT ; (*空调机组NJ-2AP(KT)5-4-水阀反馈*)",null,"AHU02E04_WVB","空调机组NJ-2AP(KT)5-4-水阀反馈",30031]
[null,{"$f":"B73","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B73&\"地址: \"&B70&\" *)\"","v":"(* IOM 0401U地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH69&AA69&\"-\"&AK69","v":"空调机组NJ-2AP(KT)5-5-回风温度"},{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-2AP(KT)5-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-5","02E05","回风温度",{"$f":"AH69&\"-\"&AK69","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU02E05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%I\"&B70*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU02E05_RT AT%I64.0 :INT ; (*空调机组NJ-2AP(KT)5-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69))),SEARCH(\":\",REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69)))))),\" \")","v":"LAHU02E05_RT            AT%I64.0       :INT ; (*空调机组NJ-2AP(KT)5-5-回风温度*)"},null,{"$f":"AM69","v":"AHU02E05_RT"},{"$f":"J69","v":"空调机组NJ-2AP(KT)5-5-回风温度"},{"$f":"30000+($B70*8+F69-1)","v":30032}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-2AP(KT)5-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI70=\"\",\"\",AI70)","v":"NJ-2AP(KT)5-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-5","02E05","水阀反馈",{"$f":"AH70&\"-\"&AK70","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"AHU02E05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%I\"&B70*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LAHU02E05_WVB AT%I66.0 :INT ; (*空调机组NJ-2AP(KT)5-5-水阀反馈*)"},"LAHU02E05_WVB           AT%I66.0       :INT ; (*空调机组NJ-2AP(KT)5-5-水阀反馈*)",null,"AHU02E05_WVB",{"$f":"J70","v":"空调机组NJ-2AP(KT)5-5-水阀反馈"},{"$f":"AS69+1","v":30033}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),3,1))","v":1},3,null,3,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%I\"&B70*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS70+1","v":30034}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),2,1))","v":0},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%I\"&B70*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30035]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),1,1))","v":0}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B82","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B82&\"地址: \"&B79&\" *)\"","v":"(* IOM 0401A地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH78&AA78&\"-\"&AK78","v":"空调机组NJ-2AP(KT)5-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-2AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-1","02E01","水阀控制",{"$f":"AH78&\"-\"&AK78","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU02E01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B79*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU02E01_WVC AT%Q80.0 :INT ; (*空调机组NJ-2AP(KT)5-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN78,SEARCH(\"AT%\",AN78),,REPT(\" \",25-SEARCH(\"AT%\",AN78))),SEARCH(\":\",REPLACE(AN78,SEARCH(\"AT%\",AN78),,REPT(\" \",25-SEARCH(\"AT%\",AN78)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN78,SEARCH(\"AT%\",AN78),,REPT(\" \",25-SEARCH(\"AT%\",AN78)))))),\" \")","v":"LAHU02E01_WVC           AT%Q80.0       :INT ; (*空调机组NJ-2AP(KT)5-1-水阀控制*)"},null,{"$f":"AM78","v":"AHU02E01_WVC"},{"$f":"J78","v":"空调机组NJ-2AP(KT)5-1-水阀控制"},{"$f":"40000+($B79*8+F78-1)","v":40040}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH79&AA79&\"-\"&AK79","v":"空调机组NJ-2AP(KT)5-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI79=\"\",\"\",AI79)","v":"NJ-2AP(KT)5-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-2","02E02","水阀控制",{"$f":"AH79&\"-\"&AK79","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU02E02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B79*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU02E02_WVC AT%Q82.0 :INT ; (*空调机组NJ-2AP(KT)5-2-水阀控制*)"},"LAHU02E02_WVC           AT%Q82.0       :INT ; (*空调机组NJ-2AP(KT)5-2-水阀控制*)",null,"AHU02E02_WVC",{"$f":"J79","v":"空调机组NJ-2AP(KT)5-2-水阀控制"},{"$f":"AS78+1","v":40041}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH80&AA80&\"-\"&AK80","v":"空调机组NJ-2AP(KT)5-3-水阀控制"},{"$nulls":16},"NJ-2AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-3","02E03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU02E03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B79*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU02E03_WVC AT%Q84.0 :INT ; (*空调机组NJ-2AP(KT)5-3-水阀控制*)"},"LAHU02E03_WVC           AT%Q84.0       :INT ; (*空调机组NJ-2AP(KT)5-3-水阀控制*)",null,"AHU02E03_WVC","空调机组NJ-2AP(KT)5-3-水阀控制",{"$f":"AS79+1","v":40042}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH81&AA81&\"-\"&AK81","v":"空调机组NJ-2AP(KT)5-4-水阀控制"},{"$nulls":16},"NJ-2AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-4","02E04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"AHU02E04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%Q\"&B79*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LAHU02E04_WVC AT%Q86.0 :INT ; (*空调机组NJ-2AP(KT)5-4-水阀控制*)"},"LAHU02E04_WVC           AT%Q86.0       :INT ; (*空调机组NJ-2AP(KT)5-4-水阀控制*)",null,"AHU02E04_WVC","空调机组NJ-2AP(KT)5-4-水阀控制",40043]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B91","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B91&\"地址: \"&B88&\" *)\"","v":"(* IOM 0401A地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH87&AA87&\"-\"&AK87","v":"空调机组NJ-2AP(KT)5-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI87=\"\",\"\",AI87)","v":"NJ-2AP(KT)5-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)5-5","02E05","水阀控制",{"$f":"AH87&\"-\"&AK87","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"AHU02E05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%Q\"&B88*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LAHU02E05_WVC AT%Q96.0 :INT ; (*空调机组NJ-2AP(KT)5-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN87,SEARCH(\"AT%\",AN87),,REPT(\" \",25-SEARCH(\"AT%\",AN87))),SEARCH(\":\",REPLACE(AN87,SEARCH(\"AT%\",AN87),,REPT(\" \",25-SEARCH(\"AT%\",AN87)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN87,SEARCH(\"AT%\",AN87),,REPT(\" \",25-SEARCH(\"AT%\",AN87)))))),\" \")","v":"LAHU02E05_WVC           AT%Q96.0       :INT ; (*空调机组NJ-2AP(KT)5-5-水阀控制*)"},null,{"$f":"AM87","v":"AHU02E05_WVC"},{"$f":"J87","v":"空调机组NJ-2AP(KT)5-5-水阀控制"},{"$f":"40000+($B88*8+F87-1)","v":40048}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH88&AA88&\"-\"&AK88","v":"-"},{"$nulls":16},{"$f":"IF(AI88=\"\",\"\",AI88)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},{"$f":"AH88&\"-\"&AK88","v":"-"},{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%Q\"&B88*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J88","v":"-"},{"$f":"AS87+1","v":40049}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH89&AA89&\"-\"&AK89","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%Q\"&B88*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS88+1","v":40050}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH90&AA90&\"-\"&AK90","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%Q\"&B88*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40051]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L105","index":14,"n_rows":128,"n_cols":45,"rows_kept":128,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[41,5,41,6],[41,9,41,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[75,5,75,6],[75,9,75,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[84,5,84,6],[84,9,84,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[93,5,93,6],[93,9,93,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[102,5,102,6],[102,9,102,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[109,5,109,6],[109,9,109,25],[111,5,111,6],[111,9,111,25],[112,5,112,6],[112,9,112,25],[113,5,113,6],[113,9,113,25],[114,5,114,6],[114,9,114,25],[115,5,115,6],[115,9,115,25],[116,5,116,6],[116,9,116,25],[117,5,117,6],[117,9,117,25],[118,5,118,6],[118,9,118,25],[120,5,120,6],[120,9,120,25],[121,5,121,6],[121,9,121,25],[122,5,122,6],[122,9,122,25],[123,5,123,6],[123,9,123,25],[124,5,124,6],[124,9,124,25],[125,5,125,6],[125,9,125,25],[126,5,126,6],[126,9,126,25],[127,5,127,6],[127,9,127,25],[4,1,5,1],[11,1,22,1],[28,1,39,1],[45,1,56,1],[62,1,65,1],[71,1,82,1],[88,1,91,1],[97,1,100,1],[106,1,109,1],[115,1,118,1],[124,1,127,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4],[32,2,39,4],[75,2,82,4],[49,2,56,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L15",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 7 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH8&AA8&\"-\"&AK8","v":"空调机组NJ-1AP(KT)5-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-1AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-1","01E01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH8,List!$B$3:$D$445,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,List!$K$2:$M$447,2,FALSE)","v":"AHU01E01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LAHU01E01_R AT%I112.0 :BOOL; (*空调机组NJ-1AP(KT)5-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LAHU01E01_R             AT%I112.0      :BOOL; (*空调机组NJ-1AP(KT)5-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L15\\L15AHU01E01_R"},{"$f":"J8","v":"空调机组NJ-1AP(KT)5-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":10896}]
[null,7,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},2,null,3,4,"空调机组NJ-1AP(KT)5-1-故障状态",{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-1AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-1","01E01","故障状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU01E01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU01E01_F AT%I112.1 :BOOL; (*空调机组NJ-1AP(KT)5-1-故障状态*)"},"LAHU01E01_F             AT%I112.1      :BOOL; (*空调机组NJ-1AP(KT)5-1-故障状态*)",null,"L15\\L15AHU01E01_F",{"$f":"J9","v":"空调机组NJ-1AP(KT)5-1-故障状态"},{"$f":"AS8+1","v":10897}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},3,null,5,6,"空调机组NJ-1AP(KT)5-1-自动状态",{"$nulls":16},"NJ-1AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-1","01E01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU01E01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU01E01_A AT%I112.2 :BOOL; (*空调机组NJ-1AP(KT)5-1-自动状态*)"},"LAHU01E01_A             AT%I112.2      :BOOL; (*空调机组NJ-1AP(KT)5-1-自动状态*)",null,"L15\\L15AHU01E01_A","空调机组NJ-1AP(KT)5-1-自动状态",{"$f":"AS9+1","v":10898}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-1AP(KT)5-1-风机压差",{"$nulls":16},"NJ-1AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-1","01E01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU01E01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU01E01_FPS AT%I112.3 :BOOL; (*空调机组NJ-1AP(KT)5-1-风机压差*)"},"LAHU01E01_FPS           AT%I112.3      :BOOL; (*空调机组NJ-1AP(KT)5-1-风机压差*)",null,"L15\\L15AHU01E01_FPS","空调机组NJ-1AP(KT)5-1-风机压差",10899]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-1AP(KT)5-1-运行状态",{"$nulls":16},"NJ-1AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-1","01E02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU01E02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU01E02_R AT%I112.4 :BOOL; (*空调机组NJ-1AP(KT)5-1-运行状态*)"},"LAHU01E02_R             AT%I112.4      :BOOL; (*空调机组NJ-1AP(KT)5-1-运行状态*)",null,"L15\\L15AHU01E02_R","空调机组NJ-1AP(KT)5-1-运行状态",10900]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-1AP(KT)5-2-故障状态",{"$nulls":16},"NJ-1AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-2","01E02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU01E02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU01E02_F AT%I112.5 :BOOL; (*空调机组NJ-1AP(KT)5-2-故障状态*)"},"LAHU01E02_F             AT%I112.5      :BOOL; (*空调机组NJ-1AP(KT)5-2-故障状态*)",null,"L15\\L15AHU01E02_F","空调机组NJ-1AP(KT)5-2-故障状态",10901]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-1AP(KT)5-2-自动状态",{"$nulls":16},"NJ-1AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-2","01E02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU01E02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU01E02_A AT%I112.6 :BOOL; (*空调机组NJ-1AP(KT)5-2-自动状态*)"},"LAHU01E02_A             AT%I112.6      :BOOL; (*空调机组NJ-1AP(KT)5-2-自动状态*)",null,"L15\\L15AHU01E02_A","空调机组NJ-1AP(KT)5-2-自动状态",10902]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-1AP(KT)5-2-风机压差",{"$nulls":16},"NJ-1AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-2","01E02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU01E02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU01E02_FPS AT%I112.7 :BOOL; (*空调机组NJ-1AP(KT)5-2-风机压差*)"},"LAHU01E02_FPS           AT%I112.7      :BOOL; (*空调机组NJ-1AP(KT)5-2-风机压差*)",null,"L15\\L15AHU01E02_FPS","空调机组NJ-1AP(KT)5-2-风机压差",10903]
[{"$nulls":5},9,null,17,18,"空调机组NJ-1AP(KT)5-2-运行状态",{"$nulls":16},"NJ-1AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-2","01E03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU01E03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU01E03_R AT%I113.0 :BOOL; (*空调机组NJ-1AP(KT)5-2-运行状态*)"},"LAHU01E03_R             AT%I113.0      :BOOL; (*空调机组NJ-1AP(KT)5-2-运行状态*)",null,"L15\\L15AHU01E03_R","空调机组NJ-1AP(KT)5-2-运行状态",10904]
[{"$nulls":5},10,null,19,20,"空调机组NJ-1AP(KT)5-3-故障状态",{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-1AP(KT)5-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-3","01E03","故障状态",{"$f":"AH17&\"-\"&AK17","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU01E03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU01E03_F AT%I113.1 :BOOL; (*空调机组NJ-1AP(KT)5-3-故障状态*)"},"LAHU01E03_F             AT%I113.1      :BOOL; (*空调机组NJ-1AP(KT)5-3-故障状态*)",null,"L15\\L15AHU01E03_F","空调机组NJ-1AP(KT)5-3-故障状态",10905]
[{"$nulls":5},11,null,21,22,"空调机组NJ-1AP(KT)5-3-自动状态",{"$nulls":16},"NJ-1AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-3","01E03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU01E03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU01E03_A AT%I113.2 :BOOL; (*空调机组NJ-1AP(KT)5-3-自动状态*)"},"LAHU01E03_A             AT%I113.2      :BOOL; (*空调机组NJ-1AP(KT)5-3-自动状态*)",null,"L15\\L15AHU01E03_A","空调机组NJ-1AP(KT)5-3-自动状态",10906]
[{"$nulls":5},12,null,23,24,"空调机组NJ-1AP(KT)5-3-风机压差",{"$nulls":16},"NJ-1AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-3","01E03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU01E03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU01E03_FPS AT%I113.3 :BOOL; (*空调机组NJ-1AP(KT)5-3-风机压差*)"},"LAHU01E03_FPS           AT%I113.3      :BOOL; (*空调机组NJ-1AP(KT)5-3-风机压差*)",null,"L15\\L15AHU01E03_FPS","空调机组NJ-1AP(KT)5-3-风机压差",10907]
[{"$nulls":5},13,null,25,26,"空调机组NJ-1AP(KT)5-4-运行状态",{"$nulls":16},"NJ-1AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-4","01E04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU01E04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU01E04_R AT%I113.4 :BOOL; (*空调机组NJ-1AP(KT)5-4-运行状态*)"},"LAHU01E04_R             AT%I113.4      :BOOL; (*空调机组NJ-1AP(KT)5-4-运行状态*)",null,"L15\\L15AHU01E04_R","空调机组NJ-1AP(KT)5-4-运行状态",10908]
[{"$nulls":5},14,null,27,28,"空调机组NJ-1AP(KT)5-4-故障状态",{"$nulls":16},"NJ-1AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-4","01E04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU01E04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU01E04_F AT%I113.5 :BOOL; (*空调机组NJ-1AP(KT)5-4-故障状态*)"},"LAHU01E04_F             AT%I113.5      :BOOL; (*空调机组NJ-1AP(KT)5-4-故障状态*)",null,"L15\\L15AHU01E04_F","空调机组NJ-1AP(KT)5-4-故障状态",10909]
[{"$nulls":5},15,null,29,30,"空调机组NJ-1AP(KT)5-4-自动状态",{"$nulls":16},"NJ-1AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-4","01E04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU01E04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU01E04_A AT%I113.6 :BOOL; (*空调机组NJ-1AP(KT)5-4-自动状态*)"},"LAHU01E04_A             AT%I113.6      :BOOL; (*空调机组NJ-1AP(KT)5-4-自动状态*)",null,"L15\\L15AHU01E04_A","空调机组NJ-1AP(KT)5-4-自动状态",10910]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-1AP(KT)5-4-风机压差",{"$nulls":16},"NJ-1AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-4","01E04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU01E04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU01E04_FPS AT%I113.7 :BOOL; (*空调机组NJ-1AP(KT)5-4-风机压差*)"},"LAHU01E04_FPS           AT%I113.7      :BOOL; (*空调机组NJ-1AP(KT)5-4-风机压差*)",null,"L15\\L15AHU01E04_FPS","空调机组NJ-1AP(KT)5-4-风机压差",10911]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 1601R地址: 8 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH25&AA25&\"-\"&AK25","v":"空调机组NJ-1AP(KT)5-5-运行状态"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-1AP(KT)5-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-5","01E05","运行状态",{"$f":"AH25&\"-\"&AK25","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"AHU01E05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LAHU01E05_R AT%I128.0 :BOOL; (*空调机组NJ-1AP(KT)5-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LAHU01E05_R             AT%I128.0      :BOOL; (*空调机组NJ-1AP(KT)5-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L15\\L15AHU01E05_R"},{"$f":"J25","v":"空调机组NJ-1AP(KT)5-5-运行状态"},{"$f":"10000+($B26*16*8+F25-1)","v":11024}]
[null,8,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-1AP(KT)5-5-故障状态",{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-1AP(KT)5-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-5","01E05","故障状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU01E05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU01E05_F AT%I128.1 :BOOL; (*空调机组NJ-1AP(KT)5-5-故障状态*)"},"LAHU01E05_F             AT%I128.1      :BOOL; (*空调机组NJ-1AP(KT)5-5-故障状态*)",null,"L15\\L15AHU01E05_F",{"$f":"J26","v":"空调机组NJ-1AP(KT)5-5-故障状态"},{"$f":"AS25+1","v":11025}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-1AP(KT)5-5-自动状态",{"$nulls":16},"NJ-1AP(KT)5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-5","01E05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU01E05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU01E05_A AT%I128.2 :BOOL; (*空调机组NJ-1AP(KT)5-5-自动状态*)"},"LAHU01E05_A             AT%I128.2      :BOOL; (*空调机组NJ-1AP(KT)5-5-自动状态*)",null,"L15\\L15AHU01E05_A","空调机组NJ-1AP(KT)5-5-自动状态",{"$f":"AS26+1","v":11026}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-1AP(KT)5-5-风机压差",{"$nulls":16},"NJ-1AP(KT)5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-5","01E05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU01E05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU01E05_FPS AT%I128.3 :BOOL; (*空调机组NJ-1AP(KT)5-5-风机压差*)"},"LAHU01E05_FPS           AT%I128.3      :BOOL; (*空调机组NJ-1AP(KT)5-5-风机压差*)",null,"L15\\L15AHU01E05_FPS","空调机组NJ-1AP(KT)5-5-风机压差",11027]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-1AP(KT)5-6-运行状态",{"$nulls":16},"NJ-1AP(KT)5-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-6","01E06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU01E06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU01E06_R AT%I128.4 :BOOL; (*空调机组NJ-1AP(KT)5-6-运行状态*)"},"LAHU01E06_R             AT%I128.4      :BOOL; (*空调机组NJ-1AP(KT)5-6-运行状态*)",null,"L15\\L15AHU01E06_R","空调机组NJ-1AP(KT)5-6-运行状态",11028]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-1AP(KT)5-6-故障状态",{"$nulls":16},"NJ-1AP(KT)5-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-6","01E06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU01E06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU01E06_F AT%I128.5 :BOOL; (*空调机组NJ-1AP(KT)5-6-故障状态*)"},"LAHU01E06_F             AT%I128.5      :BOOL; (*空调机组NJ-1AP(KT)5-6-故障状态*)",null,"L15\\L15AHU01E06_F","空调机组NJ-1AP(KT)5-6-故障状态",11029]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-1AP(KT)5-6-自动状态",{"$nulls":16},"NJ-1AP(KT)5-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-6","01E06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU01E06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU01E06_A AT%I128.6 :BOOL; (*空调机组NJ-1AP(KT)5-6-自动状态*)"},"LAHU01E06_A             AT%I128.6      :BOOL; (*空调机组NJ-1AP(KT)5-6-自动状态*)",null,"L15\\L15AHU01E06_A","空调机组NJ-1AP(KT)5-6-自动状态",11030]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-1AP(KT)5-6-风机压差",{"$nulls":16},"NJ-1AP(KT)5-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-6","01E06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU01E06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU01E06_FPS AT%I128.7 :BOOL; (*空调机组NJ-1AP(KT)5-6-风机压差*)"},"LAHU01E06_FPS           AT%I128.7      :BOOL; (*空调机组NJ-1AP(KT)5-6-风机压差*)",null,"L15\\L15AHU01E06_FPS","空调机组NJ-1AP(KT)5-6-风机压差",11031]
[{"$nulls":5},9,null,17,18,"空调机组NJ-1AP(KT)5-7-运行状态",{"$nulls":16},"NJ-1AP(KT)5-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-7","01E07","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU01E07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B26*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU01E07_R AT%I129.0 :BOOL; (*空调机组NJ-1AP(KT)5-7-运行状态*)"},"LAHU01E07_R             AT%I129.0      :BOOL; (*空调机组NJ-1AP(KT)5-7-运行状态*)",null,"L15\\L15AHU01E07_R","空调机组NJ-1AP(KT)5-7-运行状态",11032]
[{"$nulls":5},10,null,19,20,"空调机组NJ-1AP(KT)5-7-故障状态",{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-1AP(KT)5-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-7","01E07","故障状态",{"$f":"AH34&\"-\"&AK34","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU01E07_F"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B26*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU01E07_F AT%I129.1 :BOOL; (*空调机组NJ-1AP(KT)5-7-故障状态*)"},"LAHU01E07_F             AT%I129.1      :BOOL; (*空调机组NJ-1AP(KT)5-7-故障状态*)",null,"L15\\L15AHU01E07_F","空调机组NJ-1AP(KT)5-7-故障状态",11033]
[{"$nulls":5},11,null,21,22,"空调机组NJ-1AP(KT)5-7-自动状态",{"$nulls":16},"NJ-1AP(KT)5-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-7","01E07","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU01E07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B26*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU01E07_A AT%I129.2 :BOOL; (*空调机组NJ-1AP(KT)5-7-自动状态*)"},"LAHU01E07_A             AT%I129.2      :BOOL; (*空调机组NJ-1AP(KT)5-7-自动状态*)",null,"L15\\L15AHU01E07_A","空调机组NJ-1AP(KT)5-7-自动状态",11034]
[{"$nulls":5},12,null,23,24,"空调机组NJ-1AP(KT)5-7-风机压差",{"$nulls":16},"NJ-1AP(KT)5-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-7","01E07","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU01E07_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B26*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU01E07_FPS AT%I129.3 :BOOL; (*空调机组NJ-1AP(KT)5-7-风机压差*)"},"LAHU01E07_FPS           AT%I129.3      :BOOL; (*空调机组NJ-1AP(KT)5-7-风机压差*)",null,"L15\\L15AHU01E07_FPS","空调机组NJ-1AP(KT)5-7-风机压差",11035]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-1AL5-1-运行状态",{"$nulls":16},"NJ-1AL5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL5-1","01E01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"LCB01E01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B26*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LLCB01E01_R AT%I129.4 :BOOL; (*照明控制箱NJ-1AL5-1-运行状态*)"},"LLCB01E01_R             AT%I129.4      :BOOL; (*照明控制箱NJ-1AL5-1-运行状态*)",null,"L15\\L15LCB01E01_R","照明控制箱NJ-1AL5-1-运行状态",11036]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-1AL5-1-自动状态",{"$nulls":16},"NJ-1AL5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL5-1","01E01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB01E01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B26*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB01E01_A AT%I129.5 :BOOL; (*照明控制箱NJ-1AL5-1-自动状态*)"},"LLCB01E01_A             AT%I129.5      :BOOL; (*照明控制箱NJ-1AL5-1-自动状态*)",null,"L15\\L15LCB01E01_A","照明控制箱NJ-1AL5-1-自动状态",11037]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-1AL5-2-运行状态",{"$nulls":16},"NJ-1AL5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL5-2","01E02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB01E02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B26*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB01E02_R AT%I129.6 :BOOL; (*照明控制箱NJ-1AL5-2-运行状态*)"},"LLCB01E02_R             AT%I129.6      :BOOL; (*照明控制箱NJ-1AL5-2-运行状态*)",null,"L15\\L15LCB01E02_R","照明控制箱NJ-1AL5-2-运行状态",11038]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-1AL5-2-自动状态",{"$nulls":16},"NJ-1AL5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL5-2","01E02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"LCB01E02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B26*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LLCB01E02_A AT%I129.7 :BOOL; (*照明控制箱NJ-1AL5-2-自动状态*)"},"LLCB01E02_A             AT%I129.7      :BOOL; (*照明控制箱NJ-1AL5-2-自动状态*)",null,"L15\\L15LCB01E02_A","照明控制箱NJ-1AL5-2-自动状态",11039]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B46&\"地址: \"&B43&\" *)\"","v":"(* IOM 1601R地址: 9 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH42&AA42&\"-\"&AK42","v":"照明控制箱NJ-1AL5-3-运行状态"},{"$nulls":16},{"$f":"IF(AI42=\"\",\"\",AI42)","v":"NJ-1AL5-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL5-3","01E03","运行状态",{"$f":"AH42&\"-\"&AK42","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":"LCB01E03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%I\"&B43*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":"LLCB01E03_R AT%I144.0 :BOOL; (*照明控制箱NJ-1AL5-3-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42))),SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))))),\" \")","v":"LLCB01E03_R             AT%I144.0      :BOOL; (*照明控制箱NJ-1AL5-3-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM42","v":"L15\\L15LCB01E03_R"},{"$f":"J42","v":"照明控制箱NJ-1AL5-3-运行状态"},{"$f":"10000+($B43*16*8+F42-1)","v":11152}]
[null,9,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":0},2,null,3,4,"照明控制箱NJ-1AL5-3-自动状态",{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-1AL5-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL5-3","01E03","自动状态",{"$f":"AH43&\"-\"&AK43","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"LCB01E03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B43*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LLCB01E03_A AT%I144.1 :BOOL; (*照明控制箱NJ-1AL5-3-自动状态*)"},"LLCB01E03_A             AT%I144.1      :BOOL; (*照明控制箱NJ-1AL5-3-自动状态*)",null,"L15\\L15LCB01E03_A",{"$f":"J43","v":"照明控制箱NJ-1AL5-3-自动状态"},{"$f":"AS42+1","v":11153}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":0},3,null,5,6,"照明控制箱NJ-1AL5-4-运行状态",{"$nulls":16},"NJ-1AL5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL5-4","01E04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"LCB01E04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B43*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LLCB01E04_R AT%I144.2 :BOOL; (*照明控制箱NJ-1AL5-4-运行状态*)"},"LLCB01E04_R             AT%I144.2      :BOOL; (*照明控制箱NJ-1AL5-4-运行状态*)",null,"L15\\L15LCB01E04_R","照明控制箱NJ-1AL5-4-运行状态",{"$f":"AS43+1","v":11154}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},4,null,7,8,"照明控制箱NJ-1AL5-4-自动状态",{"$nulls":16},"NJ-1AL5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL5-4","01E04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"LCB01E04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B43*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LLCB01E04_A AT%I144.3 :BOOL; (*照明控制箱NJ-1AL5-4-自动状态*)"},"LLCB01E04_A             AT%I144.3      :BOOL; (*照明控制箱NJ-1AL5-4-自动状态*)",null,"L15\\L15LCB01E04_A","照明控制箱NJ-1AL5-4-自动状态",11155]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-1AL5-5-运行状态",{"$nulls":16},"NJ-1AL5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL5-5","01E05","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"LCB01E05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B43*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LLCB01E05_R AT%I144.4 :BOOL; (*照明控制箱NJ-1AL5-5-运行状态*)"},"LLCB01E05_R             AT%I144.4      :BOOL; (*照明控制箱NJ-1AL5-5-运行状态*)",null,"L15\\L15LCB01E05_R","照明控制箱NJ-1AL5-5-运行状态",11156]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-1AL5-5-自动状态",{"$nulls":16},"NJ-1AL5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL5-5","01E05","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"LCB01E05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B43*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LLCB01E05_A AT%I144.5 :BOOL; (*照明控制箱NJ-1AL5-5-自动状态*)"},"LLCB01E05_A             AT%I144.5      :BOOL; (*照明控制箱NJ-1AL5-5-自动状态*)",null,"L15\\L15LCB01E05_A","照明控制箱NJ-1AL5-5-自动状态",11157]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"水幕机NJ-1AP(KT)5-1-运行状态",{"$nulls":16},"NJ-1AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)5-1","01E01","运行状态","水幕机-运行状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"WAC01E01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B43*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LWAC01E01_R AT%I144.6 :BOOL; (*水幕机NJ-1AP(KT)5-1-运行状态*)"},"LWAC01E01_R             AT%I144.6      :BOOL; (*水幕机NJ-1AP(KT)5-1-运行状态*)",null,"L15\\L15WAC01E01_R","水幕机NJ-1AP(KT)5-1-运行状态",11158]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"水幕机NJ-1AP(KT)5-1-故障状态",{"$nulls":16},"NJ-1AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)5-1","01E01","故障状态","水幕机-故障状态",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"WAC01E01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B43*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LWAC01E01_F AT%I144.7 :BOOL; (*水幕机NJ-1AP(KT)5-1-故障状态*)"},"LWAC01E01_F             AT%I144.7      :BOOL; (*水幕机NJ-1AP(KT)5-1-故障状态*)",null,"L15\\L15WAC01E01_F","水幕机NJ-1AP(KT)5-1-故障状态",11159]
[{"$nulls":5},9,null,17,18,"水幕机NJ-1AP(KT)5-1-自动状态",{"$nulls":16},"NJ-1AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)5-1","01E01","自动状态","水幕机-自动状态",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"WAC01E01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B43*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LWAC01E01_A AT%I145.0 :BOOL; (*水幕机NJ-1AP(KT)5-1-自动状态*)"},"LWAC01E01_A             AT%I145.0      :BOOL; (*水幕机NJ-1AP(KT)5-1-自动状态*)",null,"L15\\L15WAC01E01_A","水幕机NJ-1AP(KT)5-1-自动状态",11160]
[{"$nulls":5},10,null,19,20,"水幕机NJ-1AP(KT)5-2-运行状态",{"$nulls":16},{"$f":"IF(AI51=\"\",\"\",AI51)","v":"NJ-1AP(KT)5-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)5-2","01E02","运行状态",{"$f":"AH51&\"-\"&AK51","v":"水幕机-运行状态"},{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"WAC01E02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B43*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LWAC01E02_R AT%I145.1 :BOOL; (*水幕机NJ-1AP(KT)5-2-运行状态*)"},"LWAC01E02_R             AT%I145.1      :BOOL; (*水幕机NJ-1AP(KT)5-2-运行状态*)",null,"L15\\L15WAC01E02_R",{"$f":"J51","v":"水幕机NJ-1AP(KT)5-2-运行状态"},11161]
[{"$nulls":5},11,null,21,22,"水幕机NJ-1AP(KT)5-2-故障状态",{"$nulls":16},"NJ-1AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)5-2","01E02","故障状态","水幕机-故障状态",{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"WAC01E02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%I\"&B43*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LWAC01E02_F AT%I145.2 :BOOL; (*水幕机NJ-1AP(KT)5-2-故障状态*)"},"LWAC01E02_F             AT%I145.2      :BOOL; (*水幕机NJ-1AP(KT)5-2-故障状态*)",null,"L15\\L15WAC01E02_F","水幕机NJ-1AP(KT)5-2-故障状态",11162]
[{"$nulls":5},12,null,23,24,"水幕机NJ-1AP(KT)5-2-自动状态",{"$nulls":16},"NJ-1AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)5-2","01E02","自动状态","水幕机-自动状态",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"WAC01E02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%I\"&B43*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LWAC01E02_A AT%I145.3 :BOOL; (*水幕机NJ-1AP(KT)5-2-自动状态*)"},"LWAC01E02_A             AT%I145.3      :BOOL; (*水幕机NJ-1AP(KT)5-2-自动状态*)",null,"L15\\L15WAC01E02_A","水幕机NJ-1AP(KT)5-2-自动状态",11163]
[{"$nulls":5},13,null,25,26,"水幕机NJ-1AP(KT)5-1-水阀开反馈",{"$nulls":16},"NJ-1AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)5-1","01E01","水阀开反馈","水幕机-水阀开反馈",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"WAC01E01_WVOB"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%I\"&B43*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LWAC01E01_WVOB AT%I145.4 :BOOL; (*水幕机NJ-1AP(KT)5-1-水阀开反馈*)"},"LWAC01E01_WVOB          AT%I145.4      :BOOL; (*水幕机NJ-1AP(KT)5-1-水阀开反馈*)",null,"L15\\L15WAC01E01_WVOB","水幕机NJ-1AP(KT)5-1-水阀开反馈",11164]
[{"$nulls":5},14,null,27,28,"水幕机NJ-1AP(KT)5-1-水阀关反馈",{"$nulls":16},"NJ-1AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)5-1","01E01","水阀关反馈","水幕机-水阀关反馈",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"WAC01E01_WVSB"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%I\"&B43*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LWAC01E01_WVSB AT%I145.5 :BOOL; (*水幕机NJ-1AP(KT)5-1-水阀关反馈*)"},"LWAC01E01_WVSB          AT%I145.5      :BOOL; (*水幕机NJ-1AP(KT)5-1-水阀关反馈*)",null,"L15\\L15WAC01E01_WVSB","水幕机NJ-1AP(KT)5-1-水阀关反馈",11165]
[{"$nulls":5},15,null,29,30,"风机盘管NJ-1AP(KT)5-1-运行状态",{"$nulls":16},"NJ-1AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)5-1","01E01","运行状态","风机盘管-运行状态",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"FCU01E01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%I\"&B43*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LFCU01E01_R AT%I145.6 :BOOL; (*风机盘管NJ-1AP(KT)5-1-运行状态*)"},"LFCU01E01_R             AT%I145.6      :BOOL; (*风机盘管NJ-1AP(KT)5-1-运行状态*)",null,"L15\\L15FCU01E01_R","风机盘管NJ-1AP(KT)5-1-运行状态",11166]
[".",{"$nulls":4},16,null,31,32,"风机盘管NJ-1AP(KT)5-1-自动状态",{"$nulls":16},"NJ-1AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)5-1","01E01","自动状态","风机盘管-自动状态",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"FCU01E01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%I\"&B43*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LFCU01E01_A AT%I145.7 :BOOL; (*风机盘管NJ-1AP(KT)5-1-自动状态*)"},"LFCU01E01_A             AT%I145.7      :BOOL; (*风机盘管NJ-1AP(KT)5-1-自动状态*)",null,"L15\\L15FCU01E01_A","风机盘管NJ-1AP(KT)5-1-自动状态",11167]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B63&\"地址: \"&B60&\" *)\"","v":"(* IOM 0801R 地址: 10 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH59&AA59&\"-\"&AK59","v":"风机盘管NJ-1AP(KT)5-1-电磁阀开启状态"},{"$nulls":16},{"$f":"IF(AI59=\"\",\"\",AI59)","v":"NJ-1AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)5-1","01E01","电磁阀开启状态",{"$f":"AH59&\"-\"&AK59","v":"风机盘管-电磁阀开启状态"},{"$f":"VLOOKUP(AH59,List!$B$3:$D$445,2,FALSE)&AJ59&\"_\"&VLOOKUP(AK59,List!$K$2:$M$447,2,FALSE)","v":"FCU01E01_EVR"},{"$f":"_xlfn.IFNA(\"L\"&AM59&\" \"&\"AT%I\"&B60*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J59&\"*)\",\" \")","v":"LFCU01E01_EVR AT%I160.0 :BOOL; (*风机盘管NJ-1AP(KT)5-1-电磁阀开启状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59))),SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))))),\" \")","v":"LFCU01E01_EVR           AT%I160.0      :BOOL; (*风机盘管NJ-1AP(KT)5-1-电磁阀开启状态*)"},null,{"$f":"AM59","v":"FCU01E01_EVR"},{"$f":"J59","v":"风机盘管NJ-1AP(KT)5-1-电磁阀开启状态"},{"$f":"10000+($B60*16*8+F59-1)","v":11280}]
[null,10,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":1},2,null,2,"C",{"$f":"AH60&AA60&\"-\"&AK60","v":"风机盘管NJ-1AP(KT)5-1-电磁阀自动状态"},{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-1AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)5-1","01E01","电磁阀自动状态",{"$f":"AH60&\"-\"&AK60","v":"风机盘管-电磁阀自动状态"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"FCU01E01_EVA"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%I\"&B60*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LFCU01E01_EVA AT%I160.1 :BOOL; (*风机盘管NJ-1AP(KT)5-1-电磁阀自动状态*)"},"LFCU01E01_EVA           AT%I160.1      :BOOL; (*风机盘管NJ-1AP(KT)5-1-电磁阀自动状态*)",null,{"$f":"AM60","v":"FCU01E01_EVA"},{"$f":"J60","v":"风机盘管NJ-1AP(KT)5-1-电磁阀自动状态"},{"$f":"AS59+1","v":11281}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":0},3,null,3,"C",{"$f":"AH61&AA61&\"-\"&AK61","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%I\"&B60*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN61,SEARCH(\"AT%\",AN61),,REPT(\" \",25-SEARCH(\"AT%\",AN61))),SEARCH(\":\",REPLACE(AN61,SEARCH(\"AT%\",AN61),,REPT(\" \",25-SEARCH(\"AT%\",AN61)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN61,SEARCH(\"AT%\",AN61),,REPT(\" \",25-SEARCH(\"AT%\",AN61)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",{"$f":"AS60+1","v":11282}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},4,null,4,"C",{"$f":"AH62&AA62&\"-\"&AK62","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B60*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11283]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},5,null,5,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B60*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11284]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B60*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11285]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B60*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11286]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B60*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11287]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B72&\"地址: \"&B69&\" *)\"","v":"(* IOM 1601D地址: 11 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH68&AA68&\"-\"&AK68","v":"空调机组NJ-1AP(KT)5-1-启停控制"},{"$nulls":16},{"$f":"IF(AI68=\"\",\"\",AI68)","v":"NJ-1AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-1","01E01","启停控制",{"$f":"AH68&\"-\"&AK68","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"AHU01E01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%Q\"&B69*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LAHU01E01_C AT%Q176.0 :BOOL; (*空调机组NJ-1AP(KT)5-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68))),SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))))),\" \")","v":"LAHU01E01_C             AT%Q176.0      :BOOL; (*空调机组NJ-1AP(KT)5-1-启停控制*)"},null,{"$f":"AM68","v":"AHU01E01_C"},{"$f":"J68","v":"空调机组NJ-1AP(KT)5-1-启停控制"},{"$f":"($B69*16*8+F68-1)","v":1408}]
[null,11,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-1AP(KT)5-2-启停控制",{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-1AP(KT)5-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-2","01E02","启停控制",{"$f":"AH69&\"-\"&AK69","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU01E02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%Q\"&B69*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU01E02_C AT%Q176.1 :BOOL; (*空调机组NJ-1AP(KT)5-2-启停控制*)"},"LAHU01E02_C             AT%Q176.1      :BOOL; (*空调机组NJ-1AP(KT)5-2-启停控制*)",null,"AHU01E02_C",{"$f":"J69","v":"空调机组NJ-1AP(KT)5-2-启停控制"},{"$f":"AS68+1","v":1409}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","空调机组NJ-1AP(KT)5-3-启停控制",{"$nulls":16},"NJ-1AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-3","01E03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"AHU01E03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%Q\"&B69*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LAHU01E03_C AT%Q176.2 :BOOL; (*空调机组NJ-1AP(KT)5-3-启停控制*)"},"LAHU01E03_C             AT%Q176.2      :BOOL; (*空调机组NJ-1AP(KT)5-3-启停控制*)",null,"AHU01E03_C","空调机组NJ-1AP(KT)5-3-启停控制",{"$f":"AS69+1","v":1410}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","空调机组NJ-1AP(KT)5-4-启停控制",{"$nulls":16},"NJ-1AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-4","01E04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"AHU01E04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%Q\"&B69*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LAHU01E04_C AT%Q176.3 :BOOL; (*空调机组NJ-1AP(KT)5-4-启停控制*)"},"LAHU01E04_C             AT%Q176.3      :BOOL; (*空调机组NJ-1AP(KT)5-4-启停控制*)",null,"AHU01E04_C","空调机组NJ-1AP(KT)5-4-启停控制",1411]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-1AP(KT)5-5-启停控制",{"$nulls":16},"NJ-1AP(KT)5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-5","01E05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"AHU01E05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%Q\"&B69*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LAHU01E05_C AT%Q176.4 :BOOL; (*空调机组NJ-1AP(KT)5-5-启停控制*)"},"LAHU01E05_C             AT%Q176.4      :BOOL; (*空调机组NJ-1AP(KT)5-5-启停控制*)",null,"AHU01E05_C","空调机组NJ-1AP(KT)5-5-启停控制",1412]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-1AP(KT)5-6-启停控制",{"$nulls":16},"NJ-1AP(KT)5-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-6","01E06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"AHU01E06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%Q\"&B69*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LAHU01E06_C AT%Q176.5 :BOOL; (*空调机组NJ-1AP(KT)5-6-启停控制*)"},"LAHU01E06_C             AT%Q176.5      :BOOL; (*空调机组NJ-1AP(KT)5-6-启停控制*)",null,"AHU01E06_C","空调机组NJ-1AP(KT)5-6-启停控制",1413]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","空调机组NJ-1AP(KT)5-7-启停控制",{"$nulls":16},"NJ-1AP(KT)5-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-7","01E07","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":"AHU01E07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%Q\"&B69*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":"LAHU01E07_C AT%Q176.6 :BOOL; (*空调机组NJ-1AP(KT)5-7-启停控制*)"},"LAHU01E07_C             AT%Q176.6      :BOOL; (*空调机组NJ-1AP(KT)5-7-启停控制*)",null,"AHU01E07_C","空调机组NJ-1AP(KT)5-7-启停控制",1414]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-1AL5-1-启停控制",{"$nulls":16},"NJ-1AL5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL5-1","01E01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":"LCB01E01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%Q\"&B69*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":"LLCB01E01_C AT%Q176.7 :BOOL; (*照明控制箱NJ-1AL5-1-启停控制*)"},"LLCB01E01_C             AT%Q176.7      :BOOL; (*照明控制箱NJ-1AL5-1-启停控制*)",null,"LCB01E01_C","照明控制箱NJ-1AL5-1-启停控制",1415]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-1AL5-2-启停控制",{"$nulls":16},"NJ-1AL5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL5-2","01E02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH76,List!$B$3:$D$445,2,FALSE)&AJ76&\"_\"&VLOOKUP(AK76,List!$K$2:$M$447,2,FALSE)","v":"LCB01E02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM76&\" \"&\"AT%Q\"&B69*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J76&\"*)\",\" \")","v":"LLCB01E02_C AT%Q177.0 :BOOL; (*照明控制箱NJ-1AL5-2-启停控制*)"},"LLCB01E02_C             AT%Q177.0      :BOOL; (*照明控制箱NJ-1AL5-2-启停控制*)",null,"LCB01E02_C","照明控制箱NJ-1AL5-2-启停控制",1416]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-1AL5-3-启停控制",{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-1AL5-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL5-3","01E03","启停控制",{"$f":"AH77&\"-\"&AK77","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"LCB01E03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%Q\"&B69*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LLCB01E03_C AT%Q177.1 :BOOL; (*照明控制箱NJ-1AL5-3-启停控制*)"},"LLCB01E03_C             AT%Q177.1      :BOOL; (*照明控制箱NJ-1AL5-3-启停控制*)",null,"LCB01E03_C",{"$f":"J77","v":"照明控制箱NJ-1AL5-3-启停控制"},1417]
[{"$nulls":5},11,null,"11+","11-","照明控制箱NJ-1AL5-4-启停控制",{"$nulls":16},"NJ-1AL5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL5-4","01E04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"LCB01E04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B69*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LLCB01E04_C AT%Q177.2 :BOOL; (*照明控制箱NJ-1AL5-4-启停控制*)"},"LLCB01E04_C             AT%Q177.2      :BOOL; (*照明控制箱NJ-1AL5-4-启停控制*)",null,"LCB01E04_C","照明控制箱NJ-1AL5-4-启停控制",1418]
[{"$nulls":5},12,null,"12+","12-","照明控制箱NJ-1AL5-5-启停控制",{"$nulls":16},"NJ-1AL5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL5-5","01E05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"LCB01E05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B69*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LLCB01E05_C AT%Q177.3 :BOOL; (*照明控制箱NJ-1AL5-5-启停控制*)"},"LLCB01E05_C             AT%Q177.3      :BOOL; (*照明控制箱NJ-1AL5-5-启停控制*)",null,"LCB01E05_C","照明控制箱NJ-1AL5-5-启停控制",1419]
[{"$nulls":5},13,null,"13+","13-","水幕机NJ-1AP(KT)5-1-启停控制",{"$nulls":16},"NJ-1AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)5-1","01E01","启停控制","水幕机-启停控制",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"WAC01E01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B69*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LWAC01E01_C AT%Q177.4 :BOOL; (*水幕机NJ-1AP(KT)5-1-启停控制*)"},"LWAC01E01_C             AT%Q177.4      :BOOL; (*水幕机NJ-1AP(KT)5-1-启停控制*)",null,"WAC01E01_C","水幕机NJ-1AP(KT)5-1-启停控制",1420]
[{"$nulls":5},14,null,"14+","14-","水幕机NJ-1AP(KT)5-2-启停控制",{"$nulls":16},"NJ-1AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)5-2","01E02","启停控制","水幕机-启停控制",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"WAC01E02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%Q\"&B69*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LWAC01E02_C AT%Q177.5 :BOOL; (*水幕机NJ-1AP(KT)5-2-启停控制*)"},"LWAC01E02_C             AT%Q177.5      :BOOL; (*水幕机NJ-1AP(KT)5-2-启停控制*)",null,"WAC01E02_C","水幕机NJ-1AP(KT)5-2-启停控制",1421]
[{"$nulls":5},15,null,"15+","15-","水幕机NJ-1AP(KT)5-1-水阀控制",{"$nulls":16},"NJ-1AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"水幕机","NJ-1AP(KT)5-1","01E01","水阀控制","水幕机-水阀控制",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":"WAC01E01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%Q\"&B69*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":"LWAC01E01_WVC AT%Q177.6 :BOOL; (*水幕机NJ-1AP(KT)5-1-水阀控制*)"},"LWAC01E01_WVC           AT%Q177.6      :BOOL; (*水幕机NJ-1AP(KT)5-1-水阀控制*)",null,"WAC01E01_WVC","水幕机NJ-1AP(KT)5-1-水阀控制",1422]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%Q\"&B69*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1423]
[null,"IOM 0801D",{"$nulls":38},{"$f":"\"(* \"&B89&\"地址: \"&B86&\" *)\"","v":"(* IOM 0801D地址: 12 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH85&AA85&\"-\"&AK85","v":"风机盘管NJ-1AP(KT)5-1-启停控制"},{"$nulls":16},{"$f":"IF(AI85=\"\",\"\",AI85)","v":"NJ-1AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)5-1","01E01","启停控制",{"$f":"AH85&\"-\"&AK85","v":"风机盘管-启停控制"},{"$f":"VLOOKUP(AH85,List!$B$3:$D$445,2,FALSE)&AJ85&\"_\"&VLOOKUP(AK85,List!$K$2:$M$447,2,FALSE)","v":"FCU01E01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM85&\" \"&\"AT%Q\"&B86*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J85&\"*)\",\" \")","v":"LFCU01E01_C AT%Q192.0 :BOOL; (*风机盘管NJ-1AP(KT)5-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN85,SEARCH(\"AT%\",AN85),,REPT(\" \",25-SEARCH(\"AT%\",AN85))),SEARCH(\":\",REPLACE(AN85,SEARCH(\"AT%\",AN85),,REPT(\" \",25-SEARCH(\"AT%\",AN85)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN85,SEARCH(\"AT%\",AN85),,REPT(\" \",25-SEARCH(\"AT%\",AN85)))))),\" \")","v":"LFCU01E01_C             AT%Q192.0      :BOOL; (*风机盘管NJ-1AP(KT)5-1-启停控制*)"},null,{"$f":"AM85","v":"FCU01E01_C"},{"$f":"J85","v":"风机盘管NJ-1AP(KT)5-1-启停控制"},{"$f":"($B86*16*8+F85-1)","v":1536}]
[null,12,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","风机盘管NJ-1AP(KT)5-1-电磁阀开关控制",{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-1AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)5-1","01E01","电磁阀开关控制",{"$f":"AH86&\"-\"&AK86","v":"风机盘管-电磁阀开关控制"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"FCU01E01_EVC"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%Q\"&B86*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LFCU01E01_EVC AT%Q192.1 :BOOL; (*风机盘管NJ-1AP(KT)5-1-电磁阀开关控制*)"},"LFCU01E01_EVC           AT%Q192.1      :BOOL; (*风机盘管NJ-1AP(KT)5-1-电磁阀开关控制*)",null,"FCU01E01_EVC",{"$f":"J86","v":"风机盘管NJ-1AP(KT)5-1-电磁阀开关控制"},{"$f":"AS85+1","v":1537}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%Q\"&B86*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS86+1","v":1538}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%Q\"&B86*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1539]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%Q\"&B86*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1540]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%Q\"&B86*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1541]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH91,List!$B$3:$D$445,2,FALSE)&AJ91&\"_\"&VLOOKUP(AK91,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM91&\" \"&\"AT%Q\"&B86*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J91&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1542]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH92,List!$B$3:$D$445,2,FALSE)&AJ92&\"_\"&VLOOKUP(AK92,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM92&\" \"&\"AT%Q\"&B86*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J92&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1543]
[null,{"$f":"B98","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B98&\"地址: \"&B95&\" *)\"","v":"(* IOM 0801U地址: 13 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH94&AA94&\"-\"&AK94","v":"空调机组NJ-1AP(KT)5-1-回风温度"},{"$nulls":16},{"$f":"IF(AI94=\"\",\"\",AI94)","v":"NJ-1AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-1","01E01","回风温度",{"$f":"AH94&\"-\"&AK94","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH94,List!$B$3:$D$445,2,FALSE)&AJ94&\"_\"&VLOOKUP(AK94,List!$K$2:$M$447,2,FALSE)","v":"AHU01E01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM94&\" \"&\"AT%I\"&B95*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J94&\"*)\",\" \")","v":"LAHU01E01_RT AT%I208.0 :INT ; (*空调机组NJ-1AP(KT)5-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94))),SEARCH(\":\",REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94)))))),\" \")","v":"LAHU01E01_RT            AT%I208.0      :INT ; (*空调机组NJ-1AP(KT)5-1-回风温度*)"},null,{"$f":"AM94","v":"AHU01E01_RT"},{"$f":"J94","v":"空调机组NJ-1AP(KT)5-1-回风温度"},{"$f":"30000+($B95*8+F94-1)","v":30104}]
[null,13,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-1AP(KT)5-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-1AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-1","01E01","水阀反馈",{"$f":"AH95&\"-\"&AK95","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"AHU01E01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%I\"&B95*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LAHU01E01_WVB AT%I210.0 :INT ; (*空调机组NJ-1AP(KT)5-1-水阀反馈*)"},"LAHU01E01_WVB           AT%I210.0      :INT ; (*空调机组NJ-1AP(KT)5-1-水阀反馈*)",null,"AHU01E01_WVB",{"$f":"J95","v":"空调机组NJ-1AP(KT)5-1-水阀反馈"},{"$f":"AS94+1","v":30105}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-1AP(KT)5-2-回风温度",{"$nulls":16},"NJ-1AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-2","01E02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"AHU01E02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%I\"&B95*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LAHU01E02_RT AT%I212.0 :INT ; (*空调机组NJ-1AP(KT)5-2-回风温度*)"},"LAHU01E02_RT            AT%I212.0      :INT ; (*空调机组NJ-1AP(KT)5-2-回风温度*)",null,"AHU01E02_RT","空调机组NJ-1AP(KT)5-2-回风温度",{"$f":"AS95+1","v":30106}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-1AP(KT)5-2-水阀反馈",{"$nulls":16},"NJ-1AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-2","01E02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":"AHU01E02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%I\"&B95*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":"LAHU01E02_WVB AT%I214.0 :INT ; (*空调机组NJ-1AP(KT)5-2-水阀反馈*)"},"LAHU01E02_WVB           AT%I214.0      :INT ; (*空调机组NJ-1AP(KT)5-2-水阀反馈*)",null,"AHU01E02_WVB","空调机组NJ-1AP(KT)5-2-水阀反馈",30107]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-1AP(KT)5-3-回风温度",{"$nulls":16},"NJ-1AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-3","01E03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":"AHU01E03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%I\"&B95*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":"LAHU01E03_RT AT%I216.0 :INT ; (*空调机组NJ-1AP(KT)5-3-回风温度*)"},"LAHU01E03_RT            AT%I216.0      :INT ; (*空调机组NJ-1AP(KT)5-3-回风温度*)",null,"AHU01E03_RT","空调机组NJ-1AP(KT)5-3-回风温度",30108]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-1AP(KT)5-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI99=\"\",\"\",AI99)","v":"NJ-1AP(KT)5-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-3","01E03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH99,List!$B$3:$D$445,2,FALSE)&AJ99&\"_\"&VLOOKUP(AK99,List!$K$2:$M$447,2,FALSE)","v":"AHU01E03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM99&\" \"&\"AT%I\"&B95*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J99&\"*)\",\" \")","v":"LAHU01E03_WVB AT%I218.0 :INT ; (*空调机组NJ-1AP(KT)5-3-水阀反馈*)"},"LAHU01E03_WVB           AT%I218.0      :INT ; (*空调机组NJ-1AP(KT)5-3-水阀反馈*)",null,"AHU01E03_WVB",{"$f":"J99","v":"空调机组NJ-1AP(KT)5-3-水阀反馈"},30109]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-1AP(KT)5-4-回风温度",{"$nulls":16},"NJ-1AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-4","01E04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH100,List!$B$3:$D$445,2,FALSE)&AJ100&\"_\"&VLOOKUP(AK100,List!$K$2:$M$447,2,FALSE)","v":"AHU01E04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM100&\" \"&\"AT%I\"&B95*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J100&\"*)\",\" \")","v":"LAHU01E04_RT AT%I220.0 :INT ; (*空调机组NJ-1AP(KT)5-4-回风温度*)"},"LAHU01E04_RT            AT%I220.0      :INT ; (*空调机组NJ-1AP(KT)5-4-回风温度*)",null,"AHU01E04_RT","空调机组NJ-1AP(KT)5-4-回风温度",30110]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-1AP(KT)5-4-水阀反馈",{"$nulls":16},"NJ-1AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-4","01E04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH101,List!$B$3:$D$445,2,FALSE)&AJ101&\"_\"&VLOOKUP(AK101,List!$K$2:$M$447,2,FALSE)","v":"AHU01E04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM101&\" \"&\"AT%I\"&B95*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J101&\"*)\",\" \")","v":"LAHU01E04_WVB AT%I222.0 :INT ; (*空调机组NJ-1AP(KT)5-4-水阀反馈*)"},"LAHU01E04_WVB           AT%I222.0      :INT ; (*空调机组NJ-1AP(KT)5-4-水阀反馈*)",null,"AHU01E04_WVB","空调机组NJ-1AP(KT)5-4-水阀反馈",30111]
[null,{"$f":"B107","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B107&\"地址: \"&B104&\" *)\"","v":"(* IOM 0801U地址: 14 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH103&AA103&\"-\"&AK103","v":"空调机组NJ-1AP(KT)5-5-回风温度"},{"$nulls":16},{"$f":"IF(AI103=\"\",\"\",AI103)","v":"NJ-1AP(KT)5-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-5","01E05","回风温度",{"$f":"AH103&\"-\"&AK103","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH103,List!$B$3:$D$445,2,FALSE)&AJ103&\"_\"&VLOOKUP(AK103,List!$K$2:$M$447,2,FALSE)","v":"AHU01E05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM103&\" \"&\"AT%I\"&B104*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J103&\"*)\",\" \")","v":"LAHU01E05_RT AT%I224.0 :INT ; (*空调机组NJ-1AP(KT)5-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103))),SEARCH(\":\",REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103)))))),\" \")","v":"LAHU01E05_RT            AT%I224.0      :INT ; (*空调机组NJ-1AP(KT)5-5-回风温度*)"},null,{"$f":"AM103","v":"AHU01E05_RT"},{"$f":"J103","v":"空调机组NJ-1AP(KT)5-5-回风温度"},{"$f":"30000+($B104*8+F103-1)","v":30112}]
[null,14,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-1AP(KT)5-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI104=\"\",\"\",AI104)","v":"NJ-1AP(KT)5-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-5","01E05","水阀反馈",{"$f":"AH104&\"-\"&AK104","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"AHU01E05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%I\"&B104*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LAHU01E05_WVB AT%I226.0 :INT ; (*空调机组NJ-1AP(KT)5-5-水阀反馈*)"},"LAHU01E05_WVB           AT%I226.0      :INT ; (*空调机组NJ-1AP(KT)5-5-水阀反馈*)",null,"AHU01E05_WVB",{"$f":"J104","v":"空调机组NJ-1AP(KT)5-5-水阀反馈"},{"$f":"AS103+1","v":30113}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-1AP(KT)5-6-回风温度",{"$nulls":16},"NJ-1AP(KT)5-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-6","01E06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"AHU01E06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%I\"&B104*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LAHU01E06_RT AT%I228.0 :INT ; (*空调机组NJ-1AP(KT)5-6-回风温度*)"},"LAHU01E06_RT            AT%I228.0      :INT ; (*空调机组NJ-1AP(KT)5-6-回风温度*)",null,"AHU01E06_RT","空调机组NJ-1AP(KT)5-6-回风温度",{"$f":"AS104+1","v":30114}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-1AP(KT)5-6-水阀反馈",{"$nulls":16},"NJ-1AP(KT)5-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-6","01E06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":"AHU01E06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%I\"&B104*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":"LAHU01E06_WVB AT%I230.0 :INT ; (*空调机组NJ-1AP(KT)5-6-水阀反馈*)"},"LAHU01E06_WVB           AT%I230.0      :INT ; (*空调机组NJ-1AP(KT)5-6-水阀反馈*)",null,"AHU01E06_WVB","空调机组NJ-1AP(KT)5-6-水阀反馈",30115]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-1AP(KT)5-7-回风温度",{"$nulls":16},"NJ-1AP(KT)5-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-7","01E07","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH107,List!$B$3:$D$445,2,FALSE)&AJ107&\"_\"&VLOOKUP(AK107,List!$K$2:$M$447,2,FALSE)","v":"AHU01E07_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM107&\" \"&\"AT%I\"&B104*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J107&\"*)\",\" \")","v":"LAHU01E07_RT AT%I232.0 :INT ; (*空调机组NJ-1AP(KT)5-7-回风温度*)"},"LAHU01E07_RT            AT%I232.0      :INT ; (*空调机组NJ-1AP(KT)5-7-回风温度*)",null,"AHU01E07_RT","空调机组NJ-1AP(KT)5-7-回风温度",30116]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-1AP(KT)5-7-水阀反馈",{"$nulls":16},{"$f":"IF(AI108=\"\",\"\",AI108)","v":"NJ-1AP(KT)5-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-7","01E07","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH108,List!$B$3:$D$445,2,FALSE)&AJ108&\"_\"&VLOOKUP(AK108,List!$K$2:$M$447,2,FALSE)","v":"AHU01E07_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM108&\" \"&\"AT%I\"&B104*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J108&\"*)\",\" \")","v":"LAHU01E07_WVB AT%I234.0 :INT ; (*空调机组NJ-1AP(KT)5-7-水阀反馈*)"},"LAHU01E07_WVB           AT%I234.0      :INT ; (*空调机组NJ-1AP(KT)5-7-水阀反馈*)",null,"AHU01E07_WVB",{"$f":"J108","v":"空调机组NJ-1AP(KT)5-7-水阀反馈"},30117]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","风机盘管NJ-1AP(KT)5-1-温度状态",{"$nulls":16},"NJ-1AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)5-1","01E01","温度状态","风机盘管-温度状态",{"$f":"VLOOKUP(AH109,List!$B$3:$D$445,2,FALSE)&AJ109&\"_\"&VLOOKUP(AK109,List!$K$2:$M$447,2,FALSE)","v":"FCU01E01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM109&\" \"&\"AT%I\"&B104*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J109&\"*)\",\" \")","v":"LFCU01E01_T AT%I236.0 :INT ; (*风机盘管NJ-1AP(KT)5-1-温度状态*)"},"LFCU01E01_T             AT%I236.0      :INT ; (*风机盘管NJ-1AP(KT)5-1-温度状态*)",null,"FCU01E01_T","风机盘管NJ-1AP(KT)5-1-温度状态",30118]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL110,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL110,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH110,List!$B$3:$D$445,2,FALSE)&AJ110&\"_\"&VLOOKUP(AK110,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM110&\" \"&\"AT%I\"&B104*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J110&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30119]
[null,{"$f":"B116","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B116&\"地址: \"&B113&\" *)\"","v":"(* IOM 0401A地址: 15 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH112&AA112&\"-\"&AK112","v":"空调机组NJ-1AP(KT)5-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI112=\"\",\"\",AI112)","v":"NJ-1AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-1","01E01","水阀控制",{"$f":"AH112&\"-\"&AK112","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH112,List!$B$3:$D$445,2,FALSE)&AJ112&\"_\"&VLOOKUP(AK112,List!$K$2:$M$447,2,FALSE)","v":"AHU01E01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM112&\" \"&\"AT%Q\"&B113*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J112&\"*)\",\" \")","v":"LAHU01E01_WVC AT%Q240.0 :INT ; (*空调机组NJ-1AP(KT)5-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112))),SEARCH(\":\",REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112)))))),\" \")","v":"LAHU01E01_WVC           AT%Q240.0      :INT ; (*空调机组NJ-1AP(KT)5-1-水阀控制*)"},null,{"$f":"AM112","v":"AHU01E01_WVC"},{"$f":"J112","v":"空调机组NJ-1AP(KT)5-1-水阀控制"},{"$f":"40000+($B113*8+F112-1)","v":40120}]
[null,15,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH113&AA113&\"-\"&AK113","v":"空调机组NJ-1AP(KT)5-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI113=\"\",\"\",AI113)","v":"NJ-1AP(KT)5-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-2","01E02","水阀控制",{"$f":"AH113&\"-\"&AK113","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH113,List!$B$3:$D$445,2,FALSE)&AJ113&\"_\"&VLOOKUP(AK113,List!$K$2:$M$447,2,FALSE)","v":"AHU01E02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM113&\" \"&\"AT%Q\"&B113*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J113&\"*)\",\" \")","v":"LAHU01E02_WVC AT%Q242.0 :INT ; (*空调机组NJ-1AP(KT)5-2-水阀控制*)"},"LAHU01E02_WVC           AT%Q242.0      :INT ; (*空调机组NJ-1AP(KT)5-2-水阀控制*)",null,"AHU01E02_WVC",{"$f":"J113","v":"空调机组NJ-1AP(KT)5-2-水阀控制"},{"$f":"AS112+1","v":40121}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH114&AA114&\"-\"&AK114","v":"空调机组NJ-1AP(KT)5-3-水阀控制"},{"$nulls":16},"NJ-1AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-3","01E03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH114,List!$B$3:$D$445,2,FALSE)&AJ114&\"_\"&VLOOKUP(AK114,List!$K$2:$M$447,2,FALSE)","v":"AHU01E03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM114&\" \"&\"AT%Q\"&B113*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J114&\"*)\",\" \")","v":"LAHU01E03_WVC AT%Q244.0 :INT ; (*空调机组NJ-1AP(KT)5-3-水阀控制*)"},"LAHU01E03_WVC           AT%Q244.0      :INT ; (*空调机组NJ-1AP(KT)5-3-水阀控制*)",null,"AHU01E03_WVC","空调机组NJ-1AP(KT)5-3-水阀控制",{"$f":"AS113+1","v":40122}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH115&AA115&\"-\"&AK115","v":"空调机组NJ-1AP(KT)5-4-水阀控制"},{"$nulls":16},"NJ-1AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-4","01E04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH115,List!$B$3:$D$445,2,FALSE)&AJ115&\"_\"&VLOOKUP(AK115,List!$K$2:$M$447,2,FALSE)","v":"AHU01E04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM115&\" \"&\"AT%Q\"&B113*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J115&\"*)\",\" \")","v":"LAHU01E04_WVC AT%Q246.0 :INT ; (*空调机组NJ-1AP(KT)5-4-水阀控制*)"},"LAHU01E04_WVC           AT%Q246.0      :INT ; (*空调机组NJ-1AP(KT)5-4-水阀控制*)",null,"AHU01E04_WVC","空调机组NJ-1AP(KT)5-4-水阀控制",40123]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B125","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B125&\"地址: \"&B122&\" *)\"","v":"(* IOM 0401A地址: 16 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH121&AA121&\"-\"&AK121","v":"空调机组NJ-1AP(KT)5-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI121=\"\",\"\",AI121)","v":"NJ-1AP(KT)5-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-5","01E05","水阀控制",{"$f":"AH121&\"-\"&AK121","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH121,List!$B$3:$D$445,2,FALSE)&AJ121&\"_\"&VLOOKUP(AK121,List!$K$2:$M$447,2,FALSE)","v":"AHU01E05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM121&\" \"&\"AT%Q\"&B122*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J121&\"*)\",\" \")","v":"LAHU01E05_WVC AT%Q256.0 :INT ; (*空调机组NJ-1AP(KT)5-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121))),SEARCH(\":\",REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121)))))),\" \")","v":"LAHU01E05_WVC           AT%Q256.0      :INT ; (*空调机组NJ-1AP(KT)5-5-水阀控制*)"},null,{"$f":"AM121","v":"AHU01E05_WVC"},{"$f":"J121","v":"空调机组NJ-1AP(KT)5-5-水阀控制"},{"$f":"40000+($B122*8+F121-1)","v":40128}]
[null,16,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH122&AA122&\"-\"&AK122","v":"空调机组NJ-1AP(KT)5-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI122=\"\",\"\",AI122)","v":"NJ-1AP(KT)5-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-6","01E06","水阀控制",{"$f":"AH122&\"-\"&AK122","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH122,List!$B$3:$D$445,2,FALSE)&AJ122&\"_\"&VLOOKUP(AK122,List!$K$2:$M$447,2,FALSE)","v":"AHU01E06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM122&\" \"&\"AT%Q\"&B122*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J122&\"*)\",\" \")","v":"LAHU01E06_WVC AT%Q258.0 :INT ; (*空调机组NJ-1AP(KT)5-6-水阀控制*)"},"LAHU01E06_WVC           AT%Q258.0      :INT ; (*空调机组NJ-1AP(KT)5-6-水阀控制*)",null,"AHU01E06_WVC",{"$f":"J122","v":"空调机组NJ-1AP(KT)5-6-水阀控制"},{"$f":"AS121+1","v":40129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH123&AA123&\"-\"&AK123","v":"空调机组NJ-1AP(KT)5-7-水阀控制"},{"$nulls":16},{"$f":"IF(AI123=\"\",\"\",AI123)","v":"NJ-1AP(KT)5-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)5-7","01E07","水阀控制",{"$f":"AH123&\"-\"&AK123","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH123,List!$B$3:$D$445,2,FALSE)&AJ123&\"_\"&VLOOKUP(AK123,List!$K$2:$M$447,2,FALSE)","v":"AHU01E07_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM123&\" \"&\"AT%Q\"&B122*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J123&\"*)\",\" \")","v":"LAHU01E07_WVC AT%Q260.0 :INT ; (*空调机组NJ-1AP(KT)5-7-水阀控制*)"},"LAHU01E07_WVC           AT%Q260.0      :INT ; (*空调机组NJ-1AP(KT)5-7-水阀控制*)",null,"AHU01E07_WVC","空调机组NJ-1AP(KT)5-7-水阀控制",{"$f":"AS122+1","v":40130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH124&AA124&\"-\"&AK124","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH124,List!$B$3:$D$445,2,FALSE)&AJ124&\"_\"&VLOOKUP(AK124,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM124&\" \"&\"AT%Q\"&B122*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J124&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40131]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L206","index":15,"n_rows":76,"n_cols":45,"rows_kept":76,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[6,1,6,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[75,5,75,6],[75,9,75,25],[4,1,5,1],[12,1,23,1],[29,1,40,1],[46,1,57,1],[63,1,66,1],[72,1,75,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[16,2,23,4],[33,2,40,4],[50,2,57,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L16",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"EXC-1000"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B13&\"地址: \"&B10&\" *)\"","v":"(* IOM 1601R地址: 0 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH9&AA9&\"-\"&AK9","v":"空调机组NJ-2AP(KT)6-1-运行状态"},{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-2AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-1","02F01","运行状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU02F01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B10*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU02F01_R AT%I0.0 :BOOL; (*空调机组NJ-2AP(KT)6-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9))),SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))))),\" \")","v":"LAHU02F01_R             AT%I0.0        :BOOL; (*空调机组NJ-2AP(KT)6-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM9","v":"L16\\L16AHU02F01_R"},{"$f":"J9","v":"空调机组NJ-2AP(KT)6-1-运行状态"},{"$f":"10000+($B10*16*8+F9-1)","v":10000}]
[null,0,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-2AP(KT)6-1-故障状态",{"$nulls":16},{"$f":"IF(AI10=\"\",\"\",AI10)","v":"NJ-2AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-1","02F01","故障状态",{"$f":"AH10&\"-\"&AK10","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU02F01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B10*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU02F01_F AT%I0.1 :BOOL; (*空调机组NJ-2AP(KT)6-1-故障状态*)"},"LAHU02F01_F             AT%I0.1        :BOOL; (*空调机组NJ-2AP(KT)6-1-故障状态*)",null,"L16\\L16AHU02F01_F",{"$f":"J10","v":"空调机组NJ-2AP(KT)6-1-故障状态"},{"$f":"AS9+1","v":10001}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-2AP(KT)6-1-自动状态",{"$nulls":16},"NJ-2AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-1","02F01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU02F01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B10*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU02F01_A AT%I0.2 :BOOL; (*空调机组NJ-2AP(KT)6-1-自动状态*)"},"LAHU02F01_A             AT%I0.2        :BOOL; (*空调机组NJ-2AP(KT)6-1-自动状态*)",null,"L16\\L16AHU02F01_A","空调机组NJ-2AP(KT)6-1-自动状态",{"$f":"AS10+1","v":10002}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-2AP(KT)6-1-风机压差",{"$nulls":16},"NJ-2AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-1","02F01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU02F01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B10*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU02F01_FPS AT%I0.3 :BOOL; (*空调机组NJ-2AP(KT)6-1-风机压差*)"},"LAHU02F01_FPS           AT%I0.3        :BOOL; (*空调机组NJ-2AP(KT)6-1-风机压差*)",null,"L16\\L16AHU02F01_FPS","空调机组NJ-2AP(KT)6-1-风机压差",10003]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-2AP(KT)6-2-运行状态",{"$nulls":16},"NJ-2AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-2","02F02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU02F02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B10*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU02F02_R AT%I0.4 :BOOL; (*空调机组NJ-2AP(KT)6-2-运行状态*)"},"LAHU02F02_R             AT%I0.4        :BOOL; (*空调机组NJ-2AP(KT)6-2-运行状态*)",null,"L16\\L16AHU02F02_R","空调机组NJ-2AP(KT)6-2-运行状态",10004]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-2AP(KT)6-2-故障状态",{"$nulls":16},"NJ-2AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-2","02F02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU02F02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B10*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU02F02_F AT%I0.5 :BOOL; (*空调机组NJ-2AP(KT)6-2-故障状态*)"},"LAHU02F02_F             AT%I0.5        :BOOL; (*空调机组NJ-2AP(KT)6-2-故障状态*)",null,"L16\\L16AHU02F02_F","空调机组NJ-2AP(KT)6-2-故障状态",10005]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-2AP(KT)6-2-自动状态",{"$nulls":16},"NJ-2AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-2","02F02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU02F02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B10*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU02F02_A AT%I0.6 :BOOL; (*空调机组NJ-2AP(KT)6-2-自动状态*)"},"LAHU02F02_A             AT%I0.6        :BOOL; (*空调机组NJ-2AP(KT)6-2-自动状态*)",null,"L16\\L16AHU02F02_A","空调机组NJ-2AP(KT)6-2-自动状态",10006]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-2AP(KT)6-2-风机压差",{"$nulls":16},"NJ-2AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-2","02F02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU02F02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B10*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU02F02_FPS AT%I0.7 :BOOL; (*空调机组NJ-2AP(KT)6-2-风机压差*)"},"LAHU02F02_FPS           AT%I0.7        :BOOL; (*空调机组NJ-2AP(KT)6-2-风机压差*)",null,"L16\\L16AHU02F02_FPS","空调机组NJ-2AP(KT)6-2-风机压差",10007]
[{"$nulls":5},9,null,17,18,"空调机组NJ-2AP(KT)6-3-运行状态",{"$nulls":16},"NJ-2AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-3","02F03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU02F03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B10*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU02F03_R AT%I1.0 :BOOL; (*空调机组NJ-2AP(KT)6-3-运行状态*)"},"LAHU02F03_R             AT%I1.0        :BOOL; (*空调机组NJ-2AP(KT)6-3-运行状态*)",null,"L16\\L16AHU02F03_R","空调机组NJ-2AP(KT)6-3-运行状态",10008]
[{"$nulls":5},10,null,19,20,"空调机组NJ-2AP(KT)6-3-故障状态",{"$nulls":16},{"$f":"IF(AI18=\"\",\"\",AI18)","v":"NJ-2AP(KT)6-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-3","02F03","故障状态",{"$f":"AH18&\"-\"&AK18","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU02F03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B10*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU02F03_F AT%I1.1 :BOOL; (*空调机组NJ-2AP(KT)6-3-故障状态*)"},"LAHU02F03_F             AT%I1.1        :BOOL; (*空调机组NJ-2AP(KT)6-3-故障状态*)",null,"L16\\L16AHU02F03_F","空调机组NJ-2AP(KT)6-3-故障状态",10009]
[{"$nulls":5},11,null,21,22,"空调机组NJ-2AP(KT)6-3-自动状态",{"$nulls":16},"NJ-2AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-3","02F03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU02F03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B10*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU02F03_A AT%I1.2 :BOOL; (*空调机组NJ-2AP(KT)6-3-自动状态*)"},"LAHU02F03_A             AT%I1.2        :BOOL; (*空调机组NJ-2AP(KT)6-3-自动状态*)",null,"L16\\L16AHU02F03_A","空调机组NJ-2AP(KT)6-3-自动状态",10010]
[{"$nulls":5},12,null,23,24,"空调机组NJ-2AP(KT)6-3-风机压差",{"$nulls":16},"NJ-2AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-3","02F03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU02F03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B10*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU02F03_FPS AT%I1.3 :BOOL; (*空调机组NJ-2AP(KT)6-3-风机压差*)"},"LAHU02F03_FPS           AT%I1.3        :BOOL; (*空调机组NJ-2AP(KT)6-3-风机压差*)",null,"L16\\L16AHU02F03_FPS","空调机组NJ-2AP(KT)6-3-风机压差",10011]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-2AL6-1-运行状态",{"$nulls":16},"NJ-2AL6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-1","02F01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"LCB02F01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B10*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LLCB02F01_R AT%I1.4 :BOOL; (*照明控制箱NJ-2AL6-1-运行状态*)"},"LLCB02F01_R             AT%I1.4        :BOOL; (*照明控制箱NJ-2AL6-1-运行状态*)",null,"L16\\L16LCB02F01_R","照明控制箱NJ-2AL6-1-运行状态",10012]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-2AL6-1-自动状态",{"$nulls":16},"NJ-2AL6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-1","02F01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"LCB02F01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B10*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LLCB02F01_A AT%I1.5 :BOOL; (*照明控制箱NJ-2AL6-1-自动状态*)"},"LLCB02F01_A             AT%I1.5        :BOOL; (*照明控制箱NJ-2AL6-1-自动状态*)",null,"L16\\L16LCB02F01_A","照明控制箱NJ-2AL6-1-自动状态",10013]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-2AL6-2-运行状态",{"$nulls":16},"NJ-2AL6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-2","02F02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"LCB02F02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B10*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LLCB02F02_R AT%I1.6 :BOOL; (*照明控制箱NJ-2AL6-2-运行状态*)"},"LLCB02F02_R             AT%I1.6        :BOOL; (*照明控制箱NJ-2AL6-2-运行状态*)",null,"L16\\L16LCB02F02_R","照明控制箱NJ-2AL6-2-运行状态",10014]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-2AL6-2-自动状态",{"$nulls":16},"NJ-2AL6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-2","02F02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH24,List!$B$3:$D$445,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,List!$K$2:$M$447,2,FALSE)","v":"LCB02F02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%I\"&B10*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":"LLCB02F02_A AT%I1.7 :BOOL; (*照明控制箱NJ-2AL6-2-自动状态*)"},"LLCB02F02_A             AT%I1.7        :BOOL; (*照明控制箱NJ-2AL6-2-自动状态*)",null,"L16\\L16LCB02F02_A","照明控制箱NJ-2AL6-2-自动状态",10015]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 1601R地址: 1 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH26&AA26&\"-\"&AK26","v":"照明控制箱NJ-2AL6-3-运行状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-2AL6-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-3","02F03","运行状态",{"$f":"AH26&\"-\"&AK26","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"LCB02F03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LLCB02F03_R AT%I16.0 :BOOL; (*照明控制箱NJ-2AL6-3-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LLCB02F03_R             AT%I16.0       :BOOL; (*照明控制箱NJ-2AL6-3-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L16\\L16LCB02F03_R"},{"$f":"J26","v":"照明控制箱NJ-2AL6-3-运行状态"},{"$f":"10000+($B27*16*8+F26-1)","v":10128}]
[null,1,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,3,4,"照明控制箱NJ-2AL6-3-自动状态",{"$nulls":16},{"$f":"IF(AI27=\"\",\"\",AI27)","v":"NJ-2AL6-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-3","02F03","自动状态",{"$f":"AH27&\"-\"&AK27","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"LCB02F03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LLCB02F03_A AT%I16.1 :BOOL; (*照明控制箱NJ-2AL6-3-自动状态*)"},"LLCB02F03_A             AT%I16.1       :BOOL; (*照明控制箱NJ-2AL6-3-自动状态*)",null,"L16\\L16LCB02F03_A",{"$f":"J27","v":"照明控制箱NJ-2AL6-3-自动状态"},{"$f":"AS26+1","v":10129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,5,6,"照明控制箱NJ-2AL6-4-运行状态",{"$nulls":16},"NJ-2AL6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-4","02F04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"LCB02F04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LLCB02F04_R AT%I16.2 :BOOL; (*照明控制箱NJ-2AL6-4-运行状态*)"},"LLCB02F04_R             AT%I16.2       :BOOL; (*照明控制箱NJ-2AL6-4-运行状态*)",null,"L16\\L16LCB02F04_R","照明控制箱NJ-2AL6-4-运行状态",{"$f":"AS27+1","v":10130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,7,8,"照明控制箱NJ-2AL6-4-自动状态",{"$nulls":16},"NJ-2AL6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-4","02F04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"LCB02F04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LLCB02F04_A AT%I16.3 :BOOL; (*照明控制箱NJ-2AL6-4-自动状态*)"},"LLCB02F04_A             AT%I16.3       :BOOL; (*照明控制箱NJ-2AL6-4-自动状态*)",null,"L16\\L16LCB02F04_A","照明控制箱NJ-2AL6-4-自动状态",10131]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-2AL6-5-运行状态",{"$nulls":16},"NJ-2AL6-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-5","02F05","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"LCB02F05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B27*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LLCB02F05_R AT%I16.4 :BOOL; (*照明控制箱NJ-2AL6-5-运行状态*)"},"LLCB02F05_R             AT%I16.4       :BOOL; (*照明控制箱NJ-2AL6-5-运行状态*)",null,"L16\\L16LCB02F05_R","照明控制箱NJ-2AL6-5-运行状态",10132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-2AL6-5-自动状态",{"$nulls":16},"NJ-2AL6-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-5","02F05","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"LCB02F05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B27*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LLCB02F05_A AT%I16.5 :BOOL; (*照明控制箱NJ-2AL6-5-自动状态*)"},"LLCB02F05_A             AT%I16.5       :BOOL; (*照明控制箱NJ-2AL6-5-自动状态*)",null,"L16\\L16LCB02F05_A","照明控制箱NJ-2AL6-5-自动状态",10133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"照明控制箱NJ-2AL6-6-运行状态",{"$nulls":16},"NJ-2AL6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-6","02F06","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"LCB02F06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B27*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LLCB02F06_R AT%I16.6 :BOOL; (*照明控制箱NJ-2AL6-6-运行状态*)"},"LLCB02F06_R             AT%I16.6       :BOOL; (*照明控制箱NJ-2AL6-6-运行状态*)",null,"L16\\L16LCB02F06_R","照明控制箱NJ-2AL6-6-运行状态",10134]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"照明控制箱NJ-2AL6-6-自动状态",{"$nulls":16},"NJ-2AL6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-6","02F06","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"LCB02F06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B27*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LLCB02F06_A AT%I16.7 :BOOL; (*照明控制箱NJ-2AL6-6-自动状态*)"},"LLCB02F06_A             AT%I16.7       :BOOL; (*照明控制箱NJ-2AL6-6-自动状态*)",null,"L16\\L16LCB02F06_A","照明控制箱NJ-2AL6-6-自动状态",10135]
[{"$nulls":5},9,null,17,18,"风机盘管NJ-2AP(KT)6-1-运行状态",{"$nulls":16},"NJ-2AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-2AP(KT)6-1","02F01","运行状态","风机盘管-运行状态",{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"FCU02F01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B27*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LFCU02F01_R AT%I17.0 :BOOL; (*风机盘管NJ-2AP(KT)6-1-运行状态*)"},"LFCU02F01_R             AT%I17.0       :BOOL; (*风机盘管NJ-2AP(KT)6-1-运行状态*)",null,"L16\\L16FCU02F01_R","风机盘管NJ-2AP(KT)6-1-运行状态",10136]
[{"$nulls":5},10,null,19,20,"风机盘管NJ-2AP(KT)6-1-自动状态",{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-2AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-2AP(KT)6-1","02F01","自动状态",{"$f":"AH35&\"-\"&AK35","v":"风机盘管-自动状态"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"FCU02F01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B27*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LFCU02F01_A AT%I17.1 :BOOL; (*风机盘管NJ-2AP(KT)6-1-自动状态*)"},"LFCU02F01_A             AT%I17.1       :BOOL; (*风机盘管NJ-2AP(KT)6-1-自动状态*)",null,"L16\\L16FCU02F01_A",{"$f":"J35","v":"风机盘管NJ-2AP(KT)6-1-自动状态"},10137]
[{"$nulls":5},11,null,21,22,"风机盘管NJ-2AP(KT)6-1-电磁阀开启状态",{"$nulls":16},"NJ-2AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-2AP(KT)6-1","02F01","电磁阀开启状态","风机盘管-电磁阀开启状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"FCU02F01_EVR"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B27*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LFCU02F01_EVR AT%I17.2 :BOOL; (*风机盘管NJ-2AP(KT)6-1-电磁阀开启状态*)"},"LFCU02F01_EVR           AT%I17.2       :BOOL; (*风机盘管NJ-2AP(KT)6-1-电磁阀开启状态*)",null,"L16\\L16FCU02F01_EVR","风机盘管NJ-2AP(KT)6-1-电磁阀开启状态",10138]
[{"$nulls":5},12,null,23,24,"风机盘管NJ-2AP(KT)6-1-电磁阀自动状态",{"$nulls":16},"NJ-2AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-2AP(KT)6-1","02F01","电磁阀自动状态","风机盘管-电磁阀自动状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"FCU02F01_EVA"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B27*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LFCU02F01_EVA AT%I17.3 :BOOL; (*风机盘管NJ-2AP(KT)6-1-电磁阀自动状态*)"},"LFCU02F01_EVA           AT%I17.3       :BOOL; (*风机盘管NJ-2AP(KT)6-1-电磁阀自动状态*)",null,"L16\\L16FCU02F01_EVA","风机盘管NJ-2AP(KT)6-1-电磁阀自动状态",10139]
[{"$nulls":5},13,null,25,26,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B27*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN38,SEARCH(\"AT%\",AN38),,REPT(\" \",30-SEARCH(\"AT%\",AN38))),SEARCH(\":\",REPLACE(AN38,SEARCH(\"AT%\",AN38),,REPT(\" \",30-SEARCH(\"AT%\",AN38)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN38,SEARCH(\"AT%\",AN38),,REPT(\" \",25-SEARCH(\"AT%\",AN38)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",10140]
[{"$nulls":5},14,null,27,28,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B27*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10141]
[{"$nulls":5},15,null,29,30,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B27*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10142]
[".",{"$nulls":4},16,null,31,32,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%I\"&B27*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10143]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 1601D地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH43&AA43&\"-\"&AK43","v":"空调机组NJ-2AP(KT)6-1-启停控制"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-2AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-1","02F01","启停控制",{"$f":"AH43&\"-\"&AK43","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"AHU02F01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%Q\"&B44*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LAHU02F01_C AT%Q32.0 :BOOL; (*空调机组NJ-2AP(KT)6-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LAHU02F01_C             AT%Q32.0       :BOOL; (*空调机组NJ-2AP(KT)6-1-启停控制*)"},null,{"$f":"AM43","v":"AHU02F01_C"},{"$f":"J43","v":"空调机组NJ-2AP(KT)6-1-启停控制"},{"$f":"($B44*16*8+F43-1)","v":256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-2AP(KT)6-2-启停控制",{"$nulls":16},{"$f":"IF(AI44=\"\",\"\",AI44)","v":"NJ-2AP(KT)6-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-2","02F02","启停控制",{"$f":"AH44&\"-\"&AK44","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"AHU02F02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%Q\"&B44*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LAHU02F02_C AT%Q32.1 :BOOL; (*空调机组NJ-2AP(KT)6-2-启停控制*)"},"LAHU02F02_C             AT%Q32.1       :BOOL; (*空调机组NJ-2AP(KT)6-2-启停控制*)",null,"AHU02F02_C",{"$f":"J44","v":"空调机组NJ-2AP(KT)6-2-启停控制"},{"$f":"AS43+1","v":257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","空调机组NJ-2AP(KT)6-3-启停控制",{"$nulls":16},"NJ-2AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-3","02F03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"AHU02F03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%Q\"&B44*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LAHU02F03_C AT%Q32.2 :BOOL; (*空调机组NJ-2AP(KT)6-3-启停控制*)"},"LAHU02F03_C             AT%Q32.2       :BOOL; (*空调机组NJ-2AP(KT)6-3-启停控制*)",null,"AHU02F03_C","空调机组NJ-2AP(KT)6-3-启停控制",{"$f":"AS44+1","v":258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","照明控制箱NJ-2AL6-1-启停控制",{"$nulls":16},"NJ-2AL6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-1","02F01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"LCB02F01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%Q\"&B44*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LLCB02F01_C AT%Q32.3 :BOOL; (*照明控制箱NJ-2AL6-1-启停控制*)"},"LLCB02F01_C             AT%Q32.3       :BOOL; (*照明控制箱NJ-2AL6-1-启停控制*)",null,"LCB02F01_C","照明控制箱NJ-2AL6-1-启停控制",259]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","照明控制箱NJ-2AL6-2-启停控制",{"$nulls":16},"NJ-2AL6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-2","02F02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"LCB02F02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%Q\"&B44*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LLCB02F02_C AT%Q32.4 :BOOL; (*照明控制箱NJ-2AL6-2-启停控制*)"},"LLCB02F02_C             AT%Q32.4       :BOOL; (*照明控制箱NJ-2AL6-2-启停控制*)",null,"LCB02F02_C","照明控制箱NJ-2AL6-2-启停控制",260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","照明控制箱NJ-2AL6-3-启停控制",{"$nulls":16},"NJ-2AL6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-3","02F03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"LCB02F03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%Q\"&B44*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LLCB02F03_C AT%Q32.5 :BOOL; (*照明控制箱NJ-2AL6-3-启停控制*)"},"LLCB02F03_C             AT%Q32.5       :BOOL; (*照明控制箱NJ-2AL6-3-启停控制*)",null,"LCB02F03_C","照明控制箱NJ-2AL6-3-启停控制",261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","照明控制箱NJ-2AL6-4-启停控制",{"$nulls":16},"NJ-2AL6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-4","02F04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"LCB02F04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%Q\"&B44*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LLCB02F04_C AT%Q32.6 :BOOL; (*照明控制箱NJ-2AL6-4-启停控制*)"},"LLCB02F04_C             AT%Q32.6       :BOOL; (*照明控制箱NJ-2AL6-4-启停控制*)",null,"LCB02F04_C","照明控制箱NJ-2AL6-4-启停控制",262]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-2AL6-5-启停控制",{"$nulls":16},"NJ-2AL6-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-5","02F05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"LCB02F05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%Q\"&B44*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LLCB02F05_C AT%Q32.7 :BOOL; (*照明控制箱NJ-2AL6-5-启停控制*)"},"LLCB02F05_C             AT%Q32.7       :BOOL; (*照明控制箱NJ-2AL6-5-启停控制*)",null,"LCB02F05_C","照明控制箱NJ-2AL6-5-启停控制",263]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-2AL6-6-启停控制",{"$nulls":16},"NJ-2AL6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-2AL6-6","02F06","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"LCB02F06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%Q\"&B44*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LLCB02F06_C AT%Q33.0 :BOOL; (*照明控制箱NJ-2AL6-6-启停控制*)"},"LLCB02F06_C             AT%Q33.0       :BOOL; (*照明控制箱NJ-2AL6-6-启停控制*)",null,"LCB02F06_C","照明控制箱NJ-2AL6-6-启停控制",264]
[{"$nulls":5},10,null,"10+","10-","风机盘管NJ-2AP(KT)6-1-启停控制",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-2AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-2AP(KT)6-1","02F01","启停控制",{"$f":"AH52&\"-\"&AK52","v":"风机盘管-启停控制"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"FCU02F01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%Q\"&B44*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LFCU02F01_C AT%Q33.1 :BOOL; (*风机盘管NJ-2AP(KT)6-1-启停控制*)"},"LFCU02F01_C             AT%Q33.1       :BOOL; (*风机盘管NJ-2AP(KT)6-1-启停控制*)",null,"FCU02F01_C",{"$f":"J52","v":"风机盘管NJ-2AP(KT)6-1-启停控制"},265]
[{"$nulls":5},11,null,"11+","11-","风机盘管NJ-2AP(KT)6-1-电磁阀开关控制",{"$nulls":16},"NJ-2AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-2AP(KT)6-1","02F01","电磁阀开关控制","风机盘管-电磁阀开关控制",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"FCU02F01_EVC"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%Q\"&B44*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LFCU02F01_EVC AT%Q33.2 :BOOL; (*风机盘管NJ-2AP(KT)6-1-电磁阀开关控制*)"},"LFCU02F01_EVC           AT%Q33.2       :BOOL; (*风机盘管NJ-2AP(KT)6-1-电磁阀开关控制*)",null,"FCU02F01_EVC","风机盘管NJ-2AP(KT)6-1-电磁阀开关控制",266]
[{"$nulls":5},12,null,"12+","12-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%Q\"&B44*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",267]
[{"$nulls":5},13,null,"13+","13-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%Q\"&B44*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",268]
[{"$nulls":5},14,null,"14+","14-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%Q\"&B44*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",269]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%Q\"&B44*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",270]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%Q\"&B44*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",271]
[null,{"$f":"B64","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B64&\"地址: \"&B61&\" *)\"","v":"(* IOM 0801U地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH60&AA60&\"-\"&AK60","v":"空调机组NJ-2AP(KT)6-1-回风温度"},{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-2AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-1","02F01","回风温度",{"$f":"AH60&\"-\"&AK60","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"AHU02F01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%I\"&B61*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LAHU02F01_RT AT%I48.0 :INT ; (*空调机组NJ-2AP(KT)6-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60))),SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))))),\" \")","v":"LAHU02F01_RT            AT%I48.0       :INT ; (*空调机组NJ-2AP(KT)6-1-回风温度*)"},null,{"$f":"AM60","v":"AHU02F01_RT"},{"$f":"J60","v":"空调机组NJ-2AP(KT)6-1-回风温度"},{"$f":"30000+($B61*8+F60-1)","v":30024}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-2AP(KT)6-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI61=\"\",\"\",AI61)","v":"NJ-2AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-1","02F01","水阀反馈",{"$f":"AH61&\"-\"&AK61","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"AHU02F01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%I\"&B61*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LAHU02F01_WVB AT%I50.0 :INT ; (*空调机组NJ-2AP(KT)6-1-水阀反馈*)"},"LAHU02F01_WVB           AT%I50.0       :INT ; (*空调机组NJ-2AP(KT)6-1-水阀反馈*)",null,"AHU02F01_WVB",{"$f":"J61","v":"空调机组NJ-2AP(KT)6-1-水阀反馈"},{"$f":"AS60+1","v":30025}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-2AP(KT)6-2-回风温度",{"$nulls":16},"NJ-2AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-2","02F02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"AHU02F02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B61*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LAHU02F02_RT AT%I52.0 :INT ; (*空调机组NJ-2AP(KT)6-2-回风温度*)"},"LAHU02F02_RT            AT%I52.0       :INT ; (*空调机组NJ-2AP(KT)6-2-回风温度*)",null,"AHU02F02_RT","空调机组NJ-2AP(KT)6-2-回风温度",{"$f":"AS61+1","v":30026}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-2AP(KT)6-2-水阀反馈",{"$nulls":16},"NJ-2AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-2","02F02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"AHU02F02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B61*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LAHU02F02_WVB AT%I54.0 :INT ; (*空调机组NJ-2AP(KT)6-2-水阀反馈*)"},"LAHU02F02_WVB           AT%I54.0       :INT ; (*空调机组NJ-2AP(KT)6-2-水阀反馈*)",null,"AHU02F02_WVB","空调机组NJ-2AP(KT)6-2-水阀反馈",30027]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-2AP(KT)6-3-回风温度",{"$nulls":16},"NJ-2AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-3","02F03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"AHU02F03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B61*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LAHU02F03_RT AT%I56.0 :INT ; (*空调机组NJ-2AP(KT)6-3-回风温度*)"},"LAHU02F03_RT            AT%I56.0       :INT ; (*空调机组NJ-2AP(KT)6-3-回风温度*)",null,"AHU02F03_RT","空调机组NJ-2AP(KT)6-3-回风温度",30028]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-2AP(KT)6-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI65=\"\",\"\",AI65)","v":"NJ-2AP(KT)6-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-3","02F03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":"AHU02F03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B61*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":"LAHU02F03_WVB AT%I58.0 :INT ; (*空调机组NJ-2AP(KT)6-3-水阀反馈*)"},"LAHU02F03_WVB           AT%I58.0       :INT ; (*空调机组NJ-2AP(KT)6-3-水阀反馈*)",null,"AHU02F03_WVB",{"$f":"J65","v":"空调机组NJ-2AP(KT)6-3-水阀反馈"},30029]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","风机盘管NJ-2AP(KT)6-1-温度状态",{"$nulls":16},"NJ-2AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-2AP(KT)6-1","02F01","温度状态","风机盘管-温度状态",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":"FCU02F01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B61*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":"LFCU02F01_T AT%I60.0 :INT ; (*风机盘管NJ-2AP(KT)6-1-温度状态*)"},"LFCU02F01_T             AT%I60.0       :INT ; (*风机盘管NJ-2AP(KT)6-1-温度状态*)",null,"FCU02F01_T","风机盘管NJ-2AP(KT)6-1-温度状态",30030]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%I\"&B61*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30031]
[null,{"$f":"B73","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B73&\"地址: \"&B70&\" *)\"","v":"(* IOM 0401A地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH69&AA69&\"-\"&AK69","v":"空调机组NJ-2AP(KT)6-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-2AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-1","02F01","水阀控制",{"$f":"AH69&\"-\"&AK69","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU02F01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%Q\"&B70*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU02F01_WVC AT%Q64.0 :INT ; (*空调机组NJ-2AP(KT)6-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69))),SEARCH(\":\",REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69)))))),\" \")","v":"LAHU02F01_WVC           AT%Q64.0       :INT ; (*空调机组NJ-2AP(KT)6-1-水阀控制*)"},null,{"$f":"AM69","v":"AHU02F01_WVC"},{"$f":"J69","v":"空调机组NJ-2AP(KT)6-1-水阀控制"},{"$f":"40000+($B70*8+F69-1)","v":40032}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH70&AA70&\"-\"&AK70","v":"空调机组NJ-2AP(KT)6-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI70=\"\",\"\",AI70)","v":"NJ-2AP(KT)6-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-2","02F02","水阀控制",{"$f":"AH70&\"-\"&AK70","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"AHU02F02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%Q\"&B70*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LAHU02F02_WVC AT%Q66.0 :INT ; (*空调机组NJ-2AP(KT)6-2-水阀控制*)"},"LAHU02F02_WVC           AT%Q66.0       :INT ; (*空调机组NJ-2AP(KT)6-2-水阀控制*)",null,"AHU02F02_WVC",{"$f":"J70","v":"空调机组NJ-2AP(KT)6-2-水阀控制"},{"$f":"AS69+1","v":40033}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH71&AA71&\"-\"&AK71","v":"空调机组NJ-2AP(KT)6-3-水阀控制"},{"$nulls":16},"NJ-2AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)6-3","02F03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"AHU02F03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%Q\"&B70*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LAHU02F03_WVC AT%Q68.0 :INT ; (*空调机组NJ-2AP(KT)6-3-水阀控制*)"},"LAHU02F03_WVC           AT%Q68.0       :INT ; (*空调机组NJ-2AP(KT)6-3-水阀控制*)",null,"AHU02F03_WVC","空调机组NJ-2AP(KT)6-3-水阀控制",{"$f":"AS70+1","v":40034}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH72&AA72&\"-\"&AK72","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%Q\"&B70*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40035]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L106","index":16,"n_rows":59,"n_cols":45,"rows_kept":59,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[58,5,58,6],[58,9,58,25],[4,1,5,1],[11,1,22,1],[28,1,31,1],[37,1,40,1],[46,1,49,1],[55,1,58,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L16",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH8&AA8&\"-\"&AK8","v":"空调机组NJ-1AP(KT)6-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-1AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-1","01F01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH8,List!$B$3:$D$445,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,List!$K$2:$M$447,2,FALSE)","v":"AHU01F01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LAHU01F01_R AT%I80.0 :BOOL; (*空调机组NJ-1AP(KT)6-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",30-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",30-SEARCH(\"AT%\",AN8)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LAHU01F01_R                  AT%I80.0  :BOOL; (*空调机组NJ-1AP(KT)6-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L16\\L16AHU01F01_R"},{"$f":"J8","v":"空调机组NJ-1AP(KT)6-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":10640}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-1AP(KT)6-1-故障状态",{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-1AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-1","01F01","故障状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU01F01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU01F01_F AT%I80.1 :BOOL; (*空调机组NJ-1AP(KT)6-1-故障状态*)"},"LAHU01F01_F                  AT%I80.1  :BOOL; (*空调机组NJ-1AP(KT)6-1-故障状态*)",null,"L16\\L16AHU01F01_F",{"$f":"J9","v":"空调机组NJ-1AP(KT)6-1-故障状态"},{"$f":"AS8+1","v":10641}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},3,null,5,6,"空调机组NJ-1AP(KT)6-1-自动状态",{"$nulls":16},"NJ-1AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-1","01F01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU01F01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU01F01_A AT%I80.2 :BOOL; (*空调机组NJ-1AP(KT)6-1-自动状态*)"},"LAHU01F01_A                  AT%I80.2  :BOOL; (*空调机组NJ-1AP(KT)6-1-自动状态*)",null,"L16\\L16AHU01F01_A","空调机组NJ-1AP(KT)6-1-自动状态",{"$f":"AS9+1","v":10642}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-1AP(KT)6-1-风机压差",{"$nulls":16},"NJ-1AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-1","01F01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU01F01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU01F01_FPS AT%I80.3 :BOOL; (*空调机组NJ-1AP(KT)6-1-风机压差*)"},"LAHU01F01_FPS                AT%I80.3  :BOOL; (*空调机组NJ-1AP(KT)6-1-风机压差*)",null,"L16\\L16AHU01F01_FPS","空调机组NJ-1AP(KT)6-1-风机压差",10643]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-1AP(KT)6-1-运行状态",{"$nulls":16},"NJ-1AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-1","01F02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU01F02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU01F02_R AT%I80.4 :BOOL; (*空调机组NJ-1AP(KT)6-1-运行状态*)"},"LAHU01F02_R                  AT%I80.4  :BOOL; (*空调机组NJ-1AP(KT)6-1-运行状态*)",null,"L16\\L16AHU01F02_R","空调机组NJ-1AP(KT)6-1-运行状态",10644]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-1AP(KT)6-2-故障状态",{"$nulls":16},"NJ-1AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-2","01F02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU01F02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU01F02_F AT%I80.5 :BOOL; (*空调机组NJ-1AP(KT)6-2-故障状态*)"},"LAHU01F02_F                  AT%I80.5  :BOOL; (*空调机组NJ-1AP(KT)6-2-故障状态*)",null,"L16\\L16AHU01F02_F","空调机组NJ-1AP(KT)6-2-故障状态",10645]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-1AP(KT)6-2-自动状态",{"$nulls":16},"NJ-1AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-2","01F02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU01F02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU01F02_A AT%I80.6 :BOOL; (*空调机组NJ-1AP(KT)6-2-自动状态*)"},"LAHU01F02_A                  AT%I80.6  :BOOL; (*空调机组NJ-1AP(KT)6-2-自动状态*)",null,"L16\\L16AHU01F02_A","空调机组NJ-1AP(KT)6-2-自动状态",10646]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-1AP(KT)6-2-风机压差",{"$nulls":16},"NJ-1AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-2","01F02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU01F02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU01F02_FPS AT%I80.7 :BOOL; (*空调机组NJ-1AP(KT)6-2-风机压差*)"},"LAHU01F02_FPS                AT%I80.7  :BOOL; (*空调机组NJ-1AP(KT)6-2-风机压差*)",null,"L16\\L16AHU01F02_FPS","空调机组NJ-1AP(KT)6-2-风机压差",10647]
[{"$nulls":5},9,null,17,18,"空调机组NJ-1AP(KT)6-2-运行状态",{"$nulls":16},"NJ-1AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-2","01F03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU01F03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU01F03_R AT%I81.0 :BOOL; (*空调机组NJ-1AP(KT)6-2-运行状态*)"},"LAHU01F03_R                  AT%I81.0  :BOOL; (*空调机组NJ-1AP(KT)6-2-运行状态*)",null,"L16\\L16AHU01F03_R","空调机组NJ-1AP(KT)6-2-运行状态",10648]
[{"$nulls":5},10,null,19,20,"空调机组NJ-1AP(KT)6-3-故障状态",{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-1AP(KT)6-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-3","01F03","故障状态",{"$f":"AH17&\"-\"&AK17","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU01F03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU01F03_F AT%I81.1 :BOOL; (*空调机组NJ-1AP(KT)6-3-故障状态*)"},"LAHU01F03_F                  AT%I81.1  :BOOL; (*空调机组NJ-1AP(KT)6-3-故障状态*)",null,"L16\\L16AHU01F03_F","空调机组NJ-1AP(KT)6-3-故障状态",10649]
[{"$nulls":5},11,null,21,22,"空调机组NJ-1AP(KT)6-3-自动状态",{"$nulls":16},"NJ-1AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-3","01F03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU01F03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU01F03_A AT%I81.2 :BOOL; (*空调机组NJ-1AP(KT)6-3-自动状态*)"},"LAHU01F03_A                  AT%I81.2  :BOOL; (*空调机组NJ-1AP(KT)6-3-自动状态*)",null,"L16\\L16AHU01F03_A","空调机组NJ-1AP(KT)6-3-自动状态",10650]
[{"$nulls":5},12,null,23,24,"空调机组NJ-1AP(KT)6-3-风机压差",{"$nulls":16},"NJ-1AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-3","01F03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU01F03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU01F03_FPS AT%I81.3 :BOOL; (*空调机组NJ-1AP(KT)6-3-风机压差*)"},"LAHU01F03_FPS                AT%I81.3  :BOOL; (*空调机组NJ-1AP(KT)6-3-风机压差*)",null,"L16\\L16AHU01F03_FPS","空调机组NJ-1AP(KT)6-3-风机压差",10651]
[{"$nulls":5},13,null,25,26,"空调机组NJ-1AP(KT)6-4-运行状态",{"$nulls":16},"NJ-1AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-4","01F04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU01F04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU01F04_R AT%I81.4 :BOOL; (*空调机组NJ-1AP(KT)6-4-运行状态*)"},"LAHU01F04_R                  AT%I81.4  :BOOL; (*空调机组NJ-1AP(KT)6-4-运行状态*)",null,"L16\\L16AHU01F04_R","空调机组NJ-1AP(KT)6-4-运行状态",10652]
[{"$nulls":5},14,null,27,28,"空调机组NJ-1AP(KT)6-4-故障状态",{"$nulls":16},"NJ-1AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-4","01F04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU01F04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU01F04_F AT%I81.5 :BOOL; (*空调机组NJ-1AP(KT)6-4-故障状态*)"},"LAHU01F04_F                  AT%I81.5  :BOOL; (*空调机组NJ-1AP(KT)6-4-故障状态*)",null,"L16\\L16AHU01F04_F","空调机组NJ-1AP(KT)6-4-故障状态",10653]
[{"$nulls":5},15,null,29,30,"空调机组NJ-1AP(KT)6-4-自动状态",{"$nulls":16},"NJ-1AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-4","01F04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU01F04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU01F04_A AT%I81.6 :BOOL; (*空调机组NJ-1AP(KT)6-4-自动状态*)"},"LAHU01F04_A                  AT%I81.6  :BOOL; (*空调机组NJ-1AP(KT)6-4-自动状态*)",null,"L16\\L16AHU01F04_A","空调机组NJ-1AP(KT)6-4-自动状态",10654]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-1AP(KT)6-4-风机压差",{"$nulls":16},"NJ-1AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-4","01F04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU01F04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU01F04_FPS AT%I81.7 :BOOL; (*空调机组NJ-1AP(KT)6-4-风机压差*)"},"LAHU01F04_FPS                AT%I81.7  :BOOL; (*空调机组NJ-1AP(KT)6-4-风机压差*)",null,"L16\\L16AHU01F04_FPS","空调机组NJ-1AP(KT)6-4-风机压差",10655]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 0801R 地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH25&AA25&\"-\"&AK25","v":"照明控制箱NJ-1AL6-1-运行状态"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-1AL6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL6-1","01F01","运行状态",{"$f":"AH25&\"-\"&AK25","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"LCB01F01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LLCB01F01_R AT%I96.0 :BOOL; (*照明控制箱NJ-1AL6-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LLCB01F01_R             AT%I96.0       :BOOL; (*照明控制箱NJ-1AL6-1-运行状态*)"},null,{"$f":"AM25","v":"LCB01F01_R"},{"$f":"J25","v":"照明控制箱NJ-1AL6-1-运行状态"},{"$f":"10000+($B26*16*8+F25-1)","v":10768}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},2,null,2,"C",{"$f":"AH26&AA26&\"-\"&AK26","v":"照明控制箱NJ-1AL6-1-自动状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-1AL6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL6-1","01F01","自动状态",{"$f":"AH26&\"-\"&AK26","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"LCB01F01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LLCB01F01_A AT%I96.1 :BOOL; (*照明控制箱NJ-1AL6-1-自动状态*)"},"LLCB01F01_A             AT%I96.1       :BOOL; (*照明控制箱NJ-1AL6-1-自动状态*)",null,{"$f":"AM26","v":"LCB01F01_A"},{"$f":"J26","v":"照明控制箱NJ-1AL6-1-自动状态"},{"$f":"AS25+1","v":10769}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},3,null,3,"C",{"$f":"AH27&AA27&\"-\"&AK27","v":"-运行状态"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":6}," ","运行状态","-运行状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-运行状态",{"$f":"AS26+1","v":10770}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":0},4,null,4,"C",{"$f":"AH28&AA28&\"-\"&AK28","v":"-自动状态"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":7},"自动状态","-自动状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-自动状态",10771]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,5,"C","-运行状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":7},"运行状态","-运行状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-运行状态",10772]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","-自动状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":7},"自动状态","-自动状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-自动状态",10773]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","-运行状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":7},"运行状态","-运行状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-运行状态",10774]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","-自动状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":7},"自动状态","-自动状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-自动状态",10775]
[null,"IOM 0801D",{"$nulls":38},{"$f":"\"(* \"&B38&\"地址: \"&B35&\" *)\"","v":"(* IOM 0801D地址: 7 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH34&AA34&\"-\"&AK34","v":"空调机组NJ-1AP(KT)6-1-启停控制"},{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-1AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-1","01F01","启停控制",{"$f":"AH34&\"-\"&AK34","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU01F01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%Q\"&B35*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU01F01_C AT%Q112.0 :BOOL; (*空调机组NJ-1AP(KT)6-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34))),SEARCH(\":\",REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34)))))),\" \")","v":"LAHU01F01_C             AT%Q112.0      :BOOL; (*空调机组NJ-1AP(KT)6-1-启停控制*)"},null,{"$f":"AM34","v":"AHU01F01_C"},{"$f":"J34","v":"空调机组NJ-1AP(KT)6-1-启停控制"},{"$f":"($B35*16*8+F34-1)","v":896}]
[null,7,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-1AP(KT)6-2-启停控制",{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-1AP(KT)6-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-2","01F02","启停控制",{"$f":"AH35&\"-\"&AK35","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU01F02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%Q\"&B35*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU01F02_C AT%Q112.1 :BOOL; (*空调机组NJ-1AP(KT)6-2-启停控制*)"},"LAHU01F02_C             AT%Q112.1      :BOOL; (*空调机组NJ-1AP(KT)6-2-启停控制*)",null,"AHU01F02_C",{"$f":"J35","v":"空调机组NJ-1AP(KT)6-2-启停控制"},{"$f":"AS34+1","v":897}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-1AP(KT)6-3-启停控制",{"$nulls":16},"NJ-1AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-3","01F03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU01F03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%Q\"&B35*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU01F03_C AT%Q112.2 :BOOL; (*空调机组NJ-1AP(KT)6-3-启停控制*)"},"LAHU01F03_C             AT%Q112.2      :BOOL; (*空调机组NJ-1AP(KT)6-3-启停控制*)",null,"AHU01F03_C","空调机组NJ-1AP(KT)6-3-启停控制",{"$f":"AS35+1","v":898}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","空调机组NJ-1AP(KT)6-4-启停控制",{"$nulls":16},"NJ-1AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-4","01F04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"AHU01F04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%Q\"&B35*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LAHU01F04_C AT%Q112.3 :BOOL; (*空调机组NJ-1AP(KT)6-4-启停控制*)"},"LAHU01F04_C             AT%Q112.3      :BOOL; (*空调机组NJ-1AP(KT)6-4-启停控制*)",null,"AHU01F04_C","空调机组NJ-1AP(KT)6-4-启停控制",899]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","照明控制箱NJ-1AL6-1-启停控制",{"$nulls":16},"NJ-1AL6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL6-1","01F01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB01F01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%Q\"&B35*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB01F01_C AT%Q112.4 :BOOL; (*照明控制箱NJ-1AL6-1-启停控制*)"},"LLCB01F01_C             AT%Q112.4      :BOOL; (*照明控制箱NJ-1AL6-1-启停控制*)",null,"LCB01F01_C","照明控制箱NJ-1AL6-1-启停控制",900]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%Q\"&B35*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",901]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%Q\"&B35*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",902]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%Q\"&B35*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",903]
[null,{"$f":"B47","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 0801U地址: 8 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH43&AA43&\"-\"&AK43","v":"空调机组NJ-1AP(KT)6-1-回风温度"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-1AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-1","01F01","回风温度",{"$f":"AH43&\"-\"&AK43","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"AHU01F01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B44*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LAHU01F01_RT AT%I128.0 :INT ; (*空调机组NJ-1AP(KT)6-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LAHU01F01_RT            AT%I128.0      :INT ; (*空调机组NJ-1AP(KT)6-1-回风温度*)"},null,{"$f":"AM43","v":"AHU01F01_RT"},{"$f":"J43","v":"空调机组NJ-1AP(KT)6-1-回风温度"},{"$f":"30000+($B44*8+F43-1)","v":30064}]
[null,8,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-1AP(KT)6-1-水阀反馈",{"$nulls":16},"NJ-1AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-1","01F01","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"AHU01F01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B44*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LAHU01F01_WVB AT%I130.0 :INT ; (*空调机组NJ-1AP(KT)6-1-水阀反馈*)"},"LAHU01F01_WVB           AT%I130.0      :INT ; (*空调机组NJ-1AP(KT)6-1-水阀反馈*)",null,"AHU01F01_WVB","空调机组NJ-1AP(KT)6-1-水阀反馈",{"$f":"AS43+1","v":30065}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-1AP(KT)6-2-回风温度",{"$nulls":16},"NJ-1AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-2","01F02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"AHU01F02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B44*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LAHU01F02_RT AT%I132.0 :INT ; (*空调机组NJ-1AP(KT)6-2-回风温度*)"},"LAHU01F02_RT            AT%I132.0      :INT ; (*空调机组NJ-1AP(KT)6-2-回风温度*)",null,"AHU01F02_RT","空调机组NJ-1AP(KT)6-2-回风温度",30066]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-1AP(KT)6-2-水阀反馈",{"$nulls":16},"NJ-1AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-2","01F02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"AHU01F02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B44*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LAHU01F02_WVB AT%I134.0 :INT ; (*空调机组NJ-1AP(KT)6-2-水阀反馈*)"},"LAHU01F02_WVB           AT%I134.0      :INT ; (*空调机组NJ-1AP(KT)6-2-水阀反馈*)",null,"AHU01F02_WVB","空调机组NJ-1AP(KT)6-2-水阀反馈",30067]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-1AP(KT)6-3-回风温度",{"$nulls":16},"NJ-1AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-3","01F03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"AHU01F03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B44*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LAHU01F03_RT AT%I136.0 :INT ; (*空调机组NJ-1AP(KT)6-3-回风温度*)"},"LAHU01F03_RT            AT%I136.0      :INT ; (*空调机组NJ-1AP(KT)6-3-回风温度*)",null,"AHU01F03_RT","空调机组NJ-1AP(KT)6-3-回风温度",30068]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-1AP(KT)6-3-水阀反馈",{"$nulls":16},"NJ-1AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-3","01F03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"AHU01F03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B44*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LAHU01F03_WVB AT%I138.0 :INT ; (*空调机组NJ-1AP(KT)6-3-水阀反馈*)"},"LAHU01F03_WVB           AT%I138.0      :INT ; (*空调机组NJ-1AP(KT)6-3-水阀反馈*)",null,"AHU01F03_WVB","空调机组NJ-1AP(KT)6-3-水阀反馈",30069]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-1AP(KT)6-4-回风温度",{"$nulls":16},"NJ-1AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-4","01F04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"AHU01F04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B44*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LAHU01F04_RT AT%I140.0 :INT ; (*空调机组NJ-1AP(KT)6-4-回风温度*)"},"LAHU01F04_RT            AT%I140.0      :INT ; (*空调机组NJ-1AP(KT)6-4-回风温度*)",null,"AHU01F04_RT","空调机组NJ-1AP(KT)6-4-回风温度",30070]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-1AP(KT)6-4-水阀反馈",{"$nulls":16},"NJ-1AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-4","01F04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"AHU01F04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B44*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LAHU01F04_WVB AT%I142.0 :INT ; (*空调机组NJ-1AP(KT)6-4-水阀反馈*)"},"LAHU01F04_WVB           AT%I142.0      :INT ; (*空调机组NJ-1AP(KT)6-4-水阀反馈*)",null,"AHU01F04_WVB","空调机组NJ-1AP(KT)6-4-水阀反馈",30071]
[null,{"$f":"B56","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B56&\"地址: \"&B53&\" *)\"","v":"(* IOM 0401A地址: 9 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH52&AA52&\"-\"&AK52","v":"空调机组NJ-1AP(KT)6-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-1AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-1","01F01","水阀控制",{"$f":"AH52&\"-\"&AK52","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"AHU01F01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%Q\"&B53*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LAHU01F01_WVC AT%Q144.0 :INT ; (*空调机组NJ-1AP(KT)6-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN52,SEARCH(\"AT%\",AN52),,REPT(\" \",25-SEARCH(\"AT%\",AN52))),SEARCH(\":\",REPLACE(AN52,SEARCH(\"AT%\",AN52),,REPT(\" \",25-SEARCH(\"AT%\",AN52)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN52,SEARCH(\"AT%\",AN52),,REPT(\" \",25-SEARCH(\"AT%\",AN52)))))),\" \")","v":"LAHU01F01_WVC           AT%Q144.0      :INT ; (*空调机组NJ-1AP(KT)6-1-水阀控制*)"},null,{"$f":"AM52","v":"AHU01F01_WVC"},{"$f":"J52","v":"空调机组NJ-1AP(KT)6-1-水阀控制"},{"$f":"40000+($B53*8+F52-1)","v":40072}]
[null,9,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH53&AA53&\"-\"&AK53","v":"空调机组NJ-1AP(KT)6-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI53=\"\",\"\",AI53)","v":"NJ-1AP(KT)6-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-2","01F02","水阀控制",{"$f":"AH53&\"-\"&AK53","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"AHU01F02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%Q\"&B53*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LAHU01F02_WVC AT%Q146.0 :INT ; (*空调机组NJ-1AP(KT)6-2-水阀控制*)"},"LAHU01F02_WVC           AT%Q146.0      :INT ; (*空调机组NJ-1AP(KT)6-2-水阀控制*)",null,"AHU01F02_WVC",{"$f":"J53","v":"空调机组NJ-1AP(KT)6-2-水阀控制"},{"$f":"AS52+1","v":40073}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH54&AA54&\"-\"&AK54","v":"空调机组NJ-1AP(KT)6-3-水阀控制"},{"$nulls":16},"NJ-1AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-3","01F03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"AHU01F03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%Q\"&B53*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LAHU01F03_WVC AT%Q148.0 :INT ; (*空调机组NJ-1AP(KT)6-3-水阀控制*)"},"LAHU01F03_WVC           AT%Q148.0      :INT ; (*空调机组NJ-1AP(KT)6-3-水阀控制*)",null,"AHU01F03_WVC","空调机组NJ-1AP(KT)6-3-水阀控制",{"$f":"AS53+1","v":40074}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH55&AA55&\"-\"&AK55","v":"空调机组NJ-1AP(KT)6-4-水阀控制"},{"$nulls":16},"NJ-1AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)6-4","01F04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"AHU01F04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%Q\"&B53*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LAHU01F04_WVC AT%Q150.0 :INT ; (*空调机组NJ-1AP(KT)6-4-水阀控制*)"},"LAHU01F04_WVC           AT%Q150.0      :INT ; (*空调机组NJ-1AP(KT)6-4-水阀控制*)",null,"AHU01F04_WVC","空调机组NJ-1AP(KT)6-4-水阀控制",40075]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L207","index":17,"n_rows":103,"n_cols":45,"rows_kept":103,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[6,1,6,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[75,5,75,6],[75,9,75,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[84,5,84,6],[84,9,84,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[92,5,92,6],[92,9,92,25],[93,5,93,6],[93,9,93,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[101,5,101,6],[101,9,101,25],[102,5,102,6],[102,9,102,25],[4,1,5,1],[12,1,23,1],[29,1,40,1],[46,1,49,1],[55,1,66,1],[72,1,75,1],[81,1,84,1],[90,1,93,1],[99,1,102,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[16,2,23,4],[33,2,40,4],[59,2,66,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L17",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"EXC-1000"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B13&\"地址: \"&B10&\" *)\"","v":"(* IOM 1601R地址: 0 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH9&AA9&\"-\"&AK9","v":"空调机组NJ-2AP(KT)7-1-运行状态"},{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-2AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-1","02G01","运行状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU02G01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B10*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU02G01_R AT%I0.0 :BOOL; (*空调机组NJ-2AP(KT)7-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9))),SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))))),\" \")","v":"LAHU02G01_R             AT%I0.0        :BOOL; (*空调机组NJ-2AP(KT)7-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM9","v":"L17\\L17AHU02G01_R"},{"$f":"J9","v":"空调机组NJ-2AP(KT)7-1-运行状态"},{"$f":"10000+($B10*16*8+F9-1)","v":10000}]
[null,0,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-2AP(KT)7-1-故障状态",{"$nulls":16},{"$f":"IF(AI10=\"\",\"\",AI10)","v":"NJ-2AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-1","02G01","故障状态",{"$f":"AH10&\"-\"&AK10","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU02G01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B10*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU02G01_F AT%I0.1 :BOOL; (*空调机组NJ-2AP(KT)7-1-故障状态*)"},"LAHU02G01_F             AT%I0.1        :BOOL; (*空调机组NJ-2AP(KT)7-1-故障状态*)",null,"L17\\L17AHU02G01_F",{"$f":"J10","v":"空调机组NJ-2AP(KT)7-1-故障状态"},{"$f":"AS9+1","v":10001}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-2AP(KT)7-1-自动状态",{"$nulls":16},"NJ-2AP(KT)7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-1","02G01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU02G01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B10*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU02G01_A AT%I0.2 :BOOL; (*空调机组NJ-2AP(KT)7-1-自动状态*)"},"LAHU02G01_A             AT%I0.2        :BOOL; (*空调机组NJ-2AP(KT)7-1-自动状态*)",null,"L17\\L17AHU02G01_A","空调机组NJ-2AP(KT)7-1-自动状态",{"$f":"AS10+1","v":10002}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-2AP(KT)7-1-风机压差",{"$nulls":16},"NJ-2AP(KT)7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-1","02G01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU02G01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B10*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU02G01_FPS AT%I0.3 :BOOL; (*空调机组NJ-2AP(KT)7-1-风机压差*)"},"LAHU02G01_FPS           AT%I0.3        :BOOL; (*空调机组NJ-2AP(KT)7-1-风机压差*)",null,"L17\\L17AHU02G01_FPS","空调机组NJ-2AP(KT)7-1-风机压差",10003]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-2AP(KT)7-2-运行状态",{"$nulls":16},"NJ-2AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-2","02G02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU02G02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B10*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU02G02_R AT%I0.4 :BOOL; (*空调机组NJ-2AP(KT)7-2-运行状态*)"},"LAHU02G02_R             AT%I0.4        :BOOL; (*空调机组NJ-2AP(KT)7-2-运行状态*)",null,"L17\\L17AHU02G02_R","空调机组NJ-2AP(KT)7-2-运行状态",10004]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-2AP(KT)7-2-故障状态",{"$nulls":16},"NJ-2AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-2","02G02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU02G02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B10*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU02G02_F AT%I0.5 :BOOL; (*空调机组NJ-2AP(KT)7-2-故障状态*)"},"LAHU02G02_F             AT%I0.5        :BOOL; (*空调机组NJ-2AP(KT)7-2-故障状态*)",null,"L17\\L17AHU02G02_F","空调机组NJ-2AP(KT)7-2-故障状态",10005]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-2AP(KT)7-2-自动状态",{"$nulls":16},"NJ-2AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-2","02G02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU02G02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B10*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU02G02_A AT%I0.6 :BOOL; (*空调机组NJ-2AP(KT)7-2-自动状态*)"},"LAHU02G02_A             AT%I0.6        :BOOL; (*空调机组NJ-2AP(KT)7-2-自动状态*)",null,"L17\\L17AHU02G02_A","空调机组NJ-2AP(KT)7-2-自动状态",10006]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-2AP(KT)7-2-风机压差",{"$nulls":16},"NJ-2AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-2","02G02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU02G02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B10*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU02G02_FPS AT%I0.7 :BOOL; (*空调机组NJ-2AP(KT)7-2-风机压差*)"},"LAHU02G02_FPS           AT%I0.7        :BOOL; (*空调机组NJ-2AP(KT)7-2-风机压差*)",null,"L17\\L17AHU02G02_FPS","空调机组NJ-2AP(KT)7-2-风机压差",10007]
[{"$nulls":5},9,null,17,18,"空调机组NJ-2AP(KT)7-3-运行状态",{"$nulls":16},"NJ-2AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-3","02G03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU02G03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B10*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU02G03_R AT%I1.0 :BOOL; (*空调机组NJ-2AP(KT)7-3-运行状态*)"},"LAHU02G03_R             AT%I1.0        :BOOL; (*空调机组NJ-2AP(KT)7-3-运行状态*)",null,"L17\\L17AHU02G03_R","空调机组NJ-2AP(KT)7-3-运行状态",10008]
[{"$nulls":5},10,null,19,20,"空调机组NJ-2AP(KT)7-3-故障状态",{"$nulls":16},{"$f":"IF(AI18=\"\",\"\",AI18)","v":"NJ-2AP(KT)7-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-3","02G03","故障状态",{"$f":"AH18&\"-\"&AK18","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU02G03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B10*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU02G03_F AT%I1.1 :BOOL; (*空调机组NJ-2AP(KT)7-3-故障状态*)"},"LAHU02G03_F             AT%I1.1        :BOOL; (*空调机组NJ-2AP(KT)7-3-故障状态*)",null,"L17\\L17AHU02G03_F","空调机组NJ-2AP(KT)7-3-故障状态",10009]
[{"$nulls":5},11,null,21,22,"空调机组NJ-2AP(KT)7-3-自动状态",{"$nulls":16},"NJ-2AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-3","02G03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU02G03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B10*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU02G03_A AT%I1.2 :BOOL; (*空调机组NJ-2AP(KT)7-3-自动状态*)"},"LAHU02G03_A             AT%I1.2        :BOOL; (*空调机组NJ-2AP(KT)7-3-自动状态*)",null,"L17\\L17AHU02G03_A","空调机组NJ-2AP(KT)7-3-自动状态",10010]
[{"$nulls":5},12,null,23,24,"空调机组NJ-2AP(KT)7-3-风机压差",{"$nulls":16},"NJ-2AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-3","02G03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU02G03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B10*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU02G03_FPS AT%I1.3 :BOOL; (*空调机组NJ-2AP(KT)7-3-风机压差*)"},"LAHU02G03_FPS           AT%I1.3        :BOOL; (*空调机组NJ-2AP(KT)7-3-风机压差*)",null,"L17\\L17AHU02G03_FPS","空调机组NJ-2AP(KT)7-3-风机压差",10011]
[{"$nulls":5},13,null,25,26,"空调机组NJ-2AP(KT)7-4-运行状态",{"$nulls":16},"NJ-2AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-4","02G04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU02G04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B10*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU02G04_R AT%I1.4 :BOOL; (*空调机组NJ-2AP(KT)7-4-运行状态*)"},"LAHU02G04_R             AT%I1.4        :BOOL; (*空调机组NJ-2AP(KT)7-4-运行状态*)",null,"L17\\L17AHU02G04_R","空调机组NJ-2AP(KT)7-4-运行状态",10012]
[{"$nulls":5},14,null,27,28,"空调机组NJ-2AP(KT)7-4-故障状态",{"$nulls":16},"NJ-2AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-4","02G04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU02G04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B10*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU02G04_F AT%I1.5 :BOOL; (*空调机组NJ-2AP(KT)7-4-故障状态*)"},"LAHU02G04_F             AT%I1.5        :BOOL; (*空调机组NJ-2AP(KT)7-4-故障状态*)",null,"L17\\L17AHU02G04_F","空调机组NJ-2AP(KT)7-4-故障状态",10013]
[{"$nulls":5},15,null,29,30,"空调机组NJ-2AP(KT)7-4-自动状态",{"$nulls":16},"NJ-2AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-4","02G04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU02G04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B10*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU02G04_A AT%I1.6 :BOOL; (*空调机组NJ-2AP(KT)7-4-自动状态*)"},"LAHU02G04_A             AT%I1.6        :BOOL; (*空调机组NJ-2AP(KT)7-4-自动状态*)",null,"L17\\L17AHU02G04_A","空调机组NJ-2AP(KT)7-4-自动状态",10014]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-2AP(KT)7-4-风机压差",{"$nulls":16},"NJ-2AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-4","02G04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH24,List!$B$3:$D$445,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,List!$K$2:$M$447,2,FALSE)","v":"AHU02G04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%I\"&B10*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":"LAHU02G04_FPS AT%I1.7 :BOOL; (*空调机组NJ-2AP(KT)7-4-风机压差*)"},"LAHU02G04_FPS           AT%I1.7        :BOOL; (*空调机组NJ-2AP(KT)7-4-风机压差*)",null,"L17\\L17AHU02G04_FPS","空调机组NJ-2AP(KT)7-4-风机压差",10015]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 1601R地址: 1 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH26&AA26&\"-\"&AK26","v":"空调机组NJ-2AP(KT)7-5-运行状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-2AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-5","02G05","运行状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU02G05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU02G05_R AT%I16.0 :BOOL; (*空调机组NJ-2AP(KT)7-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LAHU02G05_R             AT%I16.0       :BOOL; (*空调机组NJ-2AP(KT)7-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L17\\L17AHU02G05_R"},{"$f":"J26","v":"空调机组NJ-2AP(KT)7-5-运行状态"},{"$f":"10000+($B27*16*8+F26-1)","v":10128}]
[null,1,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-2AP(KT)7-5-故障状态",{"$nulls":16},{"$f":"IF(AI27=\"\",\"\",AI27)","v":"NJ-2AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-5","02G05","故障状态",{"$f":"AH27&\"-\"&AK27","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU02G05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU02G05_F AT%I16.1 :BOOL; (*空调机组NJ-2AP(KT)7-5-故障状态*)"},"LAHU02G05_F             AT%I16.1       :BOOL; (*空调机组NJ-2AP(KT)7-5-故障状态*)",null,"L17\\L17AHU02G05_F",{"$f":"J27","v":"空调机组NJ-2AP(KT)7-5-故障状态"},{"$f":"AS26+1","v":10129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-2AP(KT)7-5-自动状态",{"$nulls":16},"NJ-2AP(KT)7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-5","02G05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU02G05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU02G05_A AT%I16.2 :BOOL; (*空调机组NJ-2AP(KT)7-5-自动状态*)"},"LAHU02G05_A             AT%I16.2       :BOOL; (*空调机组NJ-2AP(KT)7-5-自动状态*)",null,"L17\\L17AHU02G05_A","空调机组NJ-2AP(KT)7-5-自动状态",{"$f":"AS27+1","v":10130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-2AP(KT)7-5-风机压差",{"$nulls":16},"NJ-2AP(KT)7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-5","02G05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU02G05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU02G05_FPS AT%I16.3 :BOOL; (*空调机组NJ-2AP(KT)7-5-风机压差*)"},"LAHU02G05_FPS           AT%I16.3       :BOOL; (*空调机组NJ-2AP(KT)7-5-风机压差*)",null,"L17\\L17AHU02G05_FPS","空调机组NJ-2AP(KT)7-5-风机压差",10131]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-2AP(KT)7-6-运行状态",{"$nulls":16},"NJ-2AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-6","02G06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU02G06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B27*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU02G06_R AT%I16.4 :BOOL; (*空调机组NJ-2AP(KT)7-6-运行状态*)"},"LAHU02G06_R             AT%I16.4       :BOOL; (*空调机组NJ-2AP(KT)7-6-运行状态*)",null,"L17\\L17AHU02G06_R","空调机组NJ-2AP(KT)7-6-运行状态",10132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-2AP(KT)7-6-故障状态",{"$nulls":16},"NJ-2AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-6","02G06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU02G06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B27*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU02G06_F AT%I16.5 :BOOL; (*空调机组NJ-2AP(KT)7-6-故障状态*)"},"LAHU02G06_F             AT%I16.5       :BOOL; (*空调机组NJ-2AP(KT)7-6-故障状态*)",null,"L17\\L17AHU02G06_F","空调机组NJ-2AP(KT)7-6-故障状态",10133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-2AP(KT)7-6-自动状态",{"$nulls":16},"NJ-2AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-6","02G06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU02G06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B27*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU02G06_A AT%I16.6 :BOOL; (*空调机组NJ-2AP(KT)7-6-自动状态*)"},"LAHU02G06_A             AT%I16.6       :BOOL; (*空调机组NJ-2AP(KT)7-6-自动状态*)",null,"L17\\L17AHU02G06_A","空调机组NJ-2AP(KT)7-6-自动状态",10134]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-2AP(KT)7-6-风机压差",{"$nulls":16},"NJ-2AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-6","02G06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU02G06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B27*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU02G06_FPS AT%I16.7 :BOOL; (*空调机组NJ-2AP(KT)7-6-风机压差*)"},"LAHU02G06_FPS           AT%I16.7       :BOOL; (*空调机组NJ-2AP(KT)7-6-风机压差*)",null,"L17\\L17AHU02G06_FPS","空调机组NJ-2AP(KT)7-6-风机压差",10135]
[{"$nulls":5},9,null,17,18,"空调机组NJ-2AP(KT)7-7-运行状态",{"$nulls":16},"NJ-2AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-7","02G07","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU02G07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B27*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU02G07_R AT%I17.0 :BOOL; (*空调机组NJ-2AP(KT)7-7-运行状态*)"},"LAHU02G07_R             AT%I17.0       :BOOL; (*空调机组NJ-2AP(KT)7-7-运行状态*)",null,"L17\\L17AHU02G07_R","空调机组NJ-2AP(KT)7-7-运行状态",10136]
[{"$nulls":5},10,null,19,20,"空调机组NJ-2AP(KT)7-7-故障状态",{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-2AP(KT)7-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-7","02G07","故障状态",{"$f":"AH35&\"-\"&AK35","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU02G07_F"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B27*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU02G07_F AT%I17.1 :BOOL; (*空调机组NJ-2AP(KT)7-7-故障状态*)"},"LAHU02G07_F             AT%I17.1       :BOOL; (*空调机组NJ-2AP(KT)7-7-故障状态*)",null,"L17\\L17AHU02G07_F",{"$f":"J35","v":"空调机组NJ-2AP(KT)7-7-故障状态"},10137]
[{"$nulls":5},11,null,21,22,"空调机组NJ-2AP(KT)7-7-自动状态",{"$nulls":16},"NJ-2AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-7","02G07","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU02G07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B27*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU02G07_A AT%I17.2 :BOOL; (*空调机组NJ-2AP(KT)7-7-自动状态*)"},"LAHU02G07_A             AT%I17.2       :BOOL; (*空调机组NJ-2AP(KT)7-7-自动状态*)",null,"L17\\L17AHU02G07_A","空调机组NJ-2AP(KT)7-7-自动状态",10138]
[{"$nulls":5},12,null,23,24,"空调机组NJ-2AP(KT)7-7-风机压差",{"$nulls":16},"NJ-2AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-7","02G07","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"AHU02G07_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B27*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LAHU02G07_FPS AT%I17.3 :BOOL; (*空调机组NJ-2AP(KT)7-7-风机压差*)"},"LAHU02G07_FPS           AT%I17.3       :BOOL; (*空调机组NJ-2AP(KT)7-7-风机压差*)",null,"L17\\L17AHU02G07_FPS","空调机组NJ-2AP(KT)7-7-风机压差",10139]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-2AL7-1-运行状态",{"$nulls":16},"NJ-2AL7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL7-1","02G01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB02G01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B27*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB02G01_R AT%I17.4 :BOOL; (*照明控制箱NJ-2AL7-1-运行状态*)"},"LLCB02G01_R             AT%I17.4       :BOOL; (*照明控制箱NJ-2AL7-1-运行状态*)",null,"L17\\L17LCB02G01_R","照明控制箱NJ-2AL7-1-运行状态",10140]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-2AL7-1-自动状态",{"$nulls":16},"NJ-2AL7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL7-1","02G01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB02G01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B27*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB02G01_A AT%I17.5 :BOOL; (*照明控制箱NJ-2AL7-1-自动状态*)"},"LLCB02G01_A             AT%I17.5       :BOOL; (*照明控制箱NJ-2AL7-1-自动状态*)",null,"L17\\L17LCB02G01_A","照明控制箱NJ-2AL7-1-自动状态",10141]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-2AL7-2-运行状态",{"$nulls":16},"NJ-2AL7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL7-2","02G02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"LCB02G02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B27*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LLCB02G02_R AT%I17.6 :BOOL; (*照明控制箱NJ-2AL7-2-运行状态*)"},"LLCB02G02_R             AT%I17.6       :BOOL; (*照明控制箱NJ-2AL7-2-运行状态*)",null,"L17\\L17LCB02G02_R","照明控制箱NJ-2AL7-2-运行状态",10142]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-2AL7-2-自动状态",{"$nulls":16},"NJ-2AL7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL7-2","02G02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":"LCB02G02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%I\"&B27*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":"LLCB02G02_A AT%I17.7 :BOOL; (*照明控制箱NJ-2AL7-2-自动状态*)"},"LLCB02G02_A             AT%I17.7       :BOOL; (*照明控制箱NJ-2AL7-2-自动状态*)",null,"L17\\L17LCB02G02_A","照明控制箱NJ-2AL7-2-自动状态",10143]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 0801R 地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH43&AA43&\"-\"&AK43","v":"照明控制箱NJ-2AL7-3-运行状态"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-2AL7-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL7-3","02G03","运行状态",{"$f":"AH43&\"-\"&AK43","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"LCB02G03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B44*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LLCB02G03_R AT%I32.0 :BOOL; (*照明控制箱NJ-2AL7-3-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LLCB02G03_R             AT%I32.0       :BOOL; (*照明控制箱NJ-2AL7-3-运行状态*)"},null,{"$f":"AM43","v":"LCB02G03_R"},{"$f":"J43","v":"照明控制箱NJ-2AL7-3-运行状态"},{"$f":"10000+($B44*16*8+F43-1)","v":10256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},2,null,2,"C",{"$f":"AH44&AA44&\"-\"&AK44","v":"照明控制箱NJ-2AL7-3-自动状态"},{"$nulls":16},{"$f":"IF(AI44=\"\",\"\",AI44)","v":"NJ-2AL7-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL7-3","02G03","自动状态",{"$f":"AH44&\"-\"&AK44","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"LCB02G03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B44*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LLCB02G03_A AT%I32.1 :BOOL; (*照明控制箱NJ-2AL7-3-自动状态*)"},"LLCB02G03_A             AT%I32.1       :BOOL; (*照明控制箱NJ-2AL7-3-自动状态*)",null,{"$f":"AM44","v":"LCB02G03_A"},{"$f":"J44","v":"照明控制箱NJ-2AL7-3-自动状态"},{"$f":"AS43+1","v":10257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,3,"C",{"$f":"AH45&AA45&\"-\"&AK45","v":"照明控制箱NJ-2AL7-4-运行状态"},{"$nulls":16},"NJ-2AL7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL7-4","02G04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"LCB02G04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B44*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LLCB02G04_R AT%I32.2 :BOOL; (*照明控制箱NJ-2AL7-4-运行状态*)"},"LLCB02G04_R             AT%I32.2       :BOOL; (*照明控制箱NJ-2AL7-4-运行状态*)",null,"LCB02G04_R","照明控制箱NJ-2AL7-4-运行状态",{"$f":"AS44+1","v":10258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},4,null,4,"C",{"$f":"AH46&AA46&\"-\"&AK46","v":"照明控制箱NJ-2AL7-4-自动状态"},{"$nulls":16},"NJ-2AL7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL7-4","02G04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"LCB02G04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B44*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LLCB02G04_A AT%I32.3 :BOOL; (*照明控制箱NJ-2AL7-4-自动状态*)"},"LLCB02G04_A             AT%I32.3       :BOOL; (*照明控制箱NJ-2AL7-4-自动状态*)",null,"LCB02G04_A","照明控制箱NJ-2AL7-4-自动状态",10259]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},5,null,5,"C","照明控制箱NJ-2AL7-5-运行状态",{"$nulls":16},"NJ-2AL7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL7-5","02G05","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"LCB02G05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B44*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LLCB02G05_R AT%I32.4 :BOOL; (*照明控制箱NJ-2AL7-5-运行状态*)"},"LLCB02G05_R             AT%I32.4       :BOOL; (*照明控制箱NJ-2AL7-5-运行状态*)",null,"LCB02G05_R","照明控制箱NJ-2AL7-5-运行状态",10260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","照明控制箱NJ-2AL7-5-自动状态",{"$nulls":16},"NJ-2AL7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL7-5","02G05","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"LCB02G05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B44*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LLCB02G05_A AT%I32.5 :BOOL; (*照明控制箱NJ-2AL7-5-自动状态*)"},"LLCB02G05_A             AT%I32.5       :BOOL; (*照明控制箱NJ-2AL7-5-自动状态*)",null,"LCB02G05_A","照明控制箱NJ-2AL7-5-自动状态",10261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B44*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10262]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B44*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10263]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B56&\"地址: \"&B53&\" *)\"","v":"(* IOM 1601D地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH52&AA52&\"-\"&AK52","v":"空调机组NJ-2AP(KT)7-1-启停控制"},{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-2AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-1","02G01","启停控制",{"$f":"AH52&\"-\"&AK52","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"AHU02G01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%Q\"&B53*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LAHU02G01_C AT%Q48.0 :BOOL; (*空调机组NJ-2AP(KT)7-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN52,SEARCH(\"AT%\",AN52),,REPT(\" \",25-SEARCH(\"AT%\",AN52))),SEARCH(\":\",REPLACE(AN52,SEARCH(\"AT%\",AN52),,REPT(\" \",25-SEARCH(\"AT%\",AN52)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN52,SEARCH(\"AT%\",AN52),,REPT(\" \",25-SEARCH(\"AT%\",AN52)))))),\" \")","v":"LAHU02G01_C             AT%Q48.0       :BOOL; (*空调机组NJ-2AP(KT)7-1-启停控制*)"},null,{"$f":"AM52","v":"AHU02G01_C"},{"$f":"J52","v":"空调机组NJ-2AP(KT)7-1-启停控制"},{"$f":"($B53*16*8+F52-1)","v":384}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-2AP(KT)7-2-启停控制",{"$nulls":16},{"$f":"IF(AI53=\"\",\"\",AI53)","v":"NJ-2AP(KT)7-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-2","02G02","启停控制",{"$f":"AH53&\"-\"&AK53","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"AHU02G02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%Q\"&B53*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LAHU02G02_C AT%Q48.1 :BOOL; (*空调机组NJ-2AP(KT)7-2-启停控制*)"},"LAHU02G02_C             AT%Q48.1       :BOOL; (*空调机组NJ-2AP(KT)7-2-启停控制*)",null,"AHU02G02_C",{"$f":"J53","v":"空调机组NJ-2AP(KT)7-2-启停控制"},{"$f":"AS52+1","v":385}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","空调机组NJ-2AP(KT)7-3-启停控制",{"$nulls":16},"NJ-2AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-3","02G03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"AHU02G03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%Q\"&B53*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LAHU02G03_C AT%Q48.2 :BOOL; (*空调机组NJ-2AP(KT)7-3-启停控制*)"},"LAHU02G03_C             AT%Q48.2       :BOOL; (*空调机组NJ-2AP(KT)7-3-启停控制*)",null,"AHU02G03_C","空调机组NJ-2AP(KT)7-3-启停控制",{"$f":"AS53+1","v":386}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","空调机组NJ-2AP(KT)7-4-启停控制",{"$nulls":16},"NJ-2AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-4","02G04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"AHU02G04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%Q\"&B53*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LAHU02G04_C AT%Q48.3 :BOOL; (*空调机组NJ-2AP(KT)7-4-启停控制*)"},"LAHU02G04_C             AT%Q48.3       :BOOL; (*空调机组NJ-2AP(KT)7-4-启停控制*)",null,"AHU02G04_C","空调机组NJ-2AP(KT)7-4-启停控制",387]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B53),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-2AP(KT)7-5-启停控制",{"$nulls":16},"NJ-2AP(KT)7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-5","02G05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"AHU02G05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%Q\"&B53*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LAHU02G05_C AT%Q48.4 :BOOL; (*空调机组NJ-2AP(KT)7-5-启停控制*)"},"LAHU02G05_C             AT%Q48.4       :BOOL; (*空调机组NJ-2AP(KT)7-5-启停控制*)",null,"AHU02G05_C","空调机组NJ-2AP(KT)7-5-启停控制",388]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-2AP(KT)7-6-启停控制",{"$nulls":16},"NJ-2AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-6","02G06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"AHU02G06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%Q\"&B53*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LAHU02G06_C AT%Q48.5 :BOOL; (*空调机组NJ-2AP(KT)7-6-启停控制*)"},"LAHU02G06_C             AT%Q48.5       :BOOL; (*空调机组NJ-2AP(KT)7-6-启停控制*)",null,"AHU02G06_C","空调机组NJ-2AP(KT)7-6-启停控制",389]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","空调机组NJ-2AP(KT)7-7-启停控制",{"$nulls":16},"NJ-2AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-7","02G07","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":"AHU02G07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%Q\"&B53*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":"LAHU02G07_C AT%Q48.6 :BOOL; (*空调机组NJ-2AP(KT)7-7-启停控制*)"},"LAHU02G07_C             AT%Q48.6       :BOOL; (*空调机组NJ-2AP(KT)7-7-启停控制*)",null,"AHU02G07_C","空调机组NJ-2AP(KT)7-7-启停控制",390]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B55=20,1,IF(B55=50,10,IF(B55=125,11,IF(B55=250,100,IF(B55=500,101,IF(B55=800,110,IF(B55=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-2AL7-1-启停控制",{"$nulls":16},"NJ-2AL7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL7-1","02G01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH59,List!$B$3:$D$445,2,FALSE)&AJ59&\"_\"&VLOOKUP(AK59,List!$K$2:$M$447,2,FALSE)","v":"LCB02G01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM59&\" \"&\"AT%Q\"&B53*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J59&\"*)\",\" \")","v":"LLCB02G01_C AT%Q48.7 :BOOL; (*照明控制箱NJ-2AL7-1-启停控制*)"},"LLCB02G01_C             AT%Q48.7       :BOOL; (*照明控制箱NJ-2AL7-1-启停控制*)",null,"LCB02G01_C","照明控制箱NJ-2AL7-1-启停控制",391]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-2AL7-2-启停控制",{"$nulls":16},"NJ-2AL7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL7-2","02G02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"LCB02G02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%Q\"&B53*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LLCB02G02_C AT%Q49.0 :BOOL; (*照明控制箱NJ-2AL7-2-启停控制*)"},"LLCB02G02_C             AT%Q49.0       :BOOL; (*照明控制箱NJ-2AL7-2-启停控制*)",null,"LCB02G02_C","照明控制箱NJ-2AL7-2-启停控制",392]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-2AL7-3-启停控制",{"$nulls":16},{"$f":"IF(AI61=\"\",\"\",AI61)","v":"NJ-2AL7-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL7-3","02G03","启停控制",{"$f":"AH61&\"-\"&AK61","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"LCB02G03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%Q\"&B53*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LLCB02G03_C AT%Q49.1 :BOOL; (*照明控制箱NJ-2AL7-3-启停控制*)"},"LLCB02G03_C             AT%Q49.1       :BOOL; (*照明控制箱NJ-2AL7-3-启停控制*)",null,"LCB02G03_C",{"$f":"J61","v":"照明控制箱NJ-2AL7-3-启停控制"},393]
[{"$nulls":5},11,null,"11+","11-","照明控制箱NJ-2AL7-4-启停控制",{"$nulls":16},"NJ-2AL7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL7-4","02G04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"LCB02G04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%Q\"&B53*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LLCB02G04_C AT%Q49.2 :BOOL; (*照明控制箱NJ-2AL7-4-启停控制*)"},"LLCB02G04_C             AT%Q49.2       :BOOL; (*照明控制箱NJ-2AL7-4-启停控制*)",null,"LCB02G04_C","照明控制箱NJ-2AL7-4-启停控制",394]
[{"$nulls":5},12,null,"12+","12-","照明控制箱NJ-2AL7-5-启停控制",{"$nulls":16},"NJ-2AL7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL7-5","02G05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"LCB02G05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%Q\"&B53*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LLCB02G05_C AT%Q49.3 :BOOL; (*照明控制箱NJ-2AL7-5-启停控制*)"},"LLCB02G05_C             AT%Q49.3       :BOOL; (*照明控制箱NJ-2AL7-5-启停控制*)",null,"LCB02G05_C","照明控制箱NJ-2AL7-5-启停控制",395]
[{"$nulls":5},13,null,"13+","13-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%Q\"&B53*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",396]
[{"$nulls":5},14,null,"14+","14-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%Q\"&B53*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",397]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%Q\"&B53*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",398]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%Q\"&B53*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",399]
[null,{"$f":"B73","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B73&\"地址: \"&B70&\" *)\"","v":"(* IOM 0801U地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH69&AA69&\"-\"&AK69","v":"空调机组NJ-2AP(KT)7-1-回风温度"},{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-2AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-1","02G01","回风温度",{"$f":"AH69&\"-\"&AK69","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU02G01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%I\"&B70*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU02G01_RT AT%I64.0 :INT ; (*空调机组NJ-2AP(KT)7-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69))),SEARCH(\":\",REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69)))))),\" \")","v":"LAHU02G01_RT            AT%I64.0       :INT ; (*空调机组NJ-2AP(KT)7-1-回风温度*)"},null,{"$f":"AM69","v":"AHU02G01_RT"},{"$f":"J69","v":"空调机组NJ-2AP(KT)7-1-回风温度"},{"$f":"30000+($B70*8+F69-1)","v":30032}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-2AP(KT)7-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI70=\"\",\"\",AI70)","v":"NJ-2AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-1","02G01","水阀反馈",{"$f":"AH70&\"-\"&AK70","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"AHU02G01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%I\"&B70*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LAHU02G01_WVB AT%I66.0 :INT ; (*空调机组NJ-2AP(KT)7-1-水阀反馈*)"},"LAHU02G01_WVB           AT%I66.0       :INT ; (*空调机组NJ-2AP(KT)7-1-水阀反馈*)",null,"AHU02G01_WVB",{"$f":"J70","v":"空调机组NJ-2AP(KT)7-1-水阀反馈"},{"$f":"AS69+1","v":30033}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-2AP(KT)7-2-回风温度",{"$nulls":16},"NJ-2AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-2","02G02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"AHU02G02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%I\"&B70*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LAHU02G02_RT AT%I68.0 :INT ; (*空调机组NJ-2AP(KT)7-2-回风温度*)"},"LAHU02G02_RT            AT%I68.0       :INT ; (*空调机组NJ-2AP(KT)7-2-回风温度*)",null,"AHU02G02_RT","空调机组NJ-2AP(KT)7-2-回风温度",{"$f":"AS70+1","v":30034}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-2AP(KT)7-2-水阀反馈",{"$nulls":16},"NJ-2AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-2","02G02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"AHU02G02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%I\"&B70*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LAHU02G02_WVB AT%I70.0 :INT ; (*空调机组NJ-2AP(KT)7-2-水阀反馈*)"},"LAHU02G02_WVB           AT%I70.0       :INT ; (*空调机组NJ-2AP(KT)7-2-水阀反馈*)",null,"AHU02G02_WVB","空调机组NJ-2AP(KT)7-2-水阀反馈",30035]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-2AP(KT)7-3-回风温度",{"$nulls":16},"NJ-2AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-3","02G03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"AHU02G03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%I\"&B70*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LAHU02G03_RT AT%I72.0 :INT ; (*空调机组NJ-2AP(KT)7-3-回风温度*)"},"LAHU02G03_RT            AT%I72.0       :INT ; (*空调机组NJ-2AP(KT)7-3-回风温度*)",null,"AHU02G03_RT","空调机组NJ-2AP(KT)7-3-回风温度",30036]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-2AP(KT)7-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI74=\"\",\"\",AI74)","v":"NJ-2AP(KT)7-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-3","02G03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":"AHU02G03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%I\"&B70*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":"LAHU02G03_WVB AT%I74.0 :INT ; (*空调机组NJ-2AP(KT)7-3-水阀反馈*)"},"LAHU02G03_WVB           AT%I74.0       :INT ; (*空调机组NJ-2AP(KT)7-3-水阀反馈*)",null,"AHU02G03_WVB",{"$f":"J74","v":"空调机组NJ-2AP(KT)7-3-水阀反馈"},30037]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-2AP(KT)7-4-回风温度",{"$nulls":16},"NJ-2AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-4","02G04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":"AHU02G04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%I\"&B70*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":"LAHU02G04_RT AT%I76.0 :INT ; (*空调机组NJ-2AP(KT)7-4-回风温度*)"},"LAHU02G04_RT            AT%I76.0       :INT ; (*空调机组NJ-2AP(KT)7-4-回风温度*)",null,"AHU02G04_RT","空调机组NJ-2AP(KT)7-4-回风温度",30038]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-2AP(KT)7-4-水阀反馈",{"$nulls":16},"NJ-2AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-4","02G04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH76,List!$B$3:$D$445,2,FALSE)&AJ76&\"_\"&VLOOKUP(AK76,List!$K$2:$M$447,2,FALSE)","v":"AHU02G04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM76&\" \"&\"AT%I\"&B70*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J76&\"*)\",\" \")","v":"LAHU02G04_WVB AT%I78.0 :INT ; (*空调机组NJ-2AP(KT)7-4-水阀反馈*)"},"LAHU02G04_WVB           AT%I78.0       :INT ; (*空调机组NJ-2AP(KT)7-4-水阀反馈*)",null,"AHU02G04_WVB","空调机组NJ-2AP(KT)7-4-水阀反馈",30039]
[null,{"$f":"B82","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B82&\"地址: \"&B79&\" *)\"","v":"(* IOM 0801U地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH78&AA78&\"-\"&AK78","v":"空调机组NJ-2AP(KT)7-5-回风温度"},{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-2AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-5","02G05","回风温度",{"$f":"AH78&\"-\"&AK78","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU02G05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%I\"&B79*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU02G05_RT AT%I80.0 :INT ; (*空调机组NJ-2AP(KT)7-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN78,SEARCH(\"AT%\",AN78),,REPT(\" \",25-SEARCH(\"AT%\",AN78))),SEARCH(\":\",REPLACE(AN78,SEARCH(\"AT%\",AN78),,REPT(\" \",25-SEARCH(\"AT%\",AN78)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN78,SEARCH(\"AT%\",AN78),,REPT(\" \",25-SEARCH(\"AT%\",AN78)))))),\" \")","v":"LAHU02G05_RT            AT%I80.0       :INT ; (*空调机组NJ-2AP(KT)7-5-回风温度*)"},null,{"$f":"AM78","v":"AHU02G05_RT"},{"$f":"J78","v":"空调机组NJ-2AP(KT)7-5-回风温度"},{"$f":"30000+($B79*8+F78-1)","v":30040}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-2AP(KT)7-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI79=\"\",\"\",AI79)","v":"NJ-2AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-5","02G05","水阀反馈",{"$f":"AH79&\"-\"&AK79","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU02G05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%I\"&B79*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU02G05_WVB AT%I82.0 :INT ; (*空调机组NJ-2AP(KT)7-5-水阀反馈*)"},"LAHU02G05_WVB           AT%I82.0       :INT ; (*空调机组NJ-2AP(KT)7-5-水阀反馈*)",null,"AHU02G05_WVB",{"$f":"J79","v":"空调机组NJ-2AP(KT)7-5-水阀反馈"},{"$f":"AS78+1","v":30041}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-2AP(KT)7-6-回风温度",{"$nulls":16},"NJ-2AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-6","02G06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU02G06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%I\"&B79*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU02G06_RT AT%I84.0 :INT ; (*空调机组NJ-2AP(KT)7-6-回风温度*)"},"LAHU02G06_RT            AT%I84.0       :INT ; (*空调机组NJ-2AP(KT)7-6-回风温度*)",null,"AHU02G06_RT","空调机组NJ-2AP(KT)7-6-回风温度",{"$f":"AS79+1","v":30042}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-2AP(KT)7-6-水阀反馈",{"$nulls":16},"NJ-2AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-6","02G06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"AHU02G06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%I\"&B79*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LAHU02G06_WVB AT%I86.0 :INT ; (*空调机组NJ-2AP(KT)7-6-水阀反馈*)"},"LAHU02G06_WVB           AT%I86.0       :INT ; (*空调机组NJ-2AP(KT)7-6-水阀反馈*)",null,"AHU02G06_WVB","空调机组NJ-2AP(KT)7-6-水阀反馈",30043]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B79),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-2AP(KT)7-7-回风温度",{"$nulls":16},"NJ-2AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-7","02G07","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":"AHU02G07_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%I\"&B79*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":"LAHU02G07_RT AT%I88.0 :INT ; (*空调机组NJ-2AP(KT)7-7-回风温度*)"},"LAHU02G07_RT            AT%I88.0       :INT ; (*空调机组NJ-2AP(KT)7-7-回风温度*)",null,"AHU02G07_RT","空调机组NJ-2AP(KT)7-7-回风温度",30044]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-2AP(KT)7-7-水阀反馈",{"$nulls":16},{"$f":"IF(AI83=\"\",\"\",AI83)","v":"NJ-2AP(KT)7-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-7","02G07","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":"AHU02G07_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%I\"&B79*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":"LAHU02G07_WVB AT%I90.0 :INT ; (*空调机组NJ-2AP(KT)7-7-水阀反馈*)"},"LAHU02G07_WVB           AT%I90.0       :INT ; (*空调机组NJ-2AP(KT)7-7-水阀反馈*)",null,"AHU02G07_WVB",{"$f":"J83","v":"空调机组NJ-2AP(KT)7-7-水阀反馈"},30045]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH84,List!$B$3:$D$445,2,FALSE)&AJ84&\"_\"&VLOOKUP(AK84,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM84&\" \"&\"AT%I\"&B79*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J84&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30046]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B81=20,1,IF(B81=50,10,IF(B81=125,11,IF(B81=250,100,IF(B81=500,101,IF(B81=800,110,IF(B81=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH85,List!$B$3:$D$445,2,FALSE)&AJ85&\"_\"&VLOOKUP(AK85,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM85&\" \"&\"AT%I\"&B79*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J85&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30047]
[null,{"$f":"B91","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B91&\"地址: \"&B88&\" *)\"","v":"(* IOM 0401A地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH87&AA87&\"-\"&AK87","v":"空调机组NJ-2AP(KT)7-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI87=\"\",\"\",AI87)","v":"NJ-2AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-1","02G01","水阀控制",{"$f":"AH87&\"-\"&AK87","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"AHU02G01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%Q\"&B88*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LAHU02G01_WVC AT%Q96.0 :INT ; (*空调机组NJ-2AP(KT)7-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN87,SEARCH(\"AT%\",AN87),,REPT(\" \",25-SEARCH(\"AT%\",AN87))),SEARCH(\":\",REPLACE(AN87,SEARCH(\"AT%\",AN87),,REPT(\" \",25-SEARCH(\"AT%\",AN87)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN87,SEARCH(\"AT%\",AN87),,REPT(\" \",25-SEARCH(\"AT%\",AN87)))))),\" \")","v":"LAHU02G01_WVC           AT%Q96.0       :INT ; (*空调机组NJ-2AP(KT)7-1-水阀控制*)"},null,{"$f":"AM87","v":"AHU02G01_WVC"},{"$f":"J87","v":"空调机组NJ-2AP(KT)7-1-水阀控制"},{"$f":"40000+($B88*8+F87-1)","v":40048}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH88&AA88&\"-\"&AK88","v":"空调机组NJ-2AP(KT)7-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI88=\"\",\"\",AI88)","v":"NJ-2AP(KT)7-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-2","02G02","水阀控制",{"$f":"AH88&\"-\"&AK88","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"AHU02G02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%Q\"&B88*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LAHU02G02_WVC AT%Q98.0 :INT ; (*空调机组NJ-2AP(KT)7-2-水阀控制*)"},"LAHU02G02_WVC           AT%Q98.0       :INT ; (*空调机组NJ-2AP(KT)7-2-水阀控制*)",null,"AHU02G02_WVC",{"$f":"J88","v":"空调机组NJ-2AP(KT)7-2-水阀控制"},{"$f":"AS87+1","v":40049}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH89&AA89&\"-\"&AK89","v":"空调机组NJ-2AP(KT)7-3-水阀控制"},{"$nulls":16},"NJ-2AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-3","02G03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"AHU02G03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%Q\"&B88*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LAHU02G03_WVC AT%Q100.0 :INT ; (*空调机组NJ-2AP(KT)7-3-水阀控制*)"},"LAHU02G03_WVC           AT%Q100.0      :INT ; (*空调机组NJ-2AP(KT)7-3-水阀控制*)",null,"AHU02G03_WVC","空调机组NJ-2AP(KT)7-3-水阀控制",{"$f":"AS88+1","v":40050}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH90&AA90&\"-\"&AK90","v":"空调机组NJ-2AP(KT)7-4-水阀控制"},{"$nulls":16},"NJ-2AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-4","02G04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":"AHU02G04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%Q\"&B88*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":"LAHU02G04_WVC AT%Q102.0 :INT ; (*空调机组NJ-2AP(KT)7-4-水阀控制*)"},"LAHU02G04_WVC           AT%Q102.0      :INT ; (*空调机组NJ-2AP(KT)7-4-水阀控制*)",null,"AHU02G04_WVC","空调机组NJ-2AP(KT)7-4-水阀控制",40051]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B88),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B90=20,1,IF(B90=50,10,IF(B90=125,11,IF(B90=250,100,IF(B90=500,101,IF(B90=800,110,IF(B90=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B100","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B100&\"地址: \"&B97&\" *)\"","v":"(* IOM 0401A地址: 7 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B97),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B97),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH96&AA96&\"-\"&AK96","v":"空调机组NJ-2AP(KT)7-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI96=\"\",\"\",AI96)","v":"NJ-2AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-5","02G05","水阀控制",{"$f":"AH96&\"-\"&AK96","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"AHU02G05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%Q\"&B97*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LAHU02G05_WVC AT%Q112.0 :INT ; (*空调机组NJ-2AP(KT)7-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN96,SEARCH(\"AT%\",AN96),,REPT(\" \",25-SEARCH(\"AT%\",AN96))),SEARCH(\":\",REPLACE(AN96,SEARCH(\"AT%\",AN96),,REPT(\" \",25-SEARCH(\"AT%\",AN96)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN96,SEARCH(\"AT%\",AN96),,REPT(\" \",25-SEARCH(\"AT%\",AN96)))))),\" \")","v":"LAHU02G05_WVC           AT%Q112.0      :INT ; (*空调机组NJ-2AP(KT)7-5-水阀控制*)"},null,{"$f":"AM96","v":"AHU02G05_WVC"},{"$f":"J96","v":"空调机组NJ-2AP(KT)7-5-水阀控制"},{"$f":"40000+($B97*8+F96-1)","v":40056}]
[null,7,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B97),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B97),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH97&AA97&\"-\"&AK97","v":"空调机组NJ-2AP(KT)7-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI97=\"\",\"\",AI97)","v":"NJ-2AP(KT)7-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-6","02G06","水阀控制",{"$f":"AH97&\"-\"&AK97","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":"AHU02G06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%Q\"&B97*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":"LAHU02G06_WVC AT%Q114.0 :INT ; (*空调机组NJ-2AP(KT)7-6-水阀控制*)"},"LAHU02G06_WVC           AT%Q114.0      :INT ; (*空调机组NJ-2AP(KT)7-6-水阀控制*)",null,"AHU02G06_WVC",{"$f":"J97","v":"空调机组NJ-2AP(KT)7-6-水阀控制"},{"$f":"AS96+1","v":40057}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B97),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B97),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH98&AA98&\"-\"&AK98","v":"空调机组NJ-2AP(KT)7-7-水阀控制"},{"$nulls":16},"NJ-2AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)7-7","02G07","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":"AHU02G07_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%Q\"&B97*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":"LAHU02G07_WVC AT%Q116.0 :INT ; (*空调机组NJ-2AP(KT)7-7-水阀控制*)"},"LAHU02G07_WVC           AT%Q116.0      :INT ; (*空调机组NJ-2AP(KT)7-7-水阀控制*)",null,"AHU02G07_WVC","空调机组NJ-2AP(KT)7-7-水阀控制",{"$f":"AS97+1","v":40058}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B97),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B97),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH99&AA99&\"-\"&AK99","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH99,List!$B$3:$D$445,2,FALSE)&AJ99&\"_\"&VLOOKUP(AK99,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM99&\" \"&\"AT%Q\"&B97*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J99&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40059]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B97),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B97),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B99=20,1,IF(B99=50,10,IF(B99=125,11,IF(B99=250,100,IF(B99=500,101,IF(B99=800,110,IF(B99=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B99=20,1,IF(B99=50,10,IF(B99=125,11,IF(B99=250,100,IF(B99=500,101,IF(B99=800,110,IF(B99=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B99=20,1,IF(B99=50,10,IF(B99=125,11,IF(B99=250,100,IF(B99=500,101,IF(B99=800,110,IF(B99=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B99=20,1,IF(B99=50,10,IF(B99=125,11,IF(B99=250,100,IF(B99=500,101,IF(B99=800,110,IF(B99=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B99=20,1,IF(B99=50,10,IF(B99=125,11,IF(B99=250,100,IF(B99=500,101,IF(B99=800,110,IF(B99=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B99=20,1,IF(B99=50,10,IF(B99=125,11,IF(B99=250,100,IF(B99=500,101,IF(B99=800,110,IF(B99=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L107","index":18,"n_rows":137,"n_cols":45,"rows_kept":137,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[41,5,41,6],[41,9,41,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[75,5,75,6],[75,9,75,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[84,5,84,6],[84,9,84,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[93,5,93,6],[93,9,93,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[102,5,102,6],[102,9,102,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[109,5,109,6],[109,9,109,25],[111,5,111,6],[111,9,111,25],[112,5,112,6],[112,9,112,25],[113,5,113,6],[113,9,113,25],[114,5,114,6],[114,9,114,25],[115,5,115,6],[115,9,115,25],[116,5,116,6],[116,9,116,25],[117,5,117,6],[117,9,117,25],[118,5,118,6],[118,9,118,25],[120,5,120,6],[120,9,120,25],[121,5,121,6],[121,9,121,25],[122,5,122,6],[122,9,122,25],[123,5,123,6],[123,9,123,25],[124,5,124,6],[124,9,124,25],[125,5,125,6],[125,9,125,25],[126,5,126,6],[126,9,126,25],[127,5,127,6],[127,9,127,25],[129,5,129,6],[129,9,129,25],[130,5,130,6],[130,9,130,25],[131,5,131,6],[131,9,131,25],[132,5,132,6],[132,9,132,25],[133,5,133,6],[133,9,133,25],[134,5,134,6],[134,9,134,25],[135,5,135,6],[135,9,135,25],[136,5,136,6],[136,9,136,25],[4,1,5,1],[11,1,22,1],[28,1,39,1],[45,1,56,1],[62,1,65,1],[71,1,82,1],[88,1,91,1],[97,1,100,1],[106,1,109,1],[115,1,118,1],[124,1,127,1],[133,1,136,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4],[32,2,39,4],[49,2,56,4],[75,2,82,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L17",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 8 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH8&AA8&\"-\"&AK8","v":"空调机组NJ-1AP(KT)7-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-1AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-1","01G01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH8,List!$B$3:$D$445,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,List!$K$2:$M$447,2,FALSE)","v":"AHU01G01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LAHU01G01_R AT%I128.0 :BOOL; (*空调机组NJ-1AP(KT)7-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LAHU01G01_R             AT%I128.0      :BOOL; (*空调机组NJ-1AP(KT)7-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L17\\L17AHU01G01_R"},{"$f":"J8","v":"空调机组NJ-1AP(KT)7-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":11024}]
[null,8,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-1AP(KT)7-1-故障状态",{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-1AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-1","01G01","故障状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU01G01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU01G01_F AT%I128.1 :BOOL; (*空调机组NJ-1AP(KT)7-1-故障状态*)"},"LAHU01G01_F             AT%I128.1      :BOOL; (*空调机组NJ-1AP(KT)7-1-故障状态*)",null,"L17\\L17AHU01G01_F",{"$f":"J9","v":"空调机组NJ-1AP(KT)7-1-故障状态"},{"$f":"AS8+1","v":11025}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-1AP(KT)7-1-自动状态",{"$nulls":16},"NJ-1AP(KT)7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-1","01G01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU01G01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU01G01_A AT%I128.2 :BOOL; (*空调机组NJ-1AP(KT)7-1-自动状态*)"},"LAHU01G01_A             AT%I128.2      :BOOL; (*空调机组NJ-1AP(KT)7-1-自动状态*)",null,"L17\\L17AHU01G01_A","空调机组NJ-1AP(KT)7-1-自动状态",{"$f":"AS9+1","v":11026}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-1AP(KT)7-1-风机压差",{"$nulls":16},"NJ-1AP(KT)7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-1","01G01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU01G01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU01G01_FPS AT%I128.3 :BOOL; (*空调机组NJ-1AP(KT)7-1-风机压差*)"},"LAHU01G01_FPS           AT%I128.3      :BOOL; (*空调机组NJ-1AP(KT)7-1-风机压差*)",null,"L17\\L17AHU01G01_FPS","空调机组NJ-1AP(KT)7-1-风机压差",11027]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-1AP(KT)7-1-运行状态",{"$nulls":16},"NJ-1AP(KT)7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-1","01G02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU01G02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU01G02_R AT%I128.4 :BOOL; (*空调机组NJ-1AP(KT)7-1-运行状态*)"},"LAHU01G02_R             AT%I128.4      :BOOL; (*空调机组NJ-1AP(KT)7-1-运行状态*)",null,"L17\\L17AHU01G02_R","空调机组NJ-1AP(KT)7-1-运行状态",11028]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-1AP(KT)7-2-故障状态",{"$nulls":16},"NJ-1AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-2","01G02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU01G02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU01G02_F AT%I128.5 :BOOL; (*空调机组NJ-1AP(KT)7-2-故障状态*)"},"LAHU01G02_F             AT%I128.5      :BOOL; (*空调机组NJ-1AP(KT)7-2-故障状态*)",null,"L17\\L17AHU01G02_F","空调机组NJ-1AP(KT)7-2-故障状态",11029]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-1AP(KT)7-2-自动状态",{"$nulls":16},"NJ-1AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-2","01G02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU01G02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU01G02_A AT%I128.6 :BOOL; (*空调机组NJ-1AP(KT)7-2-自动状态*)"},"LAHU01G02_A             AT%I128.6      :BOOL; (*空调机组NJ-1AP(KT)7-2-自动状态*)",null,"L17\\L17AHU01G02_A","空调机组NJ-1AP(KT)7-2-自动状态",11030]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-1AP(KT)7-2-风机压差",{"$nulls":16},"NJ-1AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-2","01G02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU01G02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU01G02_FPS AT%I128.7 :BOOL; (*空调机组NJ-1AP(KT)7-2-风机压差*)"},"LAHU01G02_FPS           AT%I128.7      :BOOL; (*空调机组NJ-1AP(KT)7-2-风机压差*)",null,"L17\\L17AHU01G02_FPS","空调机组NJ-1AP(KT)7-2-风机压差",11031]
[{"$nulls":5},9,null,17,18,"空调机组NJ-1AP(KT)7-2-运行状态",{"$nulls":16},"NJ-1AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-2","01G03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU01G03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU01G03_R AT%I129.0 :BOOL; (*空调机组NJ-1AP(KT)7-2-运行状态*)"},"LAHU01G03_R             AT%I129.0      :BOOL; (*空调机组NJ-1AP(KT)7-2-运行状态*)",null,"L17\\L17AHU01G03_R","空调机组NJ-1AP(KT)7-2-运行状态",11032]
[{"$nulls":5},10,null,19,20,"空调机组NJ-1AP(KT)7-3-故障状态",{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-1AP(KT)7-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-3","01G03","故障状态",{"$f":"AH17&\"-\"&AK17","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU01G03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU01G03_F AT%I129.1 :BOOL; (*空调机组NJ-1AP(KT)7-3-故障状态*)"},"LAHU01G03_F             AT%I129.1      :BOOL; (*空调机组NJ-1AP(KT)7-3-故障状态*)",null,"L17\\L17AHU01G03_F","空调机组NJ-1AP(KT)7-3-故障状态",11033]
[{"$nulls":5},11,null,21,22,"空调机组NJ-1AP(KT)7-3-自动状态",{"$nulls":16},"NJ-1AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-3","01G03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU01G03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU01G03_A AT%I129.2 :BOOL; (*空调机组NJ-1AP(KT)7-3-自动状态*)"},"LAHU01G03_A             AT%I129.2      :BOOL; (*空调机组NJ-1AP(KT)7-3-自动状态*)",null,"L17\\L17AHU01G03_A","空调机组NJ-1AP(KT)7-3-自动状态",11034]
[{"$nulls":5},12,null,23,24,"空调机组NJ-1AP(KT)7-3-风机压差",{"$nulls":16},"NJ-1AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-3","01G03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU01G03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU01G03_FPS AT%I129.3 :BOOL; (*空调机组NJ-1AP(KT)7-3-风机压差*)"},"LAHU01G03_FPS           AT%I129.3      :BOOL; (*空调机组NJ-1AP(KT)7-3-风机压差*)",null,"L17\\L17AHU01G03_FPS","空调机组NJ-1AP(KT)7-3-风机压差",11035]
[{"$nulls":5},13,null,25,26,"空调机组NJ-1AP(KT)7-4-运行状态",{"$nulls":16},"NJ-1AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-4","01G04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU01G04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU01G04_R AT%I129.4 :BOOL; (*空调机组NJ-1AP(KT)7-4-运行状态*)"},"LAHU01G04_R             AT%I129.4      :BOOL; (*空调机组NJ-1AP(KT)7-4-运行状态*)",null,"L17\\L17AHU01G04_R","空调机组NJ-1AP(KT)7-4-运行状态",11036]
[{"$nulls":5},14,null,27,28,"空调机组NJ-1AP(KT)7-4-故障状态",{"$nulls":16},"NJ-1AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-4","01G04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU01G04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU01G04_F AT%I129.5 :BOOL; (*空调机组NJ-1AP(KT)7-4-故障状态*)"},"LAHU01G04_F             AT%I129.5      :BOOL; (*空调机组NJ-1AP(KT)7-4-故障状态*)",null,"L17\\L17AHU01G04_F","空调机组NJ-1AP(KT)7-4-故障状态",11037]
[{"$nulls":5},15,null,29,30,"空调机组NJ-1AP(KT)7-4-自动状态",{"$nulls":16},"NJ-1AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-4","01G04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU01G04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU01G04_A AT%I129.6 :BOOL; (*空调机组NJ-1AP(KT)7-4-自动状态*)"},"LAHU01G04_A             AT%I129.6      :BOOL; (*空调机组NJ-1AP(KT)7-4-自动状态*)",null,"L17\\L17AHU01G04_A","空调机组NJ-1AP(KT)7-4-自动状态",11038]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-1AP(KT)7-4-风机压差",{"$nulls":16},"NJ-1AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-4","01G04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU01G04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU01G04_FPS AT%I129.7 :BOOL; (*空调机组NJ-1AP(KT)7-4-风机压差*)"},"LAHU01G04_FPS           AT%I129.7      :BOOL; (*空调机组NJ-1AP(KT)7-4-风机压差*)",null,"L17\\L17AHU01G04_FPS","空调机组NJ-1AP(KT)7-4-风机压差",11039]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 1601R地址: 9 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH25&AA25&\"-\"&AK25","v":"空调机组NJ-1AP(KT)7-5-运行状态"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-1AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-5","01G05","运行状态",{"$f":"AH25&\"-\"&AK25","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"AHU01G05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LAHU01G05_R AT%I144.0 :BOOL; (*空调机组NJ-1AP(KT)7-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LAHU01G05_R             AT%I144.0      :BOOL; (*空调机组NJ-1AP(KT)7-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L17\\L17AHU01G05_R"},{"$f":"J25","v":"空调机组NJ-1AP(KT)7-5-运行状态"},{"$f":"10000+($B26*16*8+F25-1)","v":11152}]
[null,9,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-1AP(KT)7-5-故障状态",{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-1AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-5","01G05","故障状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU01G05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU01G05_F AT%I144.1 :BOOL; (*空调机组NJ-1AP(KT)7-5-故障状态*)"},"LAHU01G05_F             AT%I144.1      :BOOL; (*空调机组NJ-1AP(KT)7-5-故障状态*)",null,"L17\\L17AHU01G05_F",{"$f":"J26","v":"空调机组NJ-1AP(KT)7-5-故障状态"},{"$f":"AS25+1","v":11153}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-1AP(KT)7-5-自动状态",{"$nulls":16},"NJ-1AP(KT)7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-5","01G05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU01G05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU01G05_A AT%I144.2 :BOOL; (*空调机组NJ-1AP(KT)7-5-自动状态*)"},"LAHU01G05_A             AT%I144.2      :BOOL; (*空调机组NJ-1AP(KT)7-5-自动状态*)",null,"L17\\L17AHU01G05_A","空调机组NJ-1AP(KT)7-5-自动状态",{"$f":"AS26+1","v":11154}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-1AP(KT)7-5-风机压差",{"$nulls":16},"NJ-1AP(KT)7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-5","01G05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU01G05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU01G05_FPS AT%I144.3 :BOOL; (*空调机组NJ-1AP(KT)7-5-风机压差*)"},"LAHU01G05_FPS           AT%I144.3      :BOOL; (*空调机组NJ-1AP(KT)7-5-风机压差*)",null,"L17\\L17AHU01G05_FPS","空调机组NJ-1AP(KT)7-5-风机压差",11155]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-1AP(KT)7-6-运行状态",{"$nulls":16},"NJ-1AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-6","01G06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU01G06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU01G06_R AT%I144.4 :BOOL; (*空调机组NJ-1AP(KT)7-6-运行状态*)"},"LAHU01G06_R             AT%I144.4      :BOOL; (*空调机组NJ-1AP(KT)7-6-运行状态*)",null,"L17\\L17AHU01G06_R","空调机组NJ-1AP(KT)7-6-运行状态",11156]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-1AP(KT)7-6-故障状态",{"$nulls":16},"NJ-1AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-6","01G06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU01G06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU01G06_F AT%I144.5 :BOOL; (*空调机组NJ-1AP(KT)7-6-故障状态*)"},"LAHU01G06_F             AT%I144.5      :BOOL; (*空调机组NJ-1AP(KT)7-6-故障状态*)",null,"L17\\L17AHU01G06_F","空调机组NJ-1AP(KT)7-6-故障状态",11157]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-1AP(KT)7-6-自动状态",{"$nulls":16},"NJ-1AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-6","01G06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU01G06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU01G06_A AT%I144.6 :BOOL; (*空调机组NJ-1AP(KT)7-6-自动状态*)"},"LAHU01G06_A             AT%I144.6      :BOOL; (*空调机组NJ-1AP(KT)7-6-自动状态*)",null,"L17\\L17AHU01G06_A","空调机组NJ-1AP(KT)7-6-自动状态",11158]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-1AP(KT)7-6-风机压差",{"$nulls":16},"NJ-1AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-6","01G06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU01G06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU01G06_FPS AT%I144.7 :BOOL; (*空调机组NJ-1AP(KT)7-6-风机压差*)"},"LAHU01G06_FPS           AT%I144.7      :BOOL; (*空调机组NJ-1AP(KT)7-6-风机压差*)",null,"L17\\L17AHU01G06_FPS","空调机组NJ-1AP(KT)7-6-风机压差",11159]
[{"$nulls":5},9,null,17,18,"空调机组NJ-1AP(KT)7-7-运行状态",{"$nulls":16},"NJ-1AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-7","01G07","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU01G07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B26*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU01G07_R AT%I145.0 :BOOL; (*空调机组NJ-1AP(KT)7-7-运行状态*)"},"LAHU01G07_R             AT%I145.0      :BOOL; (*空调机组NJ-1AP(KT)7-7-运行状态*)",null,"L17\\L17AHU01G07_R","空调机组NJ-1AP(KT)7-7-运行状态",11160]
[{"$nulls":5},10,null,19,20,"空调机组NJ-1AP(KT)7-7-故障状态",{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-1AP(KT)7-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-7","01G07","故障状态",{"$f":"AH34&\"-\"&AK34","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU01G07_F"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B26*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU01G07_F AT%I145.1 :BOOL; (*空调机组NJ-1AP(KT)7-7-故障状态*)"},"LAHU01G07_F             AT%I145.1      :BOOL; (*空调机组NJ-1AP(KT)7-7-故障状态*)",null,"L17\\L17AHU01G07_F","空调机组NJ-1AP(KT)7-7-故障状态",11161]
[{"$nulls":5},11,null,21,22,"空调机组NJ-1AP(KT)7-7-自动状态",{"$nulls":16},"NJ-1AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-7","01G07","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU01G07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B26*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU01G07_A AT%I145.2 :BOOL; (*空调机组NJ-1AP(KT)7-7-自动状态*)"},"LAHU01G07_A             AT%I145.2      :BOOL; (*空调机组NJ-1AP(KT)7-7-自动状态*)",null,"L17\\L17AHU01G07_A","空调机组NJ-1AP(KT)7-7-自动状态",11162]
[{"$nulls":5},12,null,23,24,"空调机组NJ-1AP(KT)7-7-风机压差",{"$nulls":16},"NJ-1AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-7","01G07","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU01G07_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B26*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU01G07_FPS AT%I145.3 :BOOL; (*空调机组NJ-1AP(KT)7-7-风机压差*)"},"LAHU01G07_FPS           AT%I145.3      :BOOL; (*空调机组NJ-1AP(KT)7-7-风机压差*)",null,"L17\\L17AHU01G07_FPS","空调机组NJ-1AP(KT)7-7-风机压差",11163]
[{"$nulls":5},13,null,25,26,"空调机组NJ-1AP(KT)7-8-运行状态",{"$nulls":16},"NJ-1AP(KT)7-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-8","01G08","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"AHU01G08_R"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B26*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LAHU01G08_R AT%I145.4 :BOOL; (*空调机组NJ-1AP(KT)7-8-运行状态*)"},"LAHU01G08_R             AT%I145.4      :BOOL; (*空调机组NJ-1AP(KT)7-8-运行状态*)",null,"L17\\L17AHU01G08_R","空调机组NJ-1AP(KT)7-8-运行状态",11164]
[{"$nulls":5},14,null,27,28,"空调机组NJ-1AP(KT)7-8-故障状态",{"$nulls":16},"NJ-1AP(KT)7-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-8","01G08","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"AHU01G08_F"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B26*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LAHU01G08_F AT%I145.5 :BOOL; (*空调机组NJ-1AP(KT)7-8-故障状态*)"},"LAHU01G08_F             AT%I145.5      :BOOL; (*空调机组NJ-1AP(KT)7-8-故障状态*)",null,"L17\\L17AHU01G08_F","空调机组NJ-1AP(KT)7-8-故障状态",11165]
[{"$nulls":5},15,null,29,30,"空调机组NJ-1AP(KT)7-8-自动状态",{"$nulls":16},"NJ-1AP(KT)7-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-8","01G08","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"AHU01G08_A"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B26*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LAHU01G08_A AT%I145.6 :BOOL; (*空调机组NJ-1AP(KT)7-8-自动状态*)"},"LAHU01G08_A             AT%I145.6      :BOOL; (*空调机组NJ-1AP(KT)7-8-自动状态*)",null,"L17\\L17AHU01G08_A","空调机组NJ-1AP(KT)7-8-自动状态",11166]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-1AP(KT)7-8-风机压差",{"$nulls":16},"NJ-1AP(KT)7-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-8","01G08","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"AHU01G08_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B26*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LAHU01G08_FPS AT%I145.7 :BOOL; (*空调机组NJ-1AP(KT)7-8-风机压差*)"},"LAHU01G08_FPS           AT%I145.7      :BOOL; (*空调机组NJ-1AP(KT)7-8-风机压差*)",null,"L17\\L17AHU01G08_FPS","空调机组NJ-1AP(KT)7-8-风机压差",11167]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B46&\"地址: \"&B43&\" *)\"","v":"(* IOM 1601R地址: 10 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH42&AA42&\"-\"&AK42","v":"空调机组NJ-1AP(KT)7-9-运行状态"},{"$nulls":16},{"$f":"IF(AI42=\"\",\"\",AI42)","v":"NJ-1AP(KT)7-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-9","01G09","运行状态",{"$f":"AH42&\"-\"&AK42","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":"AHU01G09_R"},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%I\"&B43*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":"LAHU01G09_R AT%I160.0 :BOOL; (*空调机组NJ-1AP(KT)7-9-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42))),SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))))),\" \")","v":"LAHU01G09_R             AT%I160.0      :BOOL; (*空调机组NJ-1AP(KT)7-9-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM42","v":"L17\\L17AHU01G09_R"},{"$f":"J42","v":"空调机组NJ-1AP(KT)7-9-运行状态"},{"$f":"10000+($B43*16*8+F42-1)","v":11280}]
[null,10,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},2,null,3,4,"空调机组NJ-1AP(KT)7-9-故障状态",{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-1AP(KT)7-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-9","01G09","故障状态",{"$f":"AH43&\"-\"&AK43","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"AHU01G09_F"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B43*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LAHU01G09_F AT%I160.1 :BOOL; (*空调机组NJ-1AP(KT)7-9-故障状态*)"},"LAHU01G09_F             AT%I160.1      :BOOL; (*空调机组NJ-1AP(KT)7-9-故障状态*)",null,"L17\\L17AHU01G09_F",{"$f":"J43","v":"空调机组NJ-1AP(KT)7-9-故障状态"},{"$f":"AS42+1","v":11281}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-1AP(KT)7-9-自动状态",{"$nulls":16},"NJ-1AP(KT)7-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-9","01G09","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"AHU01G09_A"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B43*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LAHU01G09_A AT%I160.2 :BOOL; (*空调机组NJ-1AP(KT)7-9-自动状态*)"},"LAHU01G09_A             AT%I160.2      :BOOL; (*空调机组NJ-1AP(KT)7-9-自动状态*)",null,"L17\\L17AHU01G09_A","空调机组NJ-1AP(KT)7-9-自动状态",{"$f":"AS43+1","v":11282}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-1AP(KT)7-9-风机压差",{"$nulls":16},"NJ-1AP(KT)7-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-9","01G09","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"AHU01G09_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B43*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LAHU01G09_FPS AT%I160.3 :BOOL; (*空调机组NJ-1AP(KT)7-9-风机压差*)"},"LAHU01G09_FPS           AT%I160.3      :BOOL; (*空调机组NJ-1AP(KT)7-9-风机压差*)",null,"L17\\L17AHU01G09_FPS","空调机组NJ-1AP(KT)7-9-风机压差",11283]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-1AP(KT)7-10-运行状态",{"$nulls":16},"NJ-1AP(KT)7-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-10","01G10","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"AHU01G10_R"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B43*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LAHU01G10_R AT%I160.4 :BOOL; (*空调机组NJ-1AP(KT)7-10-运行状态*)"},"LAHU01G10_R             AT%I160.4      :BOOL; (*空调机组NJ-1AP(KT)7-10-运行状态*)",null,"L17\\L17AHU01G10_R","空调机组NJ-1AP(KT)7-10-运行状态",11284]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-1AP(KT)7-10-故障状态",{"$nulls":16},"NJ-1AP(KT)7-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-10","01G10","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"AHU01G10_F"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B43*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LAHU01G10_F AT%I160.5 :BOOL; (*空调机组NJ-1AP(KT)7-10-故障状态*)"},"LAHU01G10_F             AT%I160.5      :BOOL; (*空调机组NJ-1AP(KT)7-10-故障状态*)",null,"L17\\L17AHU01G10_F","空调机组NJ-1AP(KT)7-10-故障状态",11285]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-1AP(KT)7-10-自动状态",{"$nulls":16},"NJ-1AP(KT)7-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-10","01G10","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"AHU01G10_A"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B43*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LAHU01G10_A AT%I160.6 :BOOL; (*空调机组NJ-1AP(KT)7-10-自动状态*)"},"LAHU01G10_A             AT%I160.6      :BOOL; (*空调机组NJ-1AP(KT)7-10-自动状态*)",null,"L17\\L17AHU01G10_A","空调机组NJ-1AP(KT)7-10-自动状态",11286]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-1AP(KT)7-10-风机压差",{"$nulls":16},"NJ-1AP(KT)7-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-10","01G10","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"AHU01G10_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B43*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LAHU01G10_FPS AT%I160.7 :BOOL; (*空调机组NJ-1AP(KT)7-10-风机压差*)"},"LAHU01G10_FPS           AT%I160.7      :BOOL; (*空调机组NJ-1AP(KT)7-10-风机压差*)",null,"L17\\L17AHU01G10_FPS","空调机组NJ-1AP(KT)7-10-风机压差",11287]
[{"$nulls":5},9,null,17,18,"空调机组NJ-1AP(KT)7-11-运行状态",{"$nulls":16},"NJ-1AP(KT)7-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-11","01G11","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"AHU01G11_R"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B43*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LAHU01G11_R AT%I161.0 :BOOL; (*空调机组NJ-1AP(KT)7-11-运行状态*)"},"LAHU01G11_R             AT%I161.0      :BOOL; (*空调机组NJ-1AP(KT)7-11-运行状态*)",null,"L17\\L17AHU01G11_R","空调机组NJ-1AP(KT)7-11-运行状态",11288]
[{"$nulls":5},10,null,19,20,"空调机组NJ-1AP(KT)7-11-故障状态",{"$nulls":16},{"$f":"IF(AI51=\"\",\"\",AI51)","v":"NJ-1AP(KT)7-11"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-11","01G11","故障状态",{"$f":"AH51&\"-\"&AK51","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"AHU01G11_F"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B43*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LAHU01G11_F AT%I161.1 :BOOL; (*空调机组NJ-1AP(KT)7-11-故障状态*)"},"LAHU01G11_F             AT%I161.1      :BOOL; (*空调机组NJ-1AP(KT)7-11-故障状态*)",null,"L17\\L17AHU01G11_F",{"$f":"J51","v":"空调机组NJ-1AP(KT)7-11-故障状态"},11289]
[{"$nulls":5},11,null,21,22,"空调机组NJ-1AP(KT)7-11-自动状态",{"$nulls":16},"NJ-1AP(KT)7-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-11","01G11","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"AHU01G11_A"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%I\"&B43*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LAHU01G11_A AT%I161.2 :BOOL; (*空调机组NJ-1AP(KT)7-11-自动状态*)"},"LAHU01G11_A             AT%I161.2      :BOOL; (*空调机组NJ-1AP(KT)7-11-自动状态*)",null,"L17\\L17AHU01G11_A","空调机组NJ-1AP(KT)7-11-自动状态",11290]
[{"$nulls":5},12,null,23,24,"空调机组NJ-1AP(KT)7-11-风机压差",{"$nulls":16},"NJ-1AP(KT)7-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-11","01G11","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"AHU01G11_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%I\"&B43*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LAHU01G11_FPS AT%I161.3 :BOOL; (*空调机组NJ-1AP(KT)7-11-风机压差*)"},"LAHU01G11_FPS           AT%I161.3      :BOOL; (*空调机组NJ-1AP(KT)7-11-风机压差*)",null,"L17\\L17AHU01G11_FPS","空调机组NJ-1AP(KT)7-11-风机压差",11291]
[{"$nulls":5},13,null,25,26,"空调机组NJ-1AP(KT)7-12-运行状态",{"$nulls":16},"NJ-1AP(KT)7-12",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-12","01G12","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"AHU01G12_R"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%I\"&B43*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LAHU01G12_R AT%I161.4 :BOOL; (*空调机组NJ-1AP(KT)7-12-运行状态*)"},"LAHU01G12_R             AT%I161.4      :BOOL; (*空调机组NJ-1AP(KT)7-12-运行状态*)",null,"L17\\L17AHU01G12_R","空调机组NJ-1AP(KT)7-12-运行状态",11292]
[{"$nulls":5},14,null,27,28,"空调机组NJ-1AP(KT)7-12-故障状态",{"$nulls":16},"NJ-1AP(KT)7-12",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-12","01G12","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"AHU01G12_F"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%I\"&B43*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LAHU01G12_F AT%I161.5 :BOOL; (*空调机组NJ-1AP(KT)7-12-故障状态*)"},"LAHU01G12_F             AT%I161.5      :BOOL; (*空调机组NJ-1AP(KT)7-12-故障状态*)",null,"L17\\L17AHU01G12_F","空调机组NJ-1AP(KT)7-12-故障状态",11293]
[{"$nulls":5},15,null,29,30,"空调机组NJ-1AP(KT)7-12-自动状态",{"$nulls":16},"NJ-1AP(KT)7-12",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-12","01G12","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"AHU01G12_A"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%I\"&B43*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LAHU01G12_A AT%I161.6 :BOOL; (*空调机组NJ-1AP(KT)7-12-自动状态*)"},"LAHU01G12_A             AT%I161.6      :BOOL; (*空调机组NJ-1AP(KT)7-12-自动状态*)",null,"L17\\L17AHU01G12_A","空调机组NJ-1AP(KT)7-12-自动状态",11294]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-1AP(KT)7-12-风机压差",{"$nulls":16},"NJ-1AP(KT)7-12",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-12","01G12","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"AHU01G12_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%I\"&B43*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LAHU01G12_FPS AT%I161.7 :BOOL; (*空调机组NJ-1AP(KT)7-12-风机压差*)"},"LAHU01G12_FPS           AT%I161.7      :BOOL; (*空调机组NJ-1AP(KT)7-12-风机压差*)",null,"L17\\L17AHU01G12_FPS","空调机组NJ-1AP(KT)7-12-风机压差",11295]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B63&\"地址: \"&B60&\" *)\"","v":"(* IOM 0801R 地址: 11 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":1},1,null,1,"C",{"$f":"AH59&AA59&\"-\"&AK59","v":"照明控制箱NJ-1AL7-1-运行状态"},{"$nulls":16},{"$f":"IF(AI59=\"\",\"\",AI59)","v":"NJ-1AL7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL7-1","01G01","运行状态",{"$f":"AH59&\"-\"&AK59","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH59,List!$B$3:$D$445,2,FALSE)&AJ59&\"_\"&VLOOKUP(AK59,List!$K$2:$M$447,2,FALSE)","v":"LCB01G01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM59&\" \"&\"AT%I\"&B60*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J59&\"*)\",\" \")","v":"LLCB01G01_R AT%I176.0 :BOOL; (*照明控制箱NJ-1AL7-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59))),SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))))),\" \")","v":"LLCB01G01_R             AT%I176.0      :BOOL; (*照明控制箱NJ-1AL7-1-运行状态*)"},null,{"$f":"AM59","v":"LCB01G01_R"},{"$f":"J59","v":"照明控制箱NJ-1AL7-1-运行状态"},{"$f":"10000+($B60*16*8+F59-1)","v":11408}]
[null,11,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":1},2,null,2,"C",{"$f":"AH60&AA60&\"-\"&AK60","v":"照明控制箱NJ-1AL7-1-自动状态"},{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-1AL7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL7-1","01G01","自动状态",{"$f":"AH60&\"-\"&AK60","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"LCB01G01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%I\"&B60*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LLCB01G01_A AT%I176.1 :BOOL; (*照明控制箱NJ-1AL7-1-自动状态*)"},"LLCB01G01_A             AT%I176.1      :BOOL; (*照明控制箱NJ-1AL7-1-自动状态*)",null,{"$f":"AM60","v":"LCB01G01_A"},{"$f":"J60","v":"照明控制箱NJ-1AL7-1-自动状态"},{"$f":"AS59+1","v":11409}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":0},3,null,3,"C",{"$f":"AH61&AA61&\"-\"&AK61","v":"照明控制箱NJ-1AL7-2-运行状态"},{"$nulls":16},"NJ-1AL7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL7-2","01G02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"LCB01G02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%I\"&B60*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LLCB01G02_R AT%I176.2 :BOOL; (*照明控制箱NJ-1AL7-2-运行状态*)"},"LLCB01G02_R             AT%I176.2      :BOOL; (*照明控制箱NJ-1AL7-2-运行状态*)",null,"LCB01G02_R","照明控制箱NJ-1AL7-2-运行状态",{"$f":"AS60+1","v":11410}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},4,null,4,"C",{"$f":"AH62&AA62&\"-\"&AK62","v":"照明控制箱NJ-1AL7-2-自动状态"},{"$nulls":16},"NJ-1AL7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-1AL7-2","01G02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"LCB01G02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B60*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LLCB01G02_A AT%I176.3 :BOOL; (*照明控制箱NJ-1AL7-2-自动状态*)"},"LLCB01G02_A             AT%I176.3      :BOOL; (*照明控制箱NJ-1AL7-2-自动状态*)",null,"LCB01G02_A","照明控制箱NJ-1AL7-2-自动状态",11411]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},5,null,5,"C","照明控制箱NJ-1AL7-3-运行状态",{"$nulls":16},"NJ-1AL7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL7-3","01G03","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"LCB01G03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B60*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LLCB01G03_R AT%I176.4 :BOOL; (*照明控制箱NJ-1AL7-3-运行状态*)"},"LLCB01G03_R             AT%I176.4      :BOOL; (*照明控制箱NJ-1AL7-3-运行状态*)",null,"LCB01G03_R","照明控制箱NJ-1AL7-3-运行状态",11412]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","照明控制箱NJ-1AL7-3-自动状态",{"$nulls":16},"NJ-1AL7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL7-3","01G03","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"LCB01G03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B60*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LLCB01G03_A AT%I176.5 :BOOL; (*照明控制箱NJ-1AL7-3-自动状态*)"},"LLCB01G03_A             AT%I176.5      :BOOL; (*照明控制箱NJ-1AL7-3-自动状态*)",null,"LCB01G03_A","照明控制箱NJ-1AL7-3-自动状态",11413]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","照明控制箱NJ-1AL7-4-运行状态",{"$nulls":16},"NJ-1AL7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL7-4","01G04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":"LCB01G04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B60*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":"LLCB01G04_R AT%I176.6 :BOOL; (*照明控制箱NJ-1AL7-4-运行状态*)"},"LLCB01G04_R             AT%I176.6      :BOOL; (*照明控制箱NJ-1AL7-4-运行状态*)",null,"LCB01G04_R","照明控制箱NJ-1AL7-4-运行状态",11414]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","照明控制箱NJ-1AL7-4-自动状态",{"$nulls":16},"NJ-1AL7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL7-4","01G04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":"LCB01G04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B60*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":"LLCB01G04_A AT%I176.7 :BOOL; (*照明控制箱NJ-1AL7-4-自动状态*)"},"LLCB01G04_A             AT%I176.7      :BOOL; (*照明控制箱NJ-1AL7-4-自动状态*)",null,"LCB01G04_A","照明控制箱NJ-1AL7-4-自动状态",11415]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B72&\"地址: \"&B69&\" *)\"","v":"(* IOM 1601D地址: 12 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH68&AA68&\"-\"&AK68","v":"空调机组NJ-1AP(KT)7-1-启停控制"},{"$nulls":16},{"$f":"IF(AI68=\"\",\"\",AI68)","v":"NJ-1AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-1","01G01","启停控制",{"$f":"AH68&\"-\"&AK68","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"AHU01G01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%Q\"&B69*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LAHU01G01_C AT%Q192.0 :BOOL; (*空调机组NJ-1AP(KT)7-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68))),SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))))),\" \")","v":"LAHU01G01_C             AT%Q192.0      :BOOL; (*空调机组NJ-1AP(KT)7-1-启停控制*)"},null,{"$f":"AM68","v":"AHU01G01_C"},{"$f":"J68","v":"空调机组NJ-1AP(KT)7-1-启停控制"},{"$f":"($B69*16*8+F68-1)","v":1536}]
[null,12,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","空调机组NJ-1AP(KT)7-2-启停控制",{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-1AP(KT)7-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-2","01G02","启停控制",{"$f":"AH69&\"-\"&AK69","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU01G02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%Q\"&B69*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU01G02_C AT%Q192.1 :BOOL; (*空调机组NJ-1AP(KT)7-2-启停控制*)"},"LAHU01G02_C             AT%Q192.1      :BOOL; (*空调机组NJ-1AP(KT)7-2-启停控制*)",null,"AHU01G02_C",{"$f":"J69","v":"空调机组NJ-1AP(KT)7-2-启停控制"},{"$f":"AS68+1","v":1537}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-1AP(KT)7-3-启停控制",{"$nulls":16},"NJ-1AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-3","01G03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"AHU01G03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%Q\"&B69*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LAHU01G03_C AT%Q192.2 :BOOL; (*空调机组NJ-1AP(KT)7-3-启停控制*)"},"LAHU01G03_C             AT%Q192.2      :BOOL; (*空调机组NJ-1AP(KT)7-3-启停控制*)",null,"AHU01G03_C","空调机组NJ-1AP(KT)7-3-启停控制",{"$f":"AS69+1","v":1538}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","空调机组NJ-1AP(KT)7-4-启停控制",{"$nulls":16},"NJ-1AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-4","01G04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"AHU01G04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%Q\"&B69*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LAHU01G04_C AT%Q192.3 :BOOL; (*空调机组NJ-1AP(KT)7-4-启停控制*)"},"LAHU01G04_C             AT%Q192.3      :BOOL; (*空调机组NJ-1AP(KT)7-4-启停控制*)",null,"AHU01G04_C","空调机组NJ-1AP(KT)7-4-启停控制",1539]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-1AP(KT)7-5-启停控制",{"$nulls":16},"NJ-1AP(KT)7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-5","01G05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"AHU01G05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%Q\"&B69*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LAHU01G05_C AT%Q192.4 :BOOL; (*空调机组NJ-1AP(KT)7-5-启停控制*)"},"LAHU01G05_C             AT%Q192.4      :BOOL; (*空调机组NJ-1AP(KT)7-5-启停控制*)",null,"AHU01G05_C","空调机组NJ-1AP(KT)7-5-启停控制",1540]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-1AP(KT)7-6-启停控制",{"$nulls":16},"NJ-1AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-6","01G06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"AHU01G06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%Q\"&B69*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LAHU01G06_C AT%Q192.5 :BOOL; (*空调机组NJ-1AP(KT)7-6-启停控制*)"},"LAHU01G06_C             AT%Q192.5      :BOOL; (*空调机组NJ-1AP(KT)7-6-启停控制*)",null,"AHU01G06_C","空调机组NJ-1AP(KT)7-6-启停控制",1541]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","空调机组NJ-1AP(KT)7-7-启停控制",{"$nulls":16},"NJ-1AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-7","01G07","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":"AHU01G07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%Q\"&B69*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":"LAHU01G07_C AT%Q192.6 :BOOL; (*空调机组NJ-1AP(KT)7-7-启停控制*)"},"LAHU01G07_C             AT%Q192.6      :BOOL; (*空调机组NJ-1AP(KT)7-7-启停控制*)",null,"AHU01G07_C","空调机组NJ-1AP(KT)7-7-启停控制",1542]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","空调机组NJ-1AP(KT)7-8-启停控制",{"$nulls":16},"NJ-1AP(KT)7-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-8","01G08","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":"AHU01G08_C"},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%Q\"&B69*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":"LAHU01G08_C AT%Q192.7 :BOOL; (*空调机组NJ-1AP(KT)7-8-启停控制*)"},"LAHU01G08_C             AT%Q192.7      :BOOL; (*空调机组NJ-1AP(KT)7-8-启停控制*)",null,"AHU01G08_C","空调机组NJ-1AP(KT)7-8-启停控制",1543]
[{"$nulls":5},9,null,"9+","9-","空调机组NJ-1AP(KT)7-9-启停控制",{"$nulls":16},"NJ-1AP(KT)7-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-9","01G09","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH76,List!$B$3:$D$445,2,FALSE)&AJ76&\"_\"&VLOOKUP(AK76,List!$K$2:$M$447,2,FALSE)","v":"AHU01G09_C"},{"$f":"_xlfn.IFNA(\"L\"&AM76&\" \"&\"AT%Q\"&B69*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J76&\"*)\",\" \")","v":"LAHU01G09_C AT%Q193.0 :BOOL; (*空调机组NJ-1AP(KT)7-9-启停控制*)"},"LAHU01G09_C             AT%Q193.0      :BOOL; (*空调机组NJ-1AP(KT)7-9-启停控制*)",null,"AHU01G09_C","空调机组NJ-1AP(KT)7-9-启停控制",1544]
[{"$nulls":5},10,null,"10+","10-","空调机组NJ-1AP(KT)7-10-启停控制",{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-1AP(KT)7-10"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-10","01G10","启停控制",{"$f":"AH77&\"-\"&AK77","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"AHU01G10_C"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%Q\"&B69*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LAHU01G10_C AT%Q193.1 :BOOL; (*空调机组NJ-1AP(KT)7-10-启停控制*)"},"LAHU01G10_C             AT%Q193.1      :BOOL; (*空调机组NJ-1AP(KT)7-10-启停控制*)",null,"AHU01G10_C",{"$f":"J77","v":"空调机组NJ-1AP(KT)7-10-启停控制"},1545]
[{"$nulls":5},11,null,"11+","11-","空调机组NJ-1AP(KT)7-11-启停控制",{"$nulls":16},"NJ-1AP(KT)7-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-11","01G11","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU01G11_C"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B69*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU01G11_C AT%Q193.2 :BOOL; (*空调机组NJ-1AP(KT)7-11-启停控制*)"},"LAHU01G11_C             AT%Q193.2      :BOOL; (*空调机组NJ-1AP(KT)7-11-启停控制*)",null,"AHU01G11_C","空调机组NJ-1AP(KT)7-11-启停控制",1546]
[{"$nulls":5},12,null,"12+","12-","空调机组NJ-1AP(KT)7-12-启停控制",{"$nulls":16},"NJ-1AP(KT)7-12",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-12","01G12","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU01G12_C"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B69*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU01G12_C AT%Q193.3 :BOOL; (*空调机组NJ-1AP(KT)7-12-启停控制*)"},"LAHU01G12_C             AT%Q193.3      :BOOL; (*空调机组NJ-1AP(KT)7-12-启停控制*)",null,"AHU01G12_C","空调机组NJ-1AP(KT)7-12-启停控制",1547]
[{"$nulls":5},13,null,"13+","13-","照明控制箱NJ-1AL7-1-启停控制",{"$nulls":16},"NJ-1AL7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL7-1","01G01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"LCB01G01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B69*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LLCB01G01_C AT%Q193.4 :BOOL; (*照明控制箱NJ-1AL7-1-启停控制*)"},"LLCB01G01_C             AT%Q193.4      :BOOL; (*照明控制箱NJ-1AL7-1-启停控制*)",null,"LCB01G01_C","照明控制箱NJ-1AL7-1-启停控制",1548]
[{"$nulls":5},14,null,"14+","14-","照明控制箱NJ-1AL7-2-启停控制",{"$nulls":16},"NJ-1AL7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL7-2","01G02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"LCB01G02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%Q\"&B69*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LLCB01G02_C AT%Q193.5 :BOOL; (*照明控制箱NJ-1AL7-2-启停控制*)"},"LLCB01G02_C             AT%Q193.5      :BOOL; (*照明控制箱NJ-1AL7-2-启停控制*)",null,"LCB01G02_C","照明控制箱NJ-1AL7-2-启停控制",1549]
[{"$nulls":5},15,null,"15+","15-","照明控制箱NJ-1AL7-3-启停控制",{"$nulls":16},"NJ-1AL7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL7-3","01G03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":"LCB01G03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%Q\"&B69*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":"LLCB01G03_C AT%Q193.6 :BOOL; (*照明控制箱NJ-1AL7-3-启停控制*)"},"LLCB01G03_C             AT%Q193.6      :BOOL; (*照明控制箱NJ-1AL7-3-启停控制*)",null,"LCB01G03_C","照明控制箱NJ-1AL7-3-启停控制",1550]
[".",{"$nulls":4},16,null,"16+","16-","照明控制箱NJ-1AL7-4-启停控制",{"$nulls":16},"NJ-1AL7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL7-4","01G04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":"LCB01G04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%Q\"&B69*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":"LLCB01G04_C AT%Q193.7 :BOOL; (*照明控制箱NJ-1AL7-4-启停控制*)"},"LLCB01G04_C             AT%Q193.7      :BOOL; (*照明控制箱NJ-1AL7-4-启停控制*)",null,"LCB01G04_C","照明控制箱NJ-1AL7-4-启停控制",1551]
[null,{"$f":"B89","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B89&\"地址: \"&B86&\" *)\"","v":"(* IOM 0801U地址: 13 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH85&AA85&\"-\"&AK85","v":"空调机组NJ-1AP(KT)7-1-回风温度"},{"$nulls":16},{"$f":"IF(AI85=\"\",\"\",AI85)","v":"NJ-1AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-1","01G01","回风温度",{"$f":"AH85&\"-\"&AK85","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH85,List!$B$3:$D$445,2,FALSE)&AJ85&\"_\"&VLOOKUP(AK85,List!$K$2:$M$447,2,FALSE)","v":"AHU01G01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM85&\" \"&\"AT%I\"&B86*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J85&\"*)\",\" \")","v":"LAHU01G01_RT AT%I208.0 :INT ; (*空调机组NJ-1AP(KT)7-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN85,SEARCH(\"AT%\",AN85),,REPT(\" \",25-SEARCH(\"AT%\",AN85))),SEARCH(\":\",REPLACE(AN85,SEARCH(\"AT%\",AN85),,REPT(\" \",25-SEARCH(\"AT%\",AN85)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN85,SEARCH(\"AT%\",AN85),,REPT(\" \",25-SEARCH(\"AT%\",AN85)))))),\" \")","v":"LAHU01G01_RT            AT%I208.0      :INT ; (*空调机组NJ-1AP(KT)7-1-回风温度*)"},null,{"$f":"AM85","v":"AHU01G01_RT"},{"$f":"J85","v":"空调机组NJ-1AP(KT)7-1-回风温度"},{"$f":"30000+($B86*8+F85-1)","v":30104}]
[null,13,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-1AP(KT)7-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-1AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-1","01G01","水阀反馈",{"$f":"AH86&\"-\"&AK86","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"AHU01G01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%I\"&B86*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LAHU01G01_WVB AT%I210.0 :INT ; (*空调机组NJ-1AP(KT)7-1-水阀反馈*)"},"LAHU01G01_WVB           AT%I210.0      :INT ; (*空调机组NJ-1AP(KT)7-1-水阀反馈*)",null,"AHU01G01_WVB",{"$f":"J86","v":"空调机组NJ-1AP(KT)7-1-水阀反馈"},{"$f":"AS85+1","v":30105}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-1AP(KT)7-2-回风温度",{"$nulls":16},"NJ-1AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-2","01G02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"AHU01G02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%I\"&B86*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LAHU01G02_RT AT%I212.0 :INT ; (*空调机组NJ-1AP(KT)7-2-回风温度*)"},"LAHU01G02_RT            AT%I212.0      :INT ; (*空调机组NJ-1AP(KT)7-2-回风温度*)",null,"AHU01G02_RT","空调机组NJ-1AP(KT)7-2-回风温度",{"$f":"AS86+1","v":30106}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-1AP(KT)7-2-水阀反馈",{"$nulls":16},"NJ-1AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-2","01G02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"AHU01G02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%I\"&B86*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LAHU01G02_WVB AT%I214.0 :INT ; (*空调机组NJ-1AP(KT)7-2-水阀反馈*)"},"LAHU01G02_WVB           AT%I214.0      :INT ; (*空调机组NJ-1AP(KT)7-2-水阀反馈*)",null,"AHU01G02_WVB","空调机组NJ-1AP(KT)7-2-水阀反馈",30107]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-1AP(KT)7-3-回风温度",{"$nulls":16},"NJ-1AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-3","01G03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"AHU01G03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%I\"&B86*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LAHU01G03_RT AT%I216.0 :INT ; (*空调机组NJ-1AP(KT)7-3-回风温度*)"},"LAHU01G03_RT            AT%I216.0      :INT ; (*空调机组NJ-1AP(KT)7-3-回风温度*)",null,"AHU01G03_RT","空调机组NJ-1AP(KT)7-3-回风温度",30108]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-1AP(KT)7-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI90=\"\",\"\",AI90)","v":"NJ-1AP(KT)7-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-3","01G03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":"AHU01G03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%I\"&B86*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":"LAHU01G03_WVB AT%I218.0 :INT ; (*空调机组NJ-1AP(KT)7-3-水阀反馈*)"},"LAHU01G03_WVB           AT%I218.0      :INT ; (*空调机组NJ-1AP(KT)7-3-水阀反馈*)",null,"AHU01G03_WVB",{"$f":"J90","v":"空调机组NJ-1AP(KT)7-3-水阀反馈"},30109]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-1AP(KT)7-4-回风温度",{"$nulls":16},"NJ-1AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-4","01G04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH91,List!$B$3:$D$445,2,FALSE)&AJ91&\"_\"&VLOOKUP(AK91,List!$K$2:$M$447,2,FALSE)","v":"AHU01G04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM91&\" \"&\"AT%I\"&B86*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J91&\"*)\",\" \")","v":"LAHU01G04_RT AT%I220.0 :INT ; (*空调机组NJ-1AP(KT)7-4-回风温度*)"},"LAHU01G04_RT            AT%I220.0      :INT ; (*空调机组NJ-1AP(KT)7-4-回风温度*)",null,"AHU01G04_RT","空调机组NJ-1AP(KT)7-4-回风温度",30110]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-1AP(KT)7-4-水阀反馈",{"$nulls":16},"NJ-1AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-4","01G04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH92,List!$B$3:$D$445,2,FALSE)&AJ92&\"_\"&VLOOKUP(AK92,List!$K$2:$M$447,2,FALSE)","v":"AHU01G04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM92&\" \"&\"AT%I\"&B86*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J92&\"*)\",\" \")","v":"LAHU01G04_WVB AT%I222.0 :INT ; (*空调机组NJ-1AP(KT)7-4-水阀反馈*)"},"LAHU01G04_WVB           AT%I222.0      :INT ; (*空调机组NJ-1AP(KT)7-4-水阀反馈*)",null,"AHU01G04_WVB","空调机组NJ-1AP(KT)7-4-水阀反馈",30111]
[null,{"$f":"B98","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B98&\"地址: \"&B95&\" *)\"","v":"(* IOM 0801U地址: 14 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH94&AA94&\"-\"&AK94","v":"空调机组NJ-1AP(KT)7-5-回风温度"},{"$nulls":16},{"$f":"IF(AI94=\"\",\"\",AI94)","v":"NJ-1AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-5","01G05","回风温度",{"$f":"AH94&\"-\"&AK94","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH94,List!$B$3:$D$445,2,FALSE)&AJ94&\"_\"&VLOOKUP(AK94,List!$K$2:$M$447,2,FALSE)","v":"AHU01G05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM94&\" \"&\"AT%I\"&B95*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J94&\"*)\",\" \")","v":"LAHU01G05_RT AT%I224.0 :INT ; (*空调机组NJ-1AP(KT)7-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94))),SEARCH(\":\",REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94)))))),\" \")","v":"LAHU01G05_RT            AT%I224.0      :INT ; (*空调机组NJ-1AP(KT)7-5-回风温度*)"},null,{"$f":"AM94","v":"AHU01G05_RT"},{"$f":"J94","v":"空调机组NJ-1AP(KT)7-5-回风温度"},{"$f":"30000+($B95*8+F94-1)","v":30112}]
[null,14,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-1AP(KT)7-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-1AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-5","01G05","水阀反馈",{"$f":"AH95&\"-\"&AK95","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"AHU01G05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%I\"&B95*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LAHU01G05_WVB AT%I226.0 :INT ; (*空调机组NJ-1AP(KT)7-5-水阀反馈*)"},"LAHU01G05_WVB           AT%I226.0      :INT ; (*空调机组NJ-1AP(KT)7-5-水阀反馈*)",null,"AHU01G05_WVB",{"$f":"J95","v":"空调机组NJ-1AP(KT)7-5-水阀反馈"},{"$f":"AS94+1","v":30113}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-1AP(KT)7-6-回风温度",{"$nulls":16},"NJ-1AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-6","01G06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"AHU01G06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%I\"&B95*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LAHU01G06_RT AT%I228.0 :INT ; (*空调机组NJ-1AP(KT)7-6-回风温度*)"},"LAHU01G06_RT            AT%I228.0      :INT ; (*空调机组NJ-1AP(KT)7-6-回风温度*)",null,"AHU01G06_RT","空调机组NJ-1AP(KT)7-6-回风温度",{"$f":"AS95+1","v":30114}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-1AP(KT)7-6-水阀反馈",{"$nulls":16},"NJ-1AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-6","01G06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":"AHU01G06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%I\"&B95*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":"LAHU01G06_WVB AT%I230.0 :INT ; (*空调机组NJ-1AP(KT)7-6-水阀反馈*)"},"LAHU01G06_WVB           AT%I230.0      :INT ; (*空调机组NJ-1AP(KT)7-6-水阀反馈*)",null,"AHU01G06_WVB","空调机组NJ-1AP(KT)7-6-水阀反馈",30115]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-1AP(KT)7-7-回风温度",{"$nulls":16},"NJ-1AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-7","01G07","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":"AHU01G07_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%I\"&B95*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":"LAHU01G07_RT AT%I232.0 :INT ; (*空调机组NJ-1AP(KT)7-7-回风温度*)"},"LAHU01G07_RT            AT%I232.0      :INT ; (*空调机组NJ-1AP(KT)7-7-回风温度*)",null,"AHU01G07_RT","空调机组NJ-1AP(KT)7-7-回风温度",30116]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-1AP(KT)7-7-水阀反馈",{"$nulls":16},{"$f":"IF(AI99=\"\",\"\",AI99)","v":"NJ-1AP(KT)7-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-7","01G07","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH99,List!$B$3:$D$445,2,FALSE)&AJ99&\"_\"&VLOOKUP(AK99,List!$K$2:$M$447,2,FALSE)","v":"AHU01G07_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM99&\" \"&\"AT%I\"&B95*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J99&\"*)\",\" \")","v":"LAHU01G07_WVB AT%I234.0 :INT ; (*空调机组NJ-1AP(KT)7-7-水阀反馈*)"},"LAHU01G07_WVB           AT%I234.0      :INT ; (*空调机组NJ-1AP(KT)7-7-水阀反馈*)",null,"AHU01G07_WVB",{"$f":"J99","v":"空调机组NJ-1AP(KT)7-7-水阀反馈"},30117]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-1AP(KT)7-8-回风温度",{"$nulls":16},"NJ-1AP(KT)7-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-8","01G08","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH100,List!$B$3:$D$445,2,FALSE)&AJ100&\"_\"&VLOOKUP(AK100,List!$K$2:$M$447,2,FALSE)","v":"AHU01G08_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM100&\" \"&\"AT%I\"&B95*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J100&\"*)\",\" \")","v":"LAHU01G08_RT AT%I236.0 :INT ; (*空调机组NJ-1AP(KT)7-8-回风温度*)"},"LAHU01G08_RT            AT%I236.0      :INT ; (*空调机组NJ-1AP(KT)7-8-回风温度*)",null,"AHU01G08_RT","空调机组NJ-1AP(KT)7-8-回风温度",30118]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-1AP(KT)7-8-水阀反馈",{"$nulls":16},"NJ-1AP(KT)7-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-8","01G08","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH101,List!$B$3:$D$445,2,FALSE)&AJ101&\"_\"&VLOOKUP(AK101,List!$K$2:$M$447,2,FALSE)","v":"AHU01G08_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM101&\" \"&\"AT%I\"&B95*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J101&\"*)\",\" \")","v":"LAHU01G08_WVB AT%I238.0 :INT ; (*空调机组NJ-1AP(KT)7-8-水阀反馈*)"},"LAHU01G08_WVB           AT%I238.0      :INT ; (*空调机组NJ-1AP(KT)7-8-水阀反馈*)",null,"AHU01G08_WVB","空调机组NJ-1AP(KT)7-8-水阀反馈",30119]
[null,{"$f":"B107","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B107&\"地址: \"&B104&\" *)\"","v":"(* IOM 0801U地址: 15 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH103&AA103&\"-\"&AK103","v":"空调机组NJ-1AP(KT)7-9-回风温度"},{"$nulls":16},{"$f":"IF(AI103=\"\",\"\",AI103)","v":"NJ-1AP(KT)7-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-9","01G09","回风温度",{"$f":"AH103&\"-\"&AK103","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH103,List!$B$3:$D$445,2,FALSE)&AJ103&\"_\"&VLOOKUP(AK103,List!$K$2:$M$447,2,FALSE)","v":"AHU01G09_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM103&\" \"&\"AT%I\"&B104*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J103&\"*)\",\" \")","v":"LAHU01G09_RT AT%I240.0 :INT ; (*空调机组NJ-1AP(KT)7-9-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103))),SEARCH(\":\",REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103)))))),\" \")","v":"LAHU01G09_RT            AT%I240.0      :INT ; (*空调机组NJ-1AP(KT)7-9-回风温度*)"},null,{"$f":"AM103","v":"AHU01G09_RT"},{"$f":"J103","v":"空调机组NJ-1AP(KT)7-9-回风温度"},{"$f":"30000+($B104*8+F103-1)","v":30120}]
[null,15,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-1AP(KT)7-9-水阀反馈",{"$nulls":16},{"$f":"IF(AI104=\"\",\"\",AI104)","v":"NJ-1AP(KT)7-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-9","01G09","水阀反馈",{"$f":"AH104&\"-\"&AK104","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"AHU01G09_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%I\"&B104*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LAHU01G09_WVB AT%I242.0 :INT ; (*空调机组NJ-1AP(KT)7-9-水阀反馈*)"},"LAHU01G09_WVB           AT%I242.0      :INT ; (*空调机组NJ-1AP(KT)7-9-水阀反馈*)",null,"AHU01G09_WVB",{"$f":"J104","v":"空调机组NJ-1AP(KT)7-9-水阀反馈"},{"$f":"AS103+1","v":30121}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-1AP(KT)7-10-回风温度",{"$nulls":16},"NJ-1AP(KT)7-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-10","01G10","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"AHU01G10_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%I\"&B104*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LAHU01G10_RT AT%I244.0 :INT ; (*空调机组NJ-1AP(KT)7-10-回风温度*)"},"LAHU01G10_RT            AT%I244.0      :INT ; (*空调机组NJ-1AP(KT)7-10-回风温度*)",null,"AHU01G10_RT","空调机组NJ-1AP(KT)7-10-回风温度",{"$f":"AS104+1","v":30122}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-1AP(KT)7-10-水阀反馈",{"$nulls":16},"NJ-1AP(KT)7-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-10","01G10","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":"AHU01G10_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%I\"&B104*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":"LAHU01G10_WVB AT%I246.0 :INT ; (*空调机组NJ-1AP(KT)7-10-水阀反馈*)"},"LAHU01G10_WVB           AT%I246.0      :INT ; (*空调机组NJ-1AP(KT)7-10-水阀反馈*)",null,"AHU01G10_WVB","空调机组NJ-1AP(KT)7-10-水阀反馈",30123]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-1AP(KT)7-11-回风温度",{"$nulls":16},"NJ-1AP(KT)7-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-11","01G11","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH107,List!$B$3:$D$445,2,FALSE)&AJ107&\"_\"&VLOOKUP(AK107,List!$K$2:$M$447,2,FALSE)","v":"AHU01G11_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM107&\" \"&\"AT%I\"&B104*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J107&\"*)\",\" \")","v":"LAHU01G11_RT AT%I248.0 :INT ; (*空调机组NJ-1AP(KT)7-11-回风温度*)"},"LAHU01G11_RT            AT%I248.0      :INT ; (*空调机组NJ-1AP(KT)7-11-回风温度*)",null,"AHU01G11_RT","空调机组NJ-1AP(KT)7-11-回风温度",30124]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-1AP(KT)7-11-水阀反馈",{"$nulls":16},{"$f":"IF(AI108=\"\",\"\",AI108)","v":"NJ-1AP(KT)7-11"},{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-11","01G11","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH108,List!$B$3:$D$445,2,FALSE)&AJ108&\"_\"&VLOOKUP(AK108,List!$K$2:$M$447,2,FALSE)","v":"AHU01G11_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM108&\" \"&\"AT%I\"&B104*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J108&\"*)\",\" \")","v":"LAHU01G11_WVB AT%I250.0 :INT ; (*空调机组NJ-1AP(KT)7-11-水阀反馈*)"},"LAHU01G11_WVB           AT%I250.0      :INT ; (*空调机组NJ-1AP(KT)7-11-水阀反馈*)",null,"AHU01G11_WVB",{"$f":"J108","v":"空调机组NJ-1AP(KT)7-11-水阀反馈"},30125]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-1AP(KT)7-12-回风温度",{"$nulls":16},"NJ-1AP(KT)7-12",{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-12","01G12","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH109,List!$B$3:$D$445,2,FALSE)&AJ109&\"_\"&VLOOKUP(AK109,List!$K$2:$M$447,2,FALSE)","v":"AHU01G12_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM109&\" \"&\"AT%I\"&B104*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J109&\"*)\",\" \")","v":"LAHU01G12_RT AT%I252.0 :INT ; (*空调机组NJ-1AP(KT)7-12-回风温度*)"},"LAHU01G12_RT            AT%I252.0      :INT ; (*空调机组NJ-1AP(KT)7-12-回风温度*)",null,"AHU01G12_RT","空调机组NJ-1AP(KT)7-12-回风温度",30126]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-1AP(KT)7-12-水阀反馈",{"$nulls":16},"NJ-1AP(KT)7-12",{"$f":"_xlfn.IFNA(VLOOKUP(AL110,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL110,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-12","01G12","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH110,List!$B$3:$D$445,2,FALSE)&AJ110&\"_\"&VLOOKUP(AK110,List!$K$2:$M$447,2,FALSE)","v":"AHU01G12_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM110&\" \"&\"AT%I\"&B104*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J110&\"*)\",\" \")","v":"LAHU01G12_WVB AT%I254.0 :INT ; (*空调机组NJ-1AP(KT)7-12-水阀反馈*)"},"LAHU01G12_WVB           AT%I254.0      :INT ; (*空调机组NJ-1AP(KT)7-12-水阀反馈*)",null,"AHU01G12_WVB","空调机组NJ-1AP(KT)7-12-水阀反馈",30127]
[null,{"$f":"B116","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B116&\"地址: \"&B113&\" *)\"","v":"(* IOM 0401A地址: 16 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH112&AA112&\"-\"&AK112","v":"空调机组NJ-1AP(KT)7-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI112=\"\",\"\",AI112)","v":"NJ-1AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-1","01G01","水阀控制",{"$f":"AH112&\"-\"&AK112","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH112,List!$B$3:$D$445,2,FALSE)&AJ112&\"_\"&VLOOKUP(AK112,List!$K$2:$M$447,2,FALSE)","v":"AHU01G01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM112&\" \"&\"AT%Q\"&B113*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J112&\"*)\",\" \")","v":"LAHU01G01_WVC AT%Q256.0 :INT ; (*空调机组NJ-1AP(KT)7-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112))),SEARCH(\":\",REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112)))))),\" \")","v":"LAHU01G01_WVC           AT%Q256.0      :INT ; (*空调机组NJ-1AP(KT)7-1-水阀控制*)"},null,{"$f":"AM112","v":"AHU01G01_WVC"},{"$f":"J112","v":"空调机组NJ-1AP(KT)7-1-水阀控制"},{"$f":"40000+($B113*8+F112-1)","v":40128}]
[null,16,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH113&AA113&\"-\"&AK113","v":"空调机组NJ-1AP(KT)7-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI113=\"\",\"\",AI113)","v":"NJ-1AP(KT)7-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-2","01G02","水阀控制",{"$f":"AH113&\"-\"&AK113","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH113,List!$B$3:$D$445,2,FALSE)&AJ113&\"_\"&VLOOKUP(AK113,List!$K$2:$M$447,2,FALSE)","v":"AHU01G02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM113&\" \"&\"AT%Q\"&B113*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J113&\"*)\",\" \")","v":"LAHU01G02_WVC AT%Q258.0 :INT ; (*空调机组NJ-1AP(KT)7-2-水阀控制*)"},"LAHU01G02_WVC           AT%Q258.0      :INT ; (*空调机组NJ-1AP(KT)7-2-水阀控制*)",null,"AHU01G02_WVC",{"$f":"J113","v":"空调机组NJ-1AP(KT)7-2-水阀控制"},{"$f":"AS112+1","v":40129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH114&AA114&\"-\"&AK114","v":"空调机组NJ-1AP(KT)7-3-水阀控制"},{"$nulls":16},"NJ-1AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-3","01G03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH114,List!$B$3:$D$445,2,FALSE)&AJ114&\"_\"&VLOOKUP(AK114,List!$K$2:$M$447,2,FALSE)","v":"AHU01G03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM114&\" \"&\"AT%Q\"&B113*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J114&\"*)\",\" \")","v":"LAHU01G03_WVC AT%Q260.0 :INT ; (*空调机组NJ-1AP(KT)7-3-水阀控制*)"},"LAHU01G03_WVC           AT%Q260.0      :INT ; (*空调机组NJ-1AP(KT)7-3-水阀控制*)",null,"AHU01G03_WVC","空调机组NJ-1AP(KT)7-3-水阀控制",{"$f":"AS113+1","v":40130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH115&AA115&\"-\"&AK115","v":"空调机组NJ-1AP(KT)7-4-水阀控制"},{"$nulls":16},"NJ-1AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-4","01G04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH115,List!$B$3:$D$445,2,FALSE)&AJ115&\"_\"&VLOOKUP(AK115,List!$K$2:$M$447,2,FALSE)","v":"AHU01G04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM115&\" \"&\"AT%Q\"&B113*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J115&\"*)\",\" \")","v":"LAHU01G04_WVC AT%Q262.0 :INT ; (*空调机组NJ-1AP(KT)7-4-水阀控制*)"},"LAHU01G04_WVC           AT%Q262.0      :INT ; (*空调机组NJ-1AP(KT)7-4-水阀控制*)",null,"AHU01G04_WVC","空调机组NJ-1AP(KT)7-4-水阀控制",40131]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B50","v":0},{"$nulls":38},{"$f":"\"(* \"&B125&\"地址: \"&B122&\" *)\"","v":"(* IOM 0401A地址: 17 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH121&AA121&\"-\"&AK121","v":"空调机组NJ-1AP(KT)7-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI121=\"\",\"\",AI121)","v":"NJ-1AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-5","01G05","水阀控制",{"$f":"AH121&\"-\"&AK121","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH121,List!$B$3:$D$445,2,FALSE)&AJ121&\"_\"&VLOOKUP(AK121,List!$K$2:$M$447,2,FALSE)","v":"AHU01G05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM121&\" \"&\"AT%Q\"&B122*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J121&\"*)\",\" \")","v":"LAHU01G05_WVC AT%Q272.0 :INT ; (*空调机组NJ-1AP(KT)7-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121))),SEARCH(\":\",REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121)))))),\" \")","v":"LAHU01G05_WVC           AT%Q272.0      :INT ; (*空调机组NJ-1AP(KT)7-5-水阀控制*)"},null,{"$f":"AM121","v":"AHU01G05_WVC"},{"$f":"J121","v":"空调机组NJ-1AP(KT)7-5-水阀控制"},{"$f":"40000+($B122*8+F121-1)","v":40136}]
[null,17,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH122&AA122&\"-\"&AK122","v":"空调机组NJ-1AP(KT)7-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI122=\"\",\"\",AI122)","v":"NJ-1AP(KT)7-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-6","01G06","水阀控制",{"$f":"AH122&\"-\"&AK122","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH122,List!$B$3:$D$445,2,FALSE)&AJ122&\"_\"&VLOOKUP(AK122,List!$K$2:$M$447,2,FALSE)","v":"AHU01G06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM122&\" \"&\"AT%Q\"&B122*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J122&\"*)\",\" \")","v":"LAHU01G06_WVC AT%Q274.0 :INT ; (*空调机组NJ-1AP(KT)7-6-水阀控制*)"},"LAHU01G06_WVC           AT%Q274.0      :INT ; (*空调机组NJ-1AP(KT)7-6-水阀控制*)",null,"AHU01G06_WVC",{"$f":"J122","v":"空调机组NJ-1AP(KT)7-6-水阀控制"},{"$f":"AS121+1","v":40137}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH123&AA123&\"-\"&AK123","v":"空调机组NJ-1AP(KT)7-7-水阀控制"},{"$nulls":16},{"$f":"IF(AI123=\"\",\"\",AI123)","v":"NJ-1AP(KT)7-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-7","01G07","水阀控制",{"$f":"AH123&\"-\"&AK123","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH123,List!$B$3:$D$445,2,FALSE)&AJ123&\"_\"&VLOOKUP(AK123,List!$K$2:$M$447,2,FALSE)","v":"AHU01G07_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM123&\" \"&\"AT%Q\"&B122*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J123&\"*)\",\" \")","v":"LAHU01G07_WVC AT%Q276.0 :INT ; (*空调机组NJ-1AP(KT)7-7-水阀控制*)"},"LAHU01G07_WVC           AT%Q276.0      :INT ; (*空调机组NJ-1AP(KT)7-7-水阀控制*)",null,"AHU01G07_WVC","空调机组NJ-1AP(KT)7-7-水阀控制",{"$f":"AS122+1","v":40138}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH124&AA124&\"-\"&AK124","v":"空调机组NJ-1AP(KT)7-8-水阀控制"},{"$nulls":16},"NJ-1AP(KT)7-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-8","01G08","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH124,List!$B$3:$D$445,2,FALSE)&AJ124&\"_\"&VLOOKUP(AK124,List!$K$2:$M$447,2,FALSE)","v":"AHU01G08_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM124&\" \"&\"AT%Q\"&B122*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J124&\"*)\",\" \")","v":"LAHU01G08_WVC AT%Q278.0 :INT ; (*空调机组NJ-1AP(KT)7-8-水阀控制*)"},"LAHU01G08_WVC           AT%Q278.0      :INT ; (*空调机组NJ-1AP(KT)7-8-水阀控制*)",null,"AHU01G08_WVC","空调机组NJ-1AP(KT)7-8-水阀控制",40139]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B134","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B134&\"地址: \"&B131&\" *)\"","v":"(* IOM 0401A地址: 18 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH130&AA130&\"-\"&AK130","v":"空调机组NJ-1AP(KT)7-9-水阀控制"},{"$nulls":16},{"$f":"IF(AI130=\"\",\"\",AI130)","v":"NJ-1AP(KT)7-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL130,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL130,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-9","01G09","水阀控制",{"$f":"AH130&\"-\"&AK130","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH130,List!$B$3:$D$445,2,FALSE)&AJ130&\"_\"&VLOOKUP(AK130,List!$K$2:$M$447,2,FALSE)","v":"AHU01G09_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM130&\" \"&\"AT%Q\"&B131*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J130&\"*)\",\" \")","v":"LAHU01G09_WVC AT%Q288.0 :INT ; (*空调机组NJ-1AP(KT)7-9-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN130,SEARCH(\"AT%\",AN130),,REPT(\" \",25-SEARCH(\"AT%\",AN130))),SEARCH(\":\",REPLACE(AN130,SEARCH(\"AT%\",AN130),,REPT(\" \",25-SEARCH(\"AT%\",AN130)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN130,SEARCH(\"AT%\",AN130),,REPT(\" \",25-SEARCH(\"AT%\",AN130)))))),\" \")","v":"LAHU01G09_WVC           AT%Q288.0      :INT ; (*空调机组NJ-1AP(KT)7-9-水阀控制*)"},null,{"$f":"AM130","v":"AHU01G09_WVC"},{"$f":"J130","v":"空调机组NJ-1AP(KT)7-9-水阀控制"},{"$f":"40000+($B131*8+F130-1)","v":40144}]
[null,18,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH131&AA131&\"-\"&AK131","v":"空调机组NJ-1AP(KT)7-10-水阀控制"},{"$nulls":16},{"$f":"IF(AI131=\"\",\"\",AI131)","v":"NJ-1AP(KT)7-10"},{"$f":"_xlfn.IFNA(VLOOKUP(AL131,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL131,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-10","01G10","水阀控制",{"$f":"AH131&\"-\"&AK131","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH131,List!$B$3:$D$445,2,FALSE)&AJ131&\"_\"&VLOOKUP(AK131,List!$K$2:$M$447,2,FALSE)","v":"AHU01G10_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM131&\" \"&\"AT%Q\"&B131*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J131&\"*)\",\" \")","v":"LAHU01G10_WVC AT%Q290.0 :INT ; (*空调机组NJ-1AP(KT)7-10-水阀控制*)"},"LAHU01G10_WVC           AT%Q290.0      :INT ; (*空调机组NJ-1AP(KT)7-10-水阀控制*)",null,"AHU01G10_WVC",{"$f":"J131","v":"空调机组NJ-1AP(KT)7-10-水阀控制"},{"$f":"AS130+1","v":40145}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH132&AA132&\"-\"&AK132","v":"空调机组NJ-1AP(KT)7-11-水阀控制"},{"$nulls":16},{"$f":"IF(AI132=\"\",\"\",AI132)","v":"NJ-1AP(KT)7-11"},{"$f":"_xlfn.IFNA(VLOOKUP(AL132,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL132,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-11","01G11","水阀控制",{"$f":"AH132&\"-\"&AK132","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH132,List!$B$3:$D$445,2,FALSE)&AJ132&\"_\"&VLOOKUP(AK132,List!$K$2:$M$447,2,FALSE)","v":"AHU01G11_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM132&\" \"&\"AT%Q\"&B131*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J132&\"*)\",\" \")","v":"LAHU01G11_WVC AT%Q292.0 :INT ; (*空调机组NJ-1AP(KT)7-11-水阀控制*)"},"LAHU01G11_WVC           AT%Q292.0      :INT ; (*空调机组NJ-1AP(KT)7-11-水阀控制*)",null,"AHU01G11_WVC","空调机组NJ-1AP(KT)7-11-水阀控制",{"$f":"AS131+1","v":40146}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH133&AA133&\"-\"&AK133","v":"空调机组NJ-1AP(KT)7-12-水阀控制"},{"$nulls":16},"NJ-1AP(KT)7-12",{"$f":"_xlfn.IFNA(VLOOKUP(AL133,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL133,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)7-12","01G12","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH133,List!$B$3:$D$445,2,FALSE)&AJ133&\"_\"&VLOOKUP(AK133,List!$K$2:$M$447,2,FALSE)","v":"AHU01G12_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM133&\" \"&\"AT%Q\"&B131*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J133&\"*)\",\" \")","v":"LAHU01G12_WVC AT%Q294.0 :INT ; (*空调机组NJ-1AP(KT)7-12-水阀控制*)"},"LAHU01G12_WVC           AT%Q294.0      :INT ; (*空调机组NJ-1AP(KT)7-12-水阀控制*)",null,"AHU01G12_WVC","空调机组NJ-1AP(KT)7-12-水阀控制",40147]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L208","index":19,"n_rows":111,"n_cols":45,"rows_kept":111,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[6,1,6,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[92,5,92,6],[92,9,92,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[101,5,101,6],[101,9,101,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[109,5,109,6],[109,9,109,25],[110,5,110,6],[110,9,110,25],[4,1,5,1],[12,1,23,1],[29,1,40,1],[46,1,57,1],[63,1,74,1],[80,1,83,1],[89,1,92,1],[98,1,101,1],[107,1,110,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[16,2,23,4],[33,2,40,4],[67,2,74,4],[50,2,57,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L18",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"EXC-1000"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B13&\"地址: \"&B10&\" *)\"","v":"(* IOM 1601R地址: 0 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH9&AA9&\"-\"&AK9","v":"空调机组NJ-2AP(KT)8-1-运行状态"},{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-2AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-1","02H01","运行状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU02H01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B10*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU02H01_R AT%I0.0 :BOOL; (*空调机组NJ-2AP(KT)8-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9))),SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))))),\" \")","v":"LAHU02H01_R             AT%I0.0        :BOOL; (*空调机组NJ-2AP(KT)8-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM9","v":"L18\\L18AHU02H01_R"},{"$f":"J9","v":"空调机组NJ-2AP(KT)8-1-运行状态"},{"$f":"10000+($B10*16*8+F9-1)","v":10000}]
[null,0,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-2AP(KT)8-1-故障状态",{"$nulls":16},{"$f":"IF(AI10=\"\",\"\",AI10)","v":"NJ-2AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-1","02H01","故障状态",{"$f":"AH10&\"-\"&AK10","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU02H01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B10*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU02H01_F AT%I0.1 :BOOL; (*空调机组NJ-2AP(KT)8-1-故障状态*)"},"LAHU02H01_F             AT%I0.1        :BOOL; (*空调机组NJ-2AP(KT)8-1-故障状态*)",null,"L18\\L18AHU02H01_F",{"$f":"J10","v":"空调机组NJ-2AP(KT)8-1-故障状态"},{"$f":"AS9+1","v":10001}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-2AP(KT)8-1-自动状态",{"$nulls":16},"NJ-2AP(KT)8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-1","02H01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU02H01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B10*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU02H01_A AT%I0.2 :BOOL; (*空调机组NJ-2AP(KT)8-1-自动状态*)"},"LAHU02H01_A             AT%I0.2        :BOOL; (*空调机组NJ-2AP(KT)8-1-自动状态*)",null,"L18\\L18AHU02H01_A","空调机组NJ-2AP(KT)8-1-自动状态",{"$f":"AS10+1","v":10002}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-2AP(KT)8-1-风机压差",{"$nulls":16},"NJ-2AP(KT)8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-1","02H01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU02H01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B10*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU02H01_FPS AT%I0.3 :BOOL; (*空调机组NJ-2AP(KT)8-1-风机压差*)"},"LAHU02H01_FPS           AT%I0.3        :BOOL; (*空调机组NJ-2AP(KT)8-1-风机压差*)",null,"L18\\L18AHU02H01_FPS","空调机组NJ-2AP(KT)8-1-风机压差",10003]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-2AP(KT)8-2-运行状态",{"$nulls":16},"NJ-2AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-2","02H02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU02H02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B10*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU02H02_R AT%I0.4 :BOOL; (*空调机组NJ-2AP(KT)8-2-运行状态*)"},"LAHU02H02_R             AT%I0.4        :BOOL; (*空调机组NJ-2AP(KT)8-2-运行状态*)",null,"L18\\L18AHU02H02_R","空调机组NJ-2AP(KT)8-2-运行状态",10004]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-2AP(KT)8-2-故障状态",{"$nulls":16},"NJ-2AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-2","02H02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU02H02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B10*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU02H02_F AT%I0.5 :BOOL; (*空调机组NJ-2AP(KT)8-2-故障状态*)"},"LAHU02H02_F             AT%I0.5        :BOOL; (*空调机组NJ-2AP(KT)8-2-故障状态*)",null,"L18\\L18AHU02H02_F","空调机组NJ-2AP(KT)8-2-故障状态",10005]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-2AP(KT)8-2-自动状态",{"$nulls":16},"NJ-2AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-2","02H02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU02H02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B10*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU02H02_A AT%I0.6 :BOOL; (*空调机组NJ-2AP(KT)8-2-自动状态*)"},"LAHU02H02_A             AT%I0.6        :BOOL; (*空调机组NJ-2AP(KT)8-2-自动状态*)",null,"L18\\L18AHU02H02_A","空调机组NJ-2AP(KT)8-2-自动状态",10006]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-2AP(KT)8-2-风机压差",{"$nulls":16},"NJ-2AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-2","02H02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU02H02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B10*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU02H02_FPS AT%I0.7 :BOOL; (*空调机组NJ-2AP(KT)8-2-风机压差*)"},"LAHU02H02_FPS           AT%I0.7        :BOOL; (*空调机组NJ-2AP(KT)8-2-风机压差*)",null,"L18\\L18AHU02H02_FPS","空调机组NJ-2AP(KT)8-2-风机压差",10007]
[{"$nulls":5},9,null,17,18,"空调机组NJ-2AP(KT)8-3-运行状态",{"$nulls":16},"NJ-2AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-3","02H03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU02H03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B10*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU02H03_R AT%I1.0 :BOOL; (*空调机组NJ-2AP(KT)8-3-运行状态*)"},"LAHU02H03_R             AT%I1.0        :BOOL; (*空调机组NJ-2AP(KT)8-3-运行状态*)",null,"L18\\L18AHU02H03_R","空调机组NJ-2AP(KT)8-3-运行状态",10008]
[{"$nulls":5},10,null,19,20,"空调机组NJ-2AP(KT)8-3-故障状态",{"$nulls":16},{"$f":"IF(AI18=\"\",\"\",AI18)","v":"NJ-2AP(KT)8-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-3","02H03","故障状态",{"$f":"AH18&\"-\"&AK18","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU02H03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B10*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU02H03_F AT%I1.1 :BOOL; (*空调机组NJ-2AP(KT)8-3-故障状态*)"},"LAHU02H03_F             AT%I1.1        :BOOL; (*空调机组NJ-2AP(KT)8-3-故障状态*)",null,"L18\\L18AHU02H03_F","空调机组NJ-2AP(KT)8-3-故障状态",10009]
[{"$nulls":5},11,null,21,22,"空调机组NJ-2AP(KT)8-3-自动状态",{"$nulls":16},"NJ-2AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-3","02H03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU02H03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B10*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU02H03_A AT%I1.2 :BOOL; (*空调机组NJ-2AP(KT)8-3-自动状态*)"},"LAHU02H03_A             AT%I1.2        :BOOL; (*空调机组NJ-2AP(KT)8-3-自动状态*)",null,"L18\\L18AHU02H03_A","空调机组NJ-2AP(KT)8-3-自动状态",10010]
[{"$nulls":5},12,null,23,24,"空调机组NJ-2AP(KT)8-3-风机压差",{"$nulls":16},"NJ-2AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-3","02H03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU02H03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B10*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU02H03_FPS AT%I1.3 :BOOL; (*空调机组NJ-2AP(KT)8-3-风机压差*)"},"LAHU02H03_FPS           AT%I1.3        :BOOL; (*空调机组NJ-2AP(KT)8-3-风机压差*)",null,"L18\\L18AHU02H03_FPS","空调机组NJ-2AP(KT)8-3-风机压差",10011]
[{"$nulls":5},13,null,25,26,"空调机组NJ-2AP(KT)8-4-运行状态",{"$nulls":16},"NJ-2AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-4","02H04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU02H04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B10*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU02H04_R AT%I1.4 :BOOL; (*空调机组NJ-2AP(KT)8-4-运行状态*)"},"LAHU02H04_R             AT%I1.4        :BOOL; (*空调机组NJ-2AP(KT)8-4-运行状态*)",null,"L18\\L18AHU02H04_R","空调机组NJ-2AP(KT)8-4-运行状态",10012]
[{"$nulls":5},14,null,27,28,"空调机组NJ-2AP(KT)8-4-故障状态",{"$nulls":16},"NJ-2AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-4","02H04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU02H04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B10*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU02H04_F AT%I1.5 :BOOL; (*空调机组NJ-2AP(KT)8-4-故障状态*)"},"LAHU02H04_F             AT%I1.5        :BOOL; (*空调机组NJ-2AP(KT)8-4-故障状态*)",null,"L18\\L18AHU02H04_F","空调机组NJ-2AP(KT)8-4-故障状态",10013]
[{"$nulls":5},15,null,29,30,"空调机组NJ-2AP(KT)8-4-自动状态",{"$nulls":16},"NJ-2AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-4","02H04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU02H04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B10*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU02H04_A AT%I1.6 :BOOL; (*空调机组NJ-2AP(KT)8-4-自动状态*)"},"LAHU02H04_A             AT%I1.6        :BOOL; (*空调机组NJ-2AP(KT)8-4-自动状态*)",null,"L18\\L18AHU02H04_A","空调机组NJ-2AP(KT)8-4-自动状态",10014]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-2AP(KT)8-4-风机压差",{"$nulls":16},"NJ-2AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-4","02H04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH24,List!$B$3:$D$445,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,List!$K$2:$M$447,2,FALSE)","v":"AHU02H04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%I\"&B10*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":"LAHU02H04_FPS AT%I1.7 :BOOL; (*空调机组NJ-2AP(KT)8-4-风机压差*)"},"LAHU02H04_FPS           AT%I1.7        :BOOL; (*空调机组NJ-2AP(KT)8-4-风机压差*)",null,"L18\\L18AHU02H04_FPS","空调机组NJ-2AP(KT)8-4-风机压差",10015]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 1601R地址: 1 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH26&AA26&\"-\"&AK26","v":"空调机组NJ-2AP(KT)8-5-运行状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-2AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-5","02H05","运行状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU02H05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU02H05_R AT%I16.0 :BOOL; (*空调机组NJ-2AP(KT)8-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LAHU02H05_R             AT%I16.0       :BOOL; (*空调机组NJ-2AP(KT)8-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L18\\L18AHU02H05_R"},{"$f":"J26","v":"空调机组NJ-2AP(KT)8-5-运行状态"},{"$f":"10000+($B27*16*8+F26-1)","v":10128}]
[null,1,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-2AP(KT)8-5-故障状态",{"$nulls":16},{"$f":"IF(AI27=\"\",\"\",AI27)","v":"NJ-2AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-5","02H05","故障状态",{"$f":"AH27&\"-\"&AK27","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU02H05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU02H05_F AT%I16.1 :BOOL; (*空调机组NJ-2AP(KT)8-5-故障状态*)"},"LAHU02H05_F             AT%I16.1       :BOOL; (*空调机组NJ-2AP(KT)8-5-故障状态*)",null,"L18\\L18AHU02H05_F",{"$f":"J27","v":"空调机组NJ-2AP(KT)8-5-故障状态"},{"$f":"AS26+1","v":10129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-2AP(KT)8-5-自动状态",{"$nulls":16},"NJ-2AP(KT)8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-5","02H05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU02H05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU02H05_A AT%I16.2 :BOOL; (*空调机组NJ-2AP(KT)8-5-自动状态*)"},"LAHU02H05_A             AT%I16.2       :BOOL; (*空调机组NJ-2AP(KT)8-5-自动状态*)",null,"L18\\L18AHU02H05_A","空调机组NJ-2AP(KT)8-5-自动状态",{"$f":"AS27+1","v":10130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-2AP(KT)8-5-风机压差",{"$nulls":16},"NJ-2AP(KT)8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-5","02H05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU02H05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU02H05_FPS AT%I16.3 :BOOL; (*空调机组NJ-2AP(KT)8-5-风机压差*)"},"LAHU02H05_FPS           AT%I16.3       :BOOL; (*空调机组NJ-2AP(KT)8-5-风机压差*)",null,"L18\\L18AHU02H05_FPS","空调机组NJ-2AP(KT)8-5-风机压差",10131]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-2AP(KT)8-6-运行状态",{"$nulls":16},"NJ-2AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-6","02H06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU02H06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B27*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU02H06_R AT%I16.4 :BOOL; (*空调机组NJ-2AP(KT)8-6-运行状态*)"},"LAHU02H06_R             AT%I16.4       :BOOL; (*空调机组NJ-2AP(KT)8-6-运行状态*)",null,"L18\\L18AHU02H06_R","空调机组NJ-2AP(KT)8-6-运行状态",10132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-2AP(KT)8-6-故障状态",{"$nulls":16},"NJ-2AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-6","02H06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU02H06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B27*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU02H06_F AT%I16.5 :BOOL; (*空调机组NJ-2AP(KT)8-6-故障状态*)"},"LAHU02H06_F             AT%I16.5       :BOOL; (*空调机组NJ-2AP(KT)8-6-故障状态*)",null,"L18\\L18AHU02H06_F","空调机组NJ-2AP(KT)8-6-故障状态",10133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-2AP(KT)8-6-自动状态",{"$nulls":16},"NJ-2AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-6","02H06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU02H06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B27*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU02H06_A AT%I16.6 :BOOL; (*空调机组NJ-2AP(KT)8-6-自动状态*)"},"LAHU02H06_A             AT%I16.6       :BOOL; (*空调机组NJ-2AP(KT)8-6-自动状态*)",null,"L18\\L18AHU02H06_A","空调机组NJ-2AP(KT)8-6-自动状态",10134]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-2AP(KT)8-6-风机压差",{"$nulls":16},"NJ-2AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-6","02H06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU02H06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B27*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU02H06_FPS AT%I16.7 :BOOL; (*空调机组NJ-2AP(KT)8-6-风机压差*)"},"LAHU02H06_FPS           AT%I16.7       :BOOL; (*空调机组NJ-2AP(KT)8-6-风机压差*)",null,"L18\\L18AHU02H06_FPS","空调机组NJ-2AP(KT)8-6-风机压差",10135]
[{"$nulls":5},9,null,17,18,"空调机组NJ-2AP(KT)8-7-运行状态",{"$nulls":16},"NJ-2AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-7","02H07","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU02H07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B27*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU02H07_R AT%I17.0 :BOOL; (*空调机组NJ-2AP(KT)8-7-运行状态*)"},"LAHU02H07_R             AT%I17.0       :BOOL; (*空调机组NJ-2AP(KT)8-7-运行状态*)",null,"L18\\L18AHU02H07_R","空调机组NJ-2AP(KT)8-7-运行状态",10136]
[{"$nulls":5},10,null,19,20,"空调机组NJ-2AP(KT)8-7-故障状态",{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-2AP(KT)8-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-7","02H07","故障状态",{"$f":"AH35&\"-\"&AK35","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU02H07_F"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B27*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU02H07_F AT%I17.1 :BOOL; (*空调机组NJ-2AP(KT)8-7-故障状态*)"},"LAHU02H07_F             AT%I17.1       :BOOL; (*空调机组NJ-2AP(KT)8-7-故障状态*)",null,"L18\\L18AHU02H07_F",{"$f":"J35","v":"空调机组NJ-2AP(KT)8-7-故障状态"},10137]
[{"$nulls":5},11,null,21,22,"空调机组NJ-2AP(KT)8-7-自动状态",{"$nulls":16},"NJ-2AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-7","02H07","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU02H07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B27*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU02H07_A AT%I17.2 :BOOL; (*空调机组NJ-2AP(KT)8-7-自动状态*)"},"LAHU02H07_A             AT%I17.2       :BOOL; (*空调机组NJ-2AP(KT)8-7-自动状态*)",null,"L18\\L18AHU02H07_A","空调机组NJ-2AP(KT)8-7-自动状态",10138]
[{"$nulls":5},12,null,23,24,"空调机组NJ-2AP(KT)8-7-风机压差",{"$nulls":16},"NJ-2AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-7","02H07","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"AHU02H07_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B27*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LAHU02H07_FPS AT%I17.3 :BOOL; (*空调机组NJ-2AP(KT)8-7-风机压差*)"},"LAHU02H07_FPS           AT%I17.3       :BOOL; (*空调机组NJ-2AP(KT)8-7-风机压差*)",null,"L18\\L18AHU02H07_FPS","空调机组NJ-2AP(KT)8-7-风机压差",10139]
[{"$nulls":5},13,null,25,26,"空调机组NJ-2AP(KT)8-8-运行状态",{"$nulls":16},"NJ-2AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-8","02H08","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"AHU02H08_R"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B27*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LAHU02H08_R AT%I17.4 :BOOL; (*空调机组NJ-2AP(KT)8-8-运行状态*)"},"LAHU02H08_R             AT%I17.4       :BOOL; (*空调机组NJ-2AP(KT)8-8-运行状态*)",null,"L18\\L18AHU02H08_R","空调机组NJ-2AP(KT)8-8-运行状态",10140]
[{"$nulls":5},14,null,27,28,"空调机组NJ-2AP(KT)8-8-故障状态",{"$nulls":16},"NJ-2AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-8","02H08","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"AHU02H08_F"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B27*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LAHU02H08_F AT%I17.5 :BOOL; (*空调机组NJ-2AP(KT)8-8-故障状态*)"},"LAHU02H08_F             AT%I17.5       :BOOL; (*空调机组NJ-2AP(KT)8-8-故障状态*)",null,"L18\\L18AHU02H08_F","空调机组NJ-2AP(KT)8-8-故障状态",10141]
[{"$nulls":5},15,null,29,30,"空调机组NJ-2AP(KT)8-8-自动状态",{"$nulls":16},"NJ-2AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-8","02H08","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"AHU02H08_A"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B27*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LAHU02H08_A AT%I17.6 :BOOL; (*空调机组NJ-2AP(KT)8-8-自动状态*)"},"LAHU02H08_A             AT%I17.6       :BOOL; (*空调机组NJ-2AP(KT)8-8-自动状态*)",null,"L18\\L18AHU02H08_A","空调机组NJ-2AP(KT)8-8-自动状态",10142]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-2AP(KT)8-8-风机压差",{"$nulls":16},"NJ-2AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-8","02H08","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":"AHU02H08_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%I\"&B27*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":"LAHU02H08_FPS AT%I17.7 :BOOL; (*空调机组NJ-2AP(KT)8-8-风机压差*)"},"LAHU02H08_FPS           AT%I17.7       :BOOL; (*空调机组NJ-2AP(KT)8-8-风机压差*)",null,"L18\\L18AHU02H08_FPS","空调机组NJ-2AP(KT)8-8-风机压差",10143]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 1601R地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH43&AA43&\"-\"&AK43","v":"照明控制箱NJ-2AL8-1-运行状态"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-2AL8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL8-1","02H01","运行状态",{"$f":"AH43&\"-\"&AK43","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"LCB02H01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B44*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LLCB02H01_R AT%I32.0 :BOOL; (*照明控制箱NJ-2AL8-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LLCB02H01_R             AT%I32.0       :BOOL; (*照明控制箱NJ-2AL8-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM43","v":"L18\\L18LCB02H01_R"},{"$f":"J43","v":"照明控制箱NJ-2AL8-1-运行状态"},{"$f":"10000+($B44*16*8+F43-1)","v":10256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},2,null,3,4,"照明控制箱NJ-2AL8-1-自动状态",{"$nulls":16},{"$f":"IF(AI44=\"\",\"\",AI44)","v":"NJ-2AL8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL8-1","02H01","自动状态",{"$f":"AH44&\"-\"&AK44","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"LCB02H01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B44*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LLCB02H01_A AT%I32.1 :BOOL; (*照明控制箱NJ-2AL8-1-自动状态*)"},"LLCB02H01_A             AT%I32.1       :BOOL; (*照明控制箱NJ-2AL8-1-自动状态*)",null,"L18\\L18LCB02H01_A",{"$f":"J44","v":"照明控制箱NJ-2AL8-1-自动状态"},{"$f":"AS43+1","v":10257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,5,6,"照明控制箱NJ-2AL8-2-运行状态",{"$nulls":16},"NJ-2AL8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-2AL8-2","02H02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"LCB02H02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B44*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LLCB02H02_R AT%I32.2 :BOOL; (*照明控制箱NJ-2AL8-2-运行状态*)"},"LLCB02H02_R             AT%I32.2       :BOOL; (*照明控制箱NJ-2AL8-2-运行状态*)",null,"L18\\L18LCB02H02_R","照明控制箱NJ-2AL8-2-运行状态",{"$f":"AS44+1","v":10258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},4,null,7,8,"照明控制箱NJ-2AL8-2-自动状态",{"$nulls":16},"NJ-2AL8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL8-2","02H02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"LCB02H02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B44*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LLCB02H02_A AT%I32.3 :BOOL; (*照明控制箱NJ-2AL8-2-自动状态*)"},"LLCB02H02_A             AT%I32.3       :BOOL; (*照明控制箱NJ-2AL8-2-自动状态*)",null,"L18\\L18LCB02H02_A","照明控制箱NJ-2AL8-2-自动状态",10259]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-2AL8-3-运行状态",{"$nulls":16},"NJ-2AL8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL8-3","02H03","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"LCB02H03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B44*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LLCB02H03_R AT%I32.4 :BOOL; (*照明控制箱NJ-2AL8-3-运行状态*)"},"LLCB02H03_R             AT%I32.4       :BOOL; (*照明控制箱NJ-2AL8-3-运行状态*)",null,"L18\\L18LCB02H03_R","照明控制箱NJ-2AL8-3-运行状态",10260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-2AL8-3-自动状态",{"$nulls":16},"NJ-2AL8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL8-3","02H03","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"LCB02H03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B44*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LLCB02H03_A AT%I32.5 :BOOL; (*照明控制箱NJ-2AL8-3-自动状态*)"},"LLCB02H03_A             AT%I32.5       :BOOL; (*照明控制箱NJ-2AL8-3-自动状态*)",null,"L18\\L18LCB02H03_A","照明控制箱NJ-2AL8-3-自动状态",10261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"照明控制箱NJ-2AL8-4-运行状态",{"$nulls":16},"NJ-2AL8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL8-4","02H04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"LCB02H04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B44*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LLCB02H04_R AT%I32.6 :BOOL; (*照明控制箱NJ-2AL8-4-运行状态*)"},"LLCB02H04_R             AT%I32.6       :BOOL; (*照明控制箱NJ-2AL8-4-运行状态*)",null,"L18\\L18LCB02H04_R","照明控制箱NJ-2AL8-4-运行状态",10262]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"照明控制箱NJ-2AL8-4-自动状态",{"$nulls":16},"NJ-2AL8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL8-4","02H04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"LCB02H04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B44*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LLCB02H04_A AT%I32.7 :BOOL; (*照明控制箱NJ-2AL8-4-自动状态*)"},"LLCB02H04_A             AT%I32.7       :BOOL; (*照明控制箱NJ-2AL8-4-自动状态*)",null,"L18\\L18LCB02H04_A","照明控制箱NJ-2AL8-4-自动状态",10263]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-2AL8-5-运行状态",{"$nulls":16},"NJ-2AL8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL8-5","02H05","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"LCB02H05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B44*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LLCB02H05_R AT%I33.0 :BOOL; (*照明控制箱NJ-2AL8-5-运行状态*)"},"LLCB02H05_R             AT%I33.0       :BOOL; (*照明控制箱NJ-2AL8-5-运行状态*)",null,"L18\\L18LCB02H05_R","照明控制箱NJ-2AL8-5-运行状态",10264]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-2AL8-5-自动状态",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-2AL8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL8-5","02H05","自动状态",{"$f":"AH52&\"-\"&AK52","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"LCB02H05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%I\"&B44*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LLCB02H05_A AT%I33.1 :BOOL; (*照明控制箱NJ-2AL8-5-自动状态*)"},"LLCB02H05_A             AT%I33.1       :BOOL; (*照明控制箱NJ-2AL8-5-自动状态*)",null,"L18\\L18LCB02H05_A",{"$f":"J52","v":"照明控制箱NJ-2AL8-5-自动状态"},10265]
[{"$nulls":5},11,null,21,22,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%I\"&B44*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10266]
[{"$nulls":5},12,null,23,24,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%I\"&B44*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN54,SEARCH(\"AT%\",AN54),,REPT(\" \",30-SEARCH(\"AT%\",AN54))),SEARCH(\":\",REPLACE(AN54,SEARCH(\"AT%\",AN54),,REPT(\" \",30-SEARCH(\"AT%\",AN54)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN54,SEARCH(\"AT%\",AN54),,REPT(\" \",25-SEARCH(\"AT%\",AN54)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",10267]
[{"$nulls":5},13,null,25,26,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%I\"&B44*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10268]
[{"$nulls":5},14,null,27,28,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%I\"&B44*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10269]
[{"$nulls":5},15,null,29,30,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%I\"&B44*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10270]
[".",{"$nulls":4},16,null,31,32,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%I\"&B44*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10271]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B64&\"地址: \"&B61&\" *)\"","v":"(* IOM 1601D地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH60&AA60&\"-\"&AK60","v":"空调机组NJ-2AP(KT)8-1-启停控制"},{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-2AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-1","02H01","启停控制",{"$f":"AH60&\"-\"&AK60","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"AHU02H01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%Q\"&B61*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LAHU02H01_C AT%Q48.0 :BOOL; (*空调机组NJ-2AP(KT)8-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60))),SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))))),\" \")","v":"LAHU02H01_C             AT%Q48.0       :BOOL; (*空调机组NJ-2AP(KT)8-1-启停控制*)"},null,{"$f":"AM60","v":"AHU02H01_C"},{"$f":"J60","v":"空调机组NJ-2AP(KT)8-1-启停控制"},{"$f":"($B61*16*8+F60-1)","v":384}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-2AP(KT)8-2-启停控制",{"$nulls":16},{"$f":"IF(AI61=\"\",\"\",AI61)","v":"NJ-2AP(KT)8-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-2","02H02","启停控制",{"$f":"AH61&\"-\"&AK61","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"AHU02H02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%Q\"&B61*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LAHU02H02_C AT%Q48.1 :BOOL; (*空调机组NJ-2AP(KT)8-2-启停控制*)"},"LAHU02H02_C             AT%Q48.1       :BOOL; (*空调机组NJ-2AP(KT)8-2-启停控制*)",null,"AHU02H02_C",{"$f":"J61","v":"空调机组NJ-2AP(KT)8-2-启停控制"},{"$f":"AS60+1","v":385}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","空调机组NJ-2AP(KT)8-3-启停控制",{"$nulls":16},"NJ-2AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-3","02H03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"AHU02H03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%Q\"&B61*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LAHU02H03_C AT%Q48.2 :BOOL; (*空调机组NJ-2AP(KT)8-3-启停控制*)"},"LAHU02H03_C             AT%Q48.2       :BOOL; (*空调机组NJ-2AP(KT)8-3-启停控制*)",null,"AHU02H03_C","空调机组NJ-2AP(KT)8-3-启停控制",{"$f":"AS61+1","v":386}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","空调机组NJ-2AP(KT)8-4-启停控制",{"$nulls":16},"NJ-2AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-4","02H04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"AHU02H04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%Q\"&B61*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LAHU02H04_C AT%Q48.3 :BOOL; (*空调机组NJ-2AP(KT)8-4-启停控制*)"},"LAHU02H04_C             AT%Q48.3       :BOOL; (*空调机组NJ-2AP(KT)8-4-启停控制*)",null,"AHU02H04_C","空调机组NJ-2AP(KT)8-4-启停控制",387]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-2AP(KT)8-5-启停控制",{"$nulls":16},"NJ-2AP(KT)8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-5","02H05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"AHU02H05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%Q\"&B61*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LAHU02H05_C AT%Q48.4 :BOOL; (*空调机组NJ-2AP(KT)8-5-启停控制*)"},"LAHU02H05_C             AT%Q48.4       :BOOL; (*空调机组NJ-2AP(KT)8-5-启停控制*)",null,"AHU02H05_C","空调机组NJ-2AP(KT)8-5-启停控制",388]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-2AP(KT)8-6-启停控制",{"$nulls":16},"NJ-2AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-6","02H06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":"AHU02H06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%Q\"&B61*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":"LAHU02H06_C AT%Q48.5 :BOOL; (*空调机组NJ-2AP(KT)8-6-启停控制*)"},"LAHU02H06_C             AT%Q48.5       :BOOL; (*空调机组NJ-2AP(KT)8-6-启停控制*)",null,"AHU02H06_C","空调机组NJ-2AP(KT)8-6-启停控制",389]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","空调机组NJ-2AP(KT)8-7-启停控制",{"$nulls":16},"NJ-2AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-7","02H07","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":"AHU02H07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%Q\"&B61*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":"LAHU02H07_C AT%Q48.6 :BOOL; (*空调机组NJ-2AP(KT)8-7-启停控制*)"},"LAHU02H07_C             AT%Q48.6       :BOOL; (*空调机组NJ-2AP(KT)8-7-启停控制*)",null,"AHU02H07_C","空调机组NJ-2AP(KT)8-7-启停控制",390]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","空调机组NJ-2AP(KT)8-8-启停控制",{"$nulls":16},"NJ-2AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-8","02H08","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":"AHU02H08_C"},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%Q\"&B61*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":"LAHU02H08_C AT%Q48.7 :BOOL; (*空调机组NJ-2AP(KT)8-8-启停控制*)"},"LAHU02H08_C             AT%Q48.7       :BOOL; (*空调机组NJ-2AP(KT)8-8-启停控制*)",null,"AHU02H08_C","空调机组NJ-2AP(KT)8-8-启停控制",391]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-2AL8-1-启停控制",{"$nulls":16},"NJ-2AL8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL8-1","02H01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"LCB02H01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%Q\"&B61*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LLCB02H01_C AT%Q49.0 :BOOL; (*照明控制箱NJ-2AL8-1-启停控制*)"},"LLCB02H01_C             AT%Q49.0       :BOOL; (*照明控制箱NJ-2AL8-1-启停控制*)",null,"LCB02H01_C","照明控制箱NJ-2AL8-1-启停控制",392]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-2AL8-2-启停控制",{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-2AL8-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL8-2","02H02","启停控制",{"$f":"AH69&\"-\"&AK69","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"LCB02H02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%Q\"&B61*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LLCB02H02_C AT%Q49.1 :BOOL; (*照明控制箱NJ-2AL8-2-启停控制*)"},"LLCB02H02_C             AT%Q49.1       :BOOL; (*照明控制箱NJ-2AL8-2-启停控制*)",null,"LCB02H02_C",{"$f":"J69","v":"照明控制箱NJ-2AL8-2-启停控制"},393]
[{"$nulls":5},11,null,"11+","11-","照明控制箱NJ-2AL8-3-启停控制",{"$nulls":16},"NJ-2AL8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL8-3","02H03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"LCB02H03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%Q\"&B61*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LLCB02H03_C AT%Q49.2 :BOOL; (*照明控制箱NJ-2AL8-3-启停控制*)"},"LLCB02H03_C             AT%Q49.2       :BOOL; (*照明控制箱NJ-2AL8-3-启停控制*)",null,"LCB02H03_C","照明控制箱NJ-2AL8-3-启停控制",394]
[{"$nulls":5},12,null,"12+","12-","照明控制箱NJ-2AL8-4-启停控制",{"$nulls":16},"NJ-2AL8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL8-4","02H04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"LCB02H04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%Q\"&B61*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LLCB02H04_C AT%Q49.3 :BOOL; (*照明控制箱NJ-2AL8-4-启停控制*)"},"LLCB02H04_C             AT%Q49.3       :BOOL; (*照明控制箱NJ-2AL8-4-启停控制*)",null,"LCB02H04_C","照明控制箱NJ-2AL8-4-启停控制",395]
[{"$nulls":5},13,null,"13+","13-","照明控制箱NJ-2AL8-5-启停控制",{"$nulls":16},"NJ-2AL8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-2AL8-5","02H05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"LCB02H05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%Q\"&B61*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LLCB02H05_C AT%Q49.4 :BOOL; (*照明控制箱NJ-2AL8-5-启停控制*)"},"LLCB02H05_C             AT%Q49.4       :BOOL; (*照明控制箱NJ-2AL8-5-启停控制*)",null,"LCB02H05_C","照明控制箱NJ-2AL8-5-启停控制",396]
[{"$nulls":5},14,null,"14+","14-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%Q\"&B61*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",397]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%Q\"&B61*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",398]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%Q\"&B61*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",399]
[null,{"$f":"B81","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B81&\"地址: \"&B78&\" *)\"","v":"(* IOM 0801U地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH77&AA77&\"-\"&AK77","v":"空调机组NJ-2AP(KT)8-1-回风温度"},{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-2AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-1","02H01","回风温度",{"$f":"AH77&\"-\"&AK77","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"AHU02H01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%I\"&B78*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LAHU02H01_RT AT%I64.0 :INT ; (*空调机组NJ-2AP(KT)8-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77))),SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))))),\" \")","v":"LAHU02H01_RT            AT%I64.0       :INT ; (*空调机组NJ-2AP(KT)8-1-回风温度*)"},null,{"$f":"AM77","v":"AHU02H01_RT"},{"$f":"J77","v":"空调机组NJ-2AP(KT)8-1-回风温度"},{"$f":"30000+($B78*8+F77-1)","v":30032}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-2AP(KT)8-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-2AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-1","02H01","水阀反馈",{"$f":"AH78&\"-\"&AK78","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU02H01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%I\"&B78*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU02H01_WVB AT%I66.0 :INT ; (*空调机组NJ-2AP(KT)8-1-水阀反馈*)"},"LAHU02H01_WVB           AT%I66.0       :INT ; (*空调机组NJ-2AP(KT)8-1-水阀反馈*)",null,"AHU02H01_WVB",{"$f":"J78","v":"空调机组NJ-2AP(KT)8-1-水阀反馈"},{"$f":"AS77+1","v":30033}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-2AP(KT)8-2-回风温度",{"$nulls":16},"NJ-2AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-2","02H02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU02H02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%I\"&B78*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU02H02_RT AT%I68.0 :INT ; (*空调机组NJ-2AP(KT)8-2-回风温度*)"},"LAHU02H02_RT            AT%I68.0       :INT ; (*空调机组NJ-2AP(KT)8-2-回风温度*)",null,"AHU02H02_RT","空调机组NJ-2AP(KT)8-2-回风温度",{"$f":"AS78+1","v":30034}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-2AP(KT)8-2-水阀反馈",{"$nulls":16},"NJ-2AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-2","02H02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU02H02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%I\"&B78*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU02H02_WVB AT%I70.0 :INT ; (*空调机组NJ-2AP(KT)8-2-水阀反馈*)"},"LAHU02H02_WVB           AT%I70.0       :INT ; (*空调机组NJ-2AP(KT)8-2-水阀反馈*)",null,"AHU02H02_WVB","空调机组NJ-2AP(KT)8-2-水阀反馈",30035]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-2AP(KT)8-3-回风温度",{"$nulls":16},"NJ-2AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-3","02H03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"AHU02H03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%I\"&B78*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LAHU02H03_RT AT%I72.0 :INT ; (*空调机组NJ-2AP(KT)8-3-回风温度*)"},"LAHU02H03_RT            AT%I72.0       :INT ; (*空调机组NJ-2AP(KT)8-3-回风温度*)",null,"AHU02H03_RT","空调机组NJ-2AP(KT)8-3-回风温度",30036]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-2AP(KT)8-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI82=\"\",\"\",AI82)","v":"NJ-2AP(KT)8-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-3","02H03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":"AHU02H03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%I\"&B78*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":"LAHU02H03_WVB AT%I74.0 :INT ; (*空调机组NJ-2AP(KT)8-3-水阀反馈*)"},"LAHU02H03_WVB           AT%I74.0       :INT ; (*空调机组NJ-2AP(KT)8-3-水阀反馈*)",null,"AHU02H03_WVB",{"$f":"J82","v":"空调机组NJ-2AP(KT)8-3-水阀反馈"},30037]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-2AP(KT)8-4-回风温度",{"$nulls":16},"NJ-2AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-4","02H04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":"AHU02H04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%I\"&B78*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":"LAHU02H04_RT AT%I76.0 :INT ; (*空调机组NJ-2AP(KT)8-4-回风温度*)"},"LAHU02H04_RT            AT%I76.0       :INT ; (*空调机组NJ-2AP(KT)8-4-回风温度*)",null,"AHU02H04_RT","空调机组NJ-2AP(KT)8-4-回风温度",30038]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-2AP(KT)8-4-水阀反馈",{"$nulls":16},"NJ-2AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-4","02H04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH84,List!$B$3:$D$445,2,FALSE)&AJ84&\"_\"&VLOOKUP(AK84,List!$K$2:$M$447,2,FALSE)","v":"AHU02H04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM84&\" \"&\"AT%I\"&B78*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J84&\"*)\",\" \")","v":"LAHU02H04_WVB AT%I78.0 :INT ; (*空调机组NJ-2AP(KT)8-4-水阀反馈*)"},"LAHU02H04_WVB           AT%I78.0       :INT ; (*空调机组NJ-2AP(KT)8-4-水阀反馈*)",null,"AHU02H04_WVB","空调机组NJ-2AP(KT)8-4-水阀反馈",30039]
[null,{"$f":"B90","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B90&\"地址: \"&B87&\" *)\"","v":"(* IOM 0801U地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH86&AA86&\"-\"&AK86","v":"空调机组NJ-2AP(KT)8-5-回风温度"},{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-2AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-5","02H05","回风温度",{"$f":"AH86&\"-\"&AK86","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"AHU02H05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%I\"&B87*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LAHU02H05_RT AT%I80.0 :INT ; (*空调机组NJ-2AP(KT)8-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86))),SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))))),\" \")","v":"LAHU02H05_RT            AT%I80.0       :INT ; (*空调机组NJ-2AP(KT)8-5-回风温度*)"},null,{"$f":"AM86","v":"AHU02H05_RT"},{"$f":"J86","v":"空调机组NJ-2AP(KT)8-5-回风温度"},{"$f":"30000+($B87*8+F86-1)","v":30040}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-2AP(KT)8-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI87=\"\",\"\",AI87)","v":"NJ-2AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-5","02H05","水阀反馈",{"$f":"AH87&\"-\"&AK87","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"AHU02H05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%I\"&B87*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LAHU02H05_WVB AT%I82.0 :INT ; (*空调机组NJ-2AP(KT)8-5-水阀反馈*)"},"LAHU02H05_WVB           AT%I82.0       :INT ; (*空调机组NJ-2AP(KT)8-5-水阀反馈*)",null,"AHU02H05_WVB",{"$f":"J87","v":"空调机组NJ-2AP(KT)8-5-水阀反馈"},{"$f":"AS86+1","v":30041}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-2AP(KT)8-6-回风温度",{"$nulls":16},"NJ-2AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-6","02H06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"AHU02H06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%I\"&B87*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LAHU02H06_RT AT%I84.0 :INT ; (*空调机组NJ-2AP(KT)8-6-回风温度*)"},"LAHU02H06_RT            AT%I84.0       :INT ; (*空调机组NJ-2AP(KT)8-6-回风温度*)",null,"AHU02H06_RT","空调机组NJ-2AP(KT)8-6-回风温度",{"$f":"AS87+1","v":30042}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-2AP(KT)8-6-水阀反馈",{"$nulls":16},"NJ-2AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-6","02H06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"AHU02H06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%I\"&B87*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LAHU02H06_WVB AT%I86.0 :INT ; (*空调机组NJ-2AP(KT)8-6-水阀反馈*)"},"LAHU02H06_WVB           AT%I86.0       :INT ; (*空调机组NJ-2AP(KT)8-6-水阀反馈*)",null,"AHU02H06_WVB","空调机组NJ-2AP(KT)8-6-水阀反馈",30043]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-2AP(KT)8-7-回风温度",{"$nulls":16},"NJ-2AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-7","02H07","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":"AHU02H07_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%I\"&B87*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":"LAHU02H07_RT AT%I88.0 :INT ; (*空调机组NJ-2AP(KT)8-7-回风温度*)"},"LAHU02H07_RT            AT%I88.0       :INT ; (*空调机组NJ-2AP(KT)8-7-回风温度*)",null,"AHU02H07_RT","空调机组NJ-2AP(KT)8-7-回风温度",30044]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-2AP(KT)8-7-水阀反馈",{"$nulls":16},"NJ-2AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-7","02H07","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH91,List!$B$3:$D$445,2,FALSE)&AJ91&\"_\"&VLOOKUP(AK91,List!$K$2:$M$447,2,FALSE)","v":"AHU02H07_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM91&\" \"&\"AT%I\"&B87*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J91&\"*)\",\" \")","v":"LAHU02H07_WVB AT%I90.0 :INT ; (*空调机组NJ-2AP(KT)8-7-水阀反馈*)"},"LAHU02H07_WVB           AT%I90.0       :INT ; (*空调机组NJ-2AP(KT)8-7-水阀反馈*)",null,"AHU02H07_WVB",{"$f":"J91","v":"空调机组NJ-2AP(KT)8-7-水阀反馈"},30045]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-2AP(KT)8-8-回风温度",{"$nulls":16},"NJ-2AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-8","02H08","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH92,List!$B$3:$D$445,2,FALSE)&AJ92&\"_\"&VLOOKUP(AK92,List!$K$2:$M$447,2,FALSE)","v":"AHU02H08_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM92&\" \"&\"AT%I\"&B87*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J92&\"*)\",\" \")","v":"LAHU02H08_RT AT%I92.0 :INT ; (*空调机组NJ-2AP(KT)8-8-回风温度*)"},"LAHU02H08_RT            AT%I92.0       :INT ; (*空调机组NJ-2AP(KT)8-8-回风温度*)",null,"AHU02H08_RT","空调机组NJ-2AP(KT)8-8-回风温度",30046]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-2AP(KT)8-8-水阀反馈",{"$nulls":16},{"$f":"IF(AI93=\"\",\"\",AI93)","v":"NJ-2AP(KT)8-8"},{"$f":"_xlfn.IFNA(VLOOKUP(AL93,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL93,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-8","02H08","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH93,List!$B$3:$D$445,2,FALSE)&AJ93&\"_\"&VLOOKUP(AK93,List!$K$2:$M$447,2,FALSE)","v":"AHU02H08_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM93&\" \"&\"AT%I\"&B87*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J93&\"*)\",\" \")","v":"LAHU02H08_WVB AT%I94.0 :INT ; (*空调机组NJ-2AP(KT)8-8-水阀反馈*)"},"LAHU02H08_WVB           AT%I94.0       :INT ; (*空调机组NJ-2AP(KT)8-8-水阀反馈*)",null,"AHU02H08_WVB","空调机组NJ-2AP(KT)8-8-水阀反馈",30047]
[null,{"$f":"B99","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B99&\"地址: \"&B96&\" *)\"","v":"(* IOM 0401A地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH95&AA95&\"-\"&AK95","v":"空调机组NJ-2AP(KT)8-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-2AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-1","02H01","水阀控制",{"$f":"AH95&\"-\"&AK95","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"AHU02H01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%Q\"&B96*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LAHU02H01_WVC AT%Q96.0 :INT ; (*空调机组NJ-2AP(KT)8-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95))),SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))))),\" \")","v":"LAHU02H01_WVC           AT%Q96.0       :INT ; (*空调机组NJ-2AP(KT)8-1-水阀控制*)"},null,{"$f":"AM95","v":"AHU02H01_WVC"},{"$f":"J95","v":"空调机组NJ-2AP(KT)8-1-水阀控制"},{"$f":"40000+($B96*8+F95-1)","v":40048}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH96&AA96&\"-\"&AK96","v":"空调机组NJ-2AP(KT)8-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI96=\"\",\"\",AI96)","v":"NJ-2AP(KT)8-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-2","02H02","水阀控制",{"$f":"AH96&\"-\"&AK96","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"AHU02H02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%Q\"&B96*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LAHU02H02_WVC AT%Q98.0 :INT ; (*空调机组NJ-2AP(KT)8-2-水阀控制*)"},"LAHU02H02_WVC           AT%Q98.0       :INT ; (*空调机组NJ-2AP(KT)8-2-水阀控制*)",null,"AHU02H02_WVC",{"$f":"J96","v":"空调机组NJ-2AP(KT)8-2-水阀控制"},{"$f":"AS95+1","v":40049}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH97&AA97&\"-\"&AK97","v":"空调机组NJ-2AP(KT)8-3-水阀控制"},{"$nulls":16},"NJ-2AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-3","02H03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":"AHU02H03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%Q\"&B96*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":"LAHU02H03_WVC AT%Q100.0 :INT ; (*空调机组NJ-2AP(KT)8-3-水阀控制*)"},"LAHU02H03_WVC           AT%Q100.0      :INT ; (*空调机组NJ-2AP(KT)8-3-水阀控制*)",null,"AHU02H03_WVC","空调机组NJ-2AP(KT)8-3-水阀控制",{"$f":"AS96+1","v":40050}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH98&AA98&\"-\"&AK98","v":"空调机组NJ-2AP(KT)8-4-水阀控制"},{"$nulls":16},"NJ-2AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-4","02H04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":"AHU02H04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%Q\"&B96*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":"LAHU02H04_WVC AT%Q102.0 :INT ; (*空调机组NJ-2AP(KT)8-4-水阀控制*)"},"LAHU02H04_WVC           AT%Q102.0      :INT ; (*空调机组NJ-2AP(KT)8-4-水阀控制*)",null,"AHU02H04_WVC","空调机组NJ-2AP(KT)8-4-水阀控制",40051]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B108","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B108&\"地址: \"&B105&\" *)\"","v":"(* IOM 0401A地址: 7 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH104&AA104&\"-\"&AK104","v":"空调机组NJ-2AP(KT)8-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI104=\"\",\"\",AI104)","v":"NJ-2AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-5","02H05","水阀控制",{"$f":"AH104&\"-\"&AK104","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"AHU02H05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%Q\"&B105*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LAHU02H05_WVC AT%Q112.0 :INT ; (*空调机组NJ-2AP(KT)8-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104))),SEARCH(\":\",REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104)))))),\" \")","v":"LAHU02H05_WVC           AT%Q112.0      :INT ; (*空调机组NJ-2AP(KT)8-5-水阀控制*)"},null,{"$f":"AM104","v":"AHU02H05_WVC"},{"$f":"J104","v":"空调机组NJ-2AP(KT)8-5-水阀控制"},{"$f":"40000+($B105*8+F104-1)","v":40056}]
[null,7,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH105&AA105&\"-\"&AK105","v":"空调机组NJ-2AP(KT)8-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI105=\"\",\"\",AI105)","v":"NJ-2AP(KT)8-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-6","02H06","水阀控制",{"$f":"AH105&\"-\"&AK105","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"AHU02H06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%Q\"&B105*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LAHU02H06_WVC AT%Q114.0 :INT ; (*空调机组NJ-2AP(KT)8-6-水阀控制*)"},"LAHU02H06_WVC           AT%Q114.0      :INT ; (*空调机组NJ-2AP(KT)8-6-水阀控制*)",null,"AHU02H06_WVC",{"$f":"J105","v":"空调机组NJ-2AP(KT)8-6-水阀控制"},{"$f":"AS104+1","v":40057}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH106&AA106&\"-\"&AK106","v":"空调机组NJ-2AP(KT)8-7-水阀控制"},{"$nulls":16},"NJ-2AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-7","02H07","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":"AHU02H07_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%Q\"&B105*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":"LAHU02H07_WVC AT%Q116.0 :INT ; (*空调机组NJ-2AP(KT)8-7-水阀控制*)"},"LAHU02H07_WVC           AT%Q116.0      :INT ; (*空调机组NJ-2AP(KT)8-7-水阀控制*)",null,"AHU02H07_WVC","空调机组NJ-2AP(KT)8-7-水阀控制",{"$f":"AS105+1","v":40058}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH107&AA107&\"-\"&AK107","v":"空调机组NJ-2AP(KT)8-8-水阀控制"},{"$nulls":16},"NJ-2AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-2AP(KT)8-8","02H08","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH107,List!$B$3:$D$445,2,FALSE)&AJ107&\"_\"&VLOOKUP(AK107,List!$K$2:$M$447,2,FALSE)","v":"AHU02H08_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM107&\" \"&\"AT%Q\"&B105*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J107&\"*)\",\" \")","v":"LAHU02H08_WVC AT%Q118.0 :INT ; (*空调机组NJ-2AP(KT)8-8-水阀控制*)"},"LAHU02H08_WVC           AT%Q118.0      :INT ; (*空调机组NJ-2AP(KT)8-8-水阀控制*)",null,"AHU02H08_WVC","空调机组NJ-2AP(KT)8-8-水阀控制",40059]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L108","index":20,"n_rows":154,"n_cols":45,"rows_kept":154,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[41,5,41,6],[41,9,41,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[75,5,75,6],[75,9,75,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[84,5,84,6],[84,9,84,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[92,5,92,6],[92,9,92,25],[93,5,93,6],[93,9,93,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[101,5,101,6],[101,9,101,25],[102,5,102,6],[102,9,102,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[110,5,110,6],[110,9,110,25],[111,5,111,6],[111,9,111,25],[112,5,112,6],[112,9,112,25],[113,5,113,6],[113,9,113,25],[114,5,114,6],[114,9,114,25],[115,5,115,6],[115,9,115,25],[116,5,116,6],[116,9,116,25],[117,5,117,6],[117,9,117,25],[119,5,119,6],[119,9,119,25],[120,5,120,6],[120,9,120,25],[121,5,121,6],[121,9,121,25],[122,5,122,6],[122,9,122,25],[123,5,123,6],[123,9,123,25],[124,5,124,6],[124,9,124,25],[125,5,125,6],[125,9,125,25],[126,5,126,6],[126,9,126,25],[128,5,128,6],[128,9,128,25],[129,5,129,6],[129,9,129,25],[130,5,130,6],[130,9,130,25],[131,5,131,6],[131,9,131,25],[132,5,132,6],[132,9,132,25],[133,5,133,6],[133,9,133,25],[134,5,134,6],[134,9,134,25],[135,5,135,6],[135,9,135,25],[137,5,137,6],[137,9,137,25],[138,5,138,6],[138,9,138,25],[139,5,139,6],[139,9,139,25],[140,5,140,6],[140,9,140,25],[141,5,141,6],[141,9,141,25],[142,5,142,6],[142,9,142,25],[143,5,143,6],[143,9,143,25],[144,5,144,6],[144,9,144,25],[146,5,146,6],[146,9,146,25],[147,5,147,6],[147,9,147,25],[148,5,148,6],[148,9,148,25],[149,5,149,6],[149,9,149,25],[150,5,150,6],[150,9,150,25],[151,5,151,6],[151,9,151,25],[152,5,152,6],[152,9,152,25],[153,5,153,6],[153,9,153,25],[4,1,5,1],[11,1,22,1],[28,1,39,1],[45,1,56,1],[62,1,73,1],[79,1,90,1],[96,1,99,1],[105,1,108,1],[114,1,117,1],[123,1,126,1],[132,1,135,1],[141,1,144,1],[150,1,153,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4],[32,2,39,4],[49,2,56,4],[66,2,73,4],[83,2,90,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L18",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 8 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH8&AA8&\"-\"&AK8","v":"空调机组NJ-1AP(KT)8-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-1AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-1","01H01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH8,List!$B$3:$D$445,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,List!$K$2:$M$447,2,FALSE)","v":"AHU01H01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LAHU01H01_R AT%I128.0 :BOOL; (*空调机组NJ-1AP(KT)8-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LAHU01H01_R             AT%I128.0      :BOOL; (*空调机组NJ-1AP(KT)8-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L18\\L18AHU01H01_R"},{"$f":"J8","v":"空调机组NJ-1AP(KT)8-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":11024}]
[null,8,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-1AP(KT)8-1-故障状态",{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-1AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-1","01H01","故障状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU01H01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU01H01_F AT%I128.1 :BOOL; (*空调机组NJ-1AP(KT)8-1-故障状态*)"},"LAHU01H01_F             AT%I128.1      :BOOL; (*空调机组NJ-1AP(KT)8-1-故障状态*)",null,"L18\\L18AHU01H01_F",{"$f":"J9","v":"空调机组NJ-1AP(KT)8-1-故障状态"},{"$f":"AS8+1","v":11025}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-1AP(KT)8-1-自动状态",{"$nulls":16},"NJ-1AP(KT)8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-1","01H01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU01H01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU01H01_A AT%I128.2 :BOOL; (*空调机组NJ-1AP(KT)8-1-自动状态*)"},"LAHU01H01_A             AT%I128.2      :BOOL; (*空调机组NJ-1AP(KT)8-1-自动状态*)",null,"L18\\L18AHU01H01_A","空调机组NJ-1AP(KT)8-1-自动状态",{"$f":"AS9+1","v":11026}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-1AP(KT)8-1-风机压差",{"$nulls":16},"NJ-1AP(KT)8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-1","01H01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU01H01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU01H01_FPS AT%I128.3 :BOOL; (*空调机组NJ-1AP(KT)8-1-风机压差*)"},"LAHU01H01_FPS           AT%I128.3      :BOOL; (*空调机组NJ-1AP(KT)8-1-风机压差*)",null,"L18\\L18AHU01H01_FPS","空调机组NJ-1AP(KT)8-1-风机压差",11027]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-1AP(KT)8-2-运行状态",{"$nulls":16},"NJ-1AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-2","01H02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU01H02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU01H02_R AT%I128.4 :BOOL; (*空调机组NJ-1AP(KT)8-2-运行状态*)"},"LAHU01H02_R             AT%I128.4      :BOOL; (*空调机组NJ-1AP(KT)8-2-运行状态*)",null,"L18\\L18AHU01H02_R","空调机组NJ-1AP(KT)8-2-运行状态",11028]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-1AP(KT)8-2-故障状态",{"$nulls":16},"NJ-1AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-2","01H02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU01H02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU01H02_F AT%I128.5 :BOOL; (*空调机组NJ-1AP(KT)8-2-故障状态*)"},"LAHU01H02_F             AT%I128.5      :BOOL; (*空调机组NJ-1AP(KT)8-2-故障状态*)",null,"L18\\L18AHU01H02_F","空调机组NJ-1AP(KT)8-2-故障状态",11029]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-1AP(KT)8-2-自动状态",{"$nulls":16},"NJ-1AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-2","01H02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU01H02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU01H02_A AT%I128.6 :BOOL; (*空调机组NJ-1AP(KT)8-2-自动状态*)"},"LAHU01H02_A             AT%I128.6      :BOOL; (*空调机组NJ-1AP(KT)8-2-自动状态*)",null,"L18\\L18AHU01H02_A","空调机组NJ-1AP(KT)8-2-自动状态",11030]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-1AP(KT)8-2-风机压差",{"$nulls":16},"NJ-1AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-2","01H02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU01H02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU01H02_FPS AT%I128.7 :BOOL; (*空调机组NJ-1AP(KT)8-2-风机压差*)"},"LAHU01H02_FPS           AT%I128.7      :BOOL; (*空调机组NJ-1AP(KT)8-2-风机压差*)",null,"L18\\L18AHU01H02_FPS","空调机组NJ-1AP(KT)8-2-风机压差",11031]
[{"$nulls":5},9,null,17,18,"空调机组NJ-1AP(KT)8-3-运行状态",{"$nulls":16},"NJ-1AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-3","01H03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU01H03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU01H03_R AT%I129.0 :BOOL; (*空调机组NJ-1AP(KT)8-3-运行状态*)"},"LAHU01H03_R             AT%I129.0      :BOOL; (*空调机组NJ-1AP(KT)8-3-运行状态*)",null,"L18\\L18AHU01H03_R","空调机组NJ-1AP(KT)8-3-运行状态",11032]
[{"$nulls":5},10,null,19,20,"空调机组NJ-1AP(KT)8-3-故障状态",{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-1AP(KT)8-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-3","01H03","故障状态",{"$f":"AH17&\"-\"&AK17","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU01H03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU01H03_F AT%I129.1 :BOOL; (*空调机组NJ-1AP(KT)8-3-故障状态*)"},"LAHU01H03_F             AT%I129.1      :BOOL; (*空调机组NJ-1AP(KT)8-3-故障状态*)",null,"L18\\L18AHU01H03_F","空调机组NJ-1AP(KT)8-3-故障状态",11033]
[{"$nulls":5},11,null,21,22,"空调机组NJ-1AP(KT)8-3-自动状态",{"$nulls":16},"NJ-1AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-3","01H03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU01H03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU01H03_A AT%I129.2 :BOOL; (*空调机组NJ-1AP(KT)8-3-自动状态*)"},"LAHU01H03_A             AT%I129.2      :BOOL; (*空调机组NJ-1AP(KT)8-3-自动状态*)",null,"L18\\L18AHU01H03_A","空调机组NJ-1AP(KT)8-3-自动状态",11034]
[{"$nulls":5},12,null,23,24,"空调机组NJ-1AP(KT)8-3-风机压差",{"$nulls":16},"NJ-1AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-3","01H03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU01H03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU01H03_FPS AT%I129.3 :BOOL; (*空调机组NJ-1AP(KT)8-3-风机压差*)"},"LAHU01H03_FPS           AT%I129.3      :BOOL; (*空调机组NJ-1AP(KT)8-3-风机压差*)",null,"L18\\L18AHU01H03_FPS","空调机组NJ-1AP(KT)8-3-风机压差",11035]
[{"$nulls":5},13,null,25,26,"空调机组NJ-1AP(KT)8-4-运行状态",{"$nulls":16},"NJ-1AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-4","01H04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU01H04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU01H04_R AT%I129.4 :BOOL; (*空调机组NJ-1AP(KT)8-4-运行状态*)"},"LAHU01H04_R             AT%I129.4      :BOOL; (*空调机组NJ-1AP(KT)8-4-运行状态*)",null,"L18\\L18AHU01H04_R","空调机组NJ-1AP(KT)8-4-运行状态",11036]
[{"$nulls":5},14,null,27,28,"空调机组NJ-1AP(KT)8-4-故障状态",{"$nulls":16},"NJ-1AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-4","01H04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU01H04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU01H04_F AT%I129.5 :BOOL; (*空调机组NJ-1AP(KT)8-4-故障状态*)"},"LAHU01H04_F             AT%I129.5      :BOOL; (*空调机组NJ-1AP(KT)8-4-故障状态*)",null,"L18\\L18AHU01H04_F","空调机组NJ-1AP(KT)8-4-故障状态",11037]
[{"$nulls":5},15,null,29,30,"空调机组NJ-1AP(KT)8-4-自动状态",{"$nulls":16},"NJ-1AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-4","01H04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU01H04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU01H04_A AT%I129.6 :BOOL; (*空调机组NJ-1AP(KT)8-4-自动状态*)"},"LAHU01H04_A             AT%I129.6      :BOOL; (*空调机组NJ-1AP(KT)8-4-自动状态*)",null,"L18\\L18AHU01H04_A","空调机组NJ-1AP(KT)8-4-自动状态",11038]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-1AP(KT)8-4-风机压差",{"$nulls":16},"NJ-1AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-4","01H04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU01H04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU01H04_FPS AT%I129.7 :BOOL; (*空调机组NJ-1AP(KT)8-4-风机压差*)"},"LAHU01H04_FPS           AT%I129.7      :BOOL; (*空调机组NJ-1AP(KT)8-4-风机压差*)",null,"L18\\L18AHU01H04_FPS","空调机组NJ-1AP(KT)8-4-风机压差",11039]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 1601R地址: 9 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH25&AA25&\"-\"&AK25","v":"空调机组NJ-1AP(KT)8-5-运行状态"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-1AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-5","01H05","运行状态",{"$f":"AH25&\"-\"&AK25","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"AHU01H05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LAHU01H05_R AT%I144.0 :BOOL; (*空调机组NJ-1AP(KT)8-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LAHU01H05_R             AT%I144.0      :BOOL; (*空调机组NJ-1AP(KT)8-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L18\\L18AHU01H05_R"},{"$f":"J25","v":"空调机组NJ-1AP(KT)8-5-运行状态"},{"$f":"10000+($B26*16*8+F25-1)","v":11152}]
[null,9,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-1AP(KT)8-5-故障状态",{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-1AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-5","01H05","故障状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU01H05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU01H05_F AT%I144.1 :BOOL; (*空调机组NJ-1AP(KT)8-5-故障状态*)"},"LAHU01H05_F             AT%I144.1      :BOOL; (*空调机组NJ-1AP(KT)8-5-故障状态*)",null,"L18\\L18AHU01H05_F",{"$f":"J26","v":"空调机组NJ-1AP(KT)8-5-故障状态"},{"$f":"AS25+1","v":11153}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-1AP(KT)8-5-自动状态",{"$nulls":16},"NJ-1AP(KT)8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-5","01H05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU01H05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU01H05_A AT%I144.2 :BOOL; (*空调机组NJ-1AP(KT)8-5-自动状态*)"},"LAHU01H05_A             AT%I144.2      :BOOL; (*空调机组NJ-1AP(KT)8-5-自动状态*)",null,"L18\\L18AHU01H05_A","空调机组NJ-1AP(KT)8-5-自动状态",{"$f":"AS26+1","v":11154}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-1AP(KT)8-5-风机压差",{"$nulls":16},"NJ-1AP(KT)8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-5","01H05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU01H05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU01H05_FPS AT%I144.3 :BOOL; (*空调机组NJ-1AP(KT)8-5-风机压差*)"},"LAHU01H05_FPS           AT%I144.3      :BOOL; (*空调机组NJ-1AP(KT)8-5-风机压差*)",null,"L18\\L18AHU01H05_FPS","空调机组NJ-1AP(KT)8-5-风机压差",11155]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-1AP(KT)8-6-运行状态",{"$nulls":16},"NJ-1AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-6","01H06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU01H06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU01H06_R AT%I144.4 :BOOL; (*空调机组NJ-1AP(KT)8-6-运行状态*)"},"LAHU01H06_R             AT%I144.4      :BOOL; (*空调机组NJ-1AP(KT)8-6-运行状态*)",null,"L18\\L18AHU01H06_R","空调机组NJ-1AP(KT)8-6-运行状态",11156]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-1AP(KT)8-6-故障状态",{"$nulls":16},"NJ-1AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-6","01H06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU01H06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU01H06_F AT%I144.5 :BOOL; (*空调机组NJ-1AP(KT)8-6-故障状态*)"},"LAHU01H06_F             AT%I144.5      :BOOL; (*空调机组NJ-1AP(KT)8-6-故障状态*)",null,"L18\\L18AHU01H06_F","空调机组NJ-1AP(KT)8-6-故障状态",11157]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-1AP(KT)8-6-自动状态",{"$nulls":16},"NJ-1AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-6","01H06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU01H06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU01H06_A AT%I144.6 :BOOL; (*空调机组NJ-1AP(KT)8-6-自动状态*)"},"LAHU01H06_A             AT%I144.6      :BOOL; (*空调机组NJ-1AP(KT)8-6-自动状态*)",null,"L18\\L18AHU01H06_A","空调机组NJ-1AP(KT)8-6-自动状态",11158]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-1AP(KT)8-6-风机压差",{"$nulls":16},"NJ-1AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-6","01H06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU01H06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU01H06_FPS AT%I144.7 :BOOL; (*空调机组NJ-1AP(KT)8-6-风机压差*)"},"LAHU01H06_FPS           AT%I144.7      :BOOL; (*空调机组NJ-1AP(KT)8-6-风机压差*)",null,"L18\\L18AHU01H06_FPS","空调机组NJ-1AP(KT)8-6-风机压差",11159]
[{"$nulls":5},9,null,17,18,"空调机组NJ-1AP(KT)8-7-运行状态",{"$nulls":16},"NJ-1AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-7","01H07","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU01H07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B26*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU01H07_R AT%I145.0 :BOOL; (*空调机组NJ-1AP(KT)8-7-运行状态*)"},"LAHU01H07_R             AT%I145.0      :BOOL; (*空调机组NJ-1AP(KT)8-7-运行状态*)",null,"L18\\L18AHU01H07_R","空调机组NJ-1AP(KT)8-7-运行状态",11160]
[{"$nulls":5},10,null,19,20,"空调机组NJ-1AP(KT)8-7-故障状态",{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-1AP(KT)8-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-7","01H07","故障状态",{"$f":"AH34&\"-\"&AK34","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU01H07_F"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B26*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU01H07_F AT%I145.1 :BOOL; (*空调机组NJ-1AP(KT)8-7-故障状态*)"},"LAHU01H07_F             AT%I145.1      :BOOL; (*空调机组NJ-1AP(KT)8-7-故障状态*)",null,"L18\\L18AHU01H07_F","空调机组NJ-1AP(KT)8-7-故障状态",11161]
[{"$nulls":5},11,null,21,22,"空调机组NJ-1AP(KT)8-7-自动状态",{"$nulls":16},"NJ-1AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-7","01H07","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU01H07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B26*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU01H07_A AT%I145.2 :BOOL; (*空调机组NJ-1AP(KT)8-7-自动状态*)"},"LAHU01H07_A             AT%I145.2      :BOOL; (*空调机组NJ-1AP(KT)8-7-自动状态*)",null,"L18\\L18AHU01H07_A","空调机组NJ-1AP(KT)8-7-自动状态",11162]
[{"$nulls":5},12,null,23,24,"空调机组NJ-1AP(KT)8-7-风机压差",{"$nulls":16},"NJ-1AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-7","01H07","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU01H07_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B26*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU01H07_FPS AT%I145.3 :BOOL; (*空调机组NJ-1AP(KT)8-7-风机压差*)"},"LAHU01H07_FPS           AT%I145.3      :BOOL; (*空调机组NJ-1AP(KT)8-7-风机压差*)",null,"L18\\L18AHU01H07_FPS","空调机组NJ-1AP(KT)8-7-风机压差",11163]
[{"$nulls":5},13,null,25,26,"空调机组NJ-1AP(KT)8-8-运行状态",{"$nulls":16},"NJ-1AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-8","01H08","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"AHU01H08_R"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B26*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LAHU01H08_R AT%I145.4 :BOOL; (*空调机组NJ-1AP(KT)8-8-运行状态*)"},"LAHU01H08_R             AT%I145.4      :BOOL; (*空调机组NJ-1AP(KT)8-8-运行状态*)",null,"L18\\L18AHU01H08_R","空调机组NJ-1AP(KT)8-8-运行状态",11164]
[{"$nulls":5},14,null,27,28,"空调机组NJ-1AP(KT)8-8-故障状态",{"$nulls":16},"NJ-1AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-8","01H08","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"AHU01H08_F"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B26*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LAHU01H08_F AT%I145.5 :BOOL; (*空调机组NJ-1AP(KT)8-8-故障状态*)"},"LAHU01H08_F             AT%I145.5      :BOOL; (*空调机组NJ-1AP(KT)8-8-故障状态*)",null,"L18\\L18AHU01H08_F","空调机组NJ-1AP(KT)8-8-故障状态",11165]
[{"$nulls":5},15,null,29,30,"空调机组NJ-1AP(KT)8-8-自动状态",{"$nulls":16},"NJ-1AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-8","01H08","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"AHU01H08_A"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B26*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LAHU01H08_A AT%I145.6 :BOOL; (*空调机组NJ-1AP(KT)8-8-自动状态*)"},"LAHU01H08_A             AT%I145.6      :BOOL; (*空调机组NJ-1AP(KT)8-8-自动状态*)",null,"L18\\L18AHU01H08_A","空调机组NJ-1AP(KT)8-8-自动状态",11166]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-1AP(KT)8-8-风机压差",{"$nulls":16},"NJ-1AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-8","01H08","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"AHU01H08_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B26*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LAHU01H08_FPS AT%I145.7 :BOOL; (*空调机组NJ-1AP(KT)8-8-风机压差*)"},"LAHU01H08_FPS           AT%I145.7      :BOOL; (*空调机组NJ-1AP(KT)8-8-风机压差*)",null,"L18\\L18AHU01H08_FPS","空调机组NJ-1AP(KT)8-8-风机压差",11167]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B46&\"地址: \"&B43&\" *)\"","v":"(* IOM 1601R地址: 10 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH42&AA42&\"-\"&AK42","v":"空调机组NJ-1AP(KT)8-9-运行状态"},{"$nulls":16},{"$f":"IF(AI42=\"\",\"\",AI42)","v":"NJ-1AP(KT)8-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-9","01H09","运行状态",{"$f":"AH42&\"-\"&AK42","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":"AHU01H09_R"},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%I\"&B43*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":"LAHU01H09_R AT%I160.0 :BOOL; (*空调机组NJ-1AP(KT)8-9-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42))),SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))))),\" \")","v":"LAHU01H09_R             AT%I160.0      :BOOL; (*空调机组NJ-1AP(KT)8-9-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM42","v":"L18\\L18AHU01H09_R"},{"$f":"J42","v":"空调机组NJ-1AP(KT)8-9-运行状态"},{"$f":"10000+($B43*16*8+F42-1)","v":11280}]
[null,10,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},2,null,3,4,"空调机组NJ-1AP(KT)8-9-故障状态",{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-1AP(KT)8-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-9","01H09","故障状态",{"$f":"AH43&\"-\"&AK43","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"AHU01H09_F"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B43*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LAHU01H09_F AT%I160.1 :BOOL; (*空调机组NJ-1AP(KT)8-9-故障状态*)"},"LAHU01H09_F             AT%I160.1      :BOOL; (*空调机组NJ-1AP(KT)8-9-故障状态*)",null,"L18\\L18AHU01H09_F",{"$f":"J43","v":"空调机组NJ-1AP(KT)8-9-故障状态"},{"$f":"AS42+1","v":11281}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-1AP(KT)8-9-自动状态",{"$nulls":16},"NJ-1AP(KT)8-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-9","01H09","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"AHU01H09_A"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B43*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LAHU01H09_A AT%I160.2 :BOOL; (*空调机组NJ-1AP(KT)8-9-自动状态*)"},"LAHU01H09_A             AT%I160.2      :BOOL; (*空调机组NJ-1AP(KT)8-9-自动状态*)",null,"L18\\L18AHU01H09_A","空调机组NJ-1AP(KT)8-9-自动状态",{"$f":"AS43+1","v":11282}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-1AP(KT)8-9-风机压差",{"$nulls":16},"NJ-1AP(KT)8-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-9","01H09","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"AHU01H09_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B43*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LAHU01H09_FPS AT%I160.3 :BOOL; (*空调机组NJ-1AP(KT)8-9-风机压差*)"},"LAHU01H09_FPS           AT%I160.3      :BOOL; (*空调机组NJ-1AP(KT)8-9-风机压差*)",null,"L18\\L18AHU01H09_FPS","空调机组NJ-1AP(KT)8-9-风机压差",11283]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-1AP(KT)8-10-运行状态",{"$nulls":16},"NJ-1AP(KT)8-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-10","01H10","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"AHU01H10_R"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B43*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LAHU01H10_R AT%I160.4 :BOOL; (*空调机组NJ-1AP(KT)8-10-运行状态*)"},"LAHU01H10_R             AT%I160.4      :BOOL; (*空调机组NJ-1AP(KT)8-10-运行状态*)",null,"L18\\L18AHU01H10_R","空调机组NJ-1AP(KT)8-10-运行状态",11284]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-1AP(KT)8-10-故障状态",{"$nulls":16},"NJ-1AP(KT)8-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-10","01H10","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"AHU01H10_F"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B43*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LAHU01H10_F AT%I160.5 :BOOL; (*空调机组NJ-1AP(KT)8-10-故障状态*)"},"LAHU01H10_F             AT%I160.5      :BOOL; (*空调机组NJ-1AP(KT)8-10-故障状态*)",null,"L18\\L18AHU01H10_F","空调机组NJ-1AP(KT)8-10-故障状态",11285]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-1AP(KT)8-10-自动状态",{"$nulls":16},"NJ-1AP(KT)8-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-10","01H10","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"AHU01H10_A"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B43*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LAHU01H10_A AT%I160.6 :BOOL; (*空调机组NJ-1AP(KT)8-10-自动状态*)"},"LAHU01H10_A             AT%I160.6      :BOOL; (*空调机组NJ-1AP(KT)8-10-自动状态*)",null,"L18\\L18AHU01H10_A","空调机组NJ-1AP(KT)8-10-自动状态",11286]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-1AP(KT)8-10-风机压差",{"$nulls":16},"NJ-1AP(KT)8-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-10","01H10","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"AHU01H10_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B43*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LAHU01H10_FPS AT%I160.7 :BOOL; (*空调机组NJ-1AP(KT)8-10-风机压差*)"},"LAHU01H10_FPS           AT%I160.7      :BOOL; (*空调机组NJ-1AP(KT)8-10-风机压差*)",null,"L18\\L18AHU01H10_FPS","空调机组NJ-1AP(KT)8-10-风机压差",11287]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-1AL8-1-运行状态",{"$nulls":16},"NJ-1AL8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-1AL8-1","01H01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"LCB01H01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B43*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LLCB01H01_R AT%I161.0 :BOOL; (*照明控制箱NJ-1AL8-1-运行状态*)"},"LLCB01H01_R             AT%I161.0      :BOOL; (*照明控制箱NJ-1AL8-1-运行状态*)",null,"L18\\L18LCB01H01_R","照明控制箱NJ-1AL8-1-运行状态",11288]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-1AL8-1-自动状态",{"$nulls":16},{"$f":"IF(AI51=\"\",\"\",AI51)","v":"NJ-1AL8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-1AL8-1","01H01","自动状态",{"$f":"AH51&\"-\"&AK51","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"LCB01H01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B43*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LLCB01H01_A AT%I161.1 :BOOL; (*照明控制箱NJ-1AL8-1-自动状态*)"},"LLCB01H01_A             AT%I161.1      :BOOL; (*照明控制箱NJ-1AL8-1-自动状态*)",null,"L18\\L18LCB01H01_A",{"$f":"J51","v":"照明控制箱NJ-1AL8-1-自动状态"},11289]
[{"$nulls":5},11,null,21,22,"照明控制箱NJ-1AL8-2-运行状态",{"$nulls":16},"NJ-1AL8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL8-2","01H02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"LCB01H02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%I\"&B43*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LLCB01H02_R AT%I161.2 :BOOL; (*照明控制箱NJ-1AL8-2-运行状态*)"},"LLCB01H02_R             AT%I161.2      :BOOL; (*照明控制箱NJ-1AL8-2-运行状态*)",null,"L18\\L18LCB01H02_R","照明控制箱NJ-1AL8-2-运行状态",11290]
[{"$nulls":5},12,null,23,24,"照明控制箱NJ-1AL8-2-自动状态",{"$nulls":16},"NJ-1AL8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL8-2","01H02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"LCB01H02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%I\"&B43*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LLCB01H02_A AT%I161.3 :BOOL; (*照明控制箱NJ-1AL8-2-自动状态*)"},"LLCB01H02_A             AT%I161.3      :BOOL; (*照明控制箱NJ-1AL8-2-自动状态*)",null,"L18\\L18LCB01H02_A","照明控制箱NJ-1AL8-2-自动状态",11291]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-1AL8-3-运行状态",{"$nulls":16},"NJ-1AL8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL8-3","01H03","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"LCB01H03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%I\"&B43*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LLCB01H03_R AT%I161.4 :BOOL; (*照明控制箱NJ-1AL8-3-运行状态*)"},"LLCB01H03_R             AT%I161.4      :BOOL; (*照明控制箱NJ-1AL8-3-运行状态*)",null,"L18\\L18LCB01H03_R","照明控制箱NJ-1AL8-3-运行状态",11292]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-1AL8-3-自动状态",{"$nulls":16},"NJ-1AL8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL8-3","01H03","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"LCB01H03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%I\"&B43*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LLCB01H03_A AT%I161.5 :BOOL; (*照明控制箱NJ-1AL8-3-自动状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN55,SEARCH(\"AT%\",AN55),,REPT(\" \",30-SEARCH(\"AT%\",AN55))),SEARCH(\":\",REPLACE(AN55,SEARCH(\"AT%\",AN55),,REPT(\" \",30-SEARCH(\"AT%\",AN55)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN55,SEARCH(\"AT%\",AN55),,REPT(\" \",25-SEARCH(\"AT%\",AN55)))))),\" \")","v":"LLCB01H03_A                  AT%I161.5 :BOOL; (*照明控制箱NJ-1AL8-3-自动状态*)"},null,"L18\\L18LCB01H03_A","照明控制箱NJ-1AL8-3-自动状态",11293]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-1AL8-4-运行状态",{"$nulls":16},"NJ-1AL8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL8-4","01H04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"LCB01H04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%I\"&B43*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LLCB01H04_R AT%I161.6 :BOOL; (*照明控制箱NJ-1AL8-4-运行状态*)"},"LLCB01H04_R                  AT%I161.6 :BOOL; (*照明控制箱NJ-1AL8-4-运行状态*)",null,"L18\\L18LCB01H04_R","照明控制箱NJ-1AL8-4-运行状态",11294]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-1AL8-4-自动状态",{"$nulls":16},"NJ-1AL8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL8-4","01H04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"LCB01H04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%I\"&B43*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LLCB01H04_A AT%I161.7 :BOOL; (*照明控制箱NJ-1AL8-4-自动状态*)"},"LLCB01H04_A                  AT%I161.7 :BOOL; (*照明控制箱NJ-1AL8-4-自动状态*)",null,"L18\\L18LCB01H04_A","照明控制箱NJ-1AL8-4-自动状态",11295]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B63&\"地址: \"&B60&\" *)\"","v":"(* IOM 1601R地址: 11 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH59&AA59&\"-\"&AK59","v":"照明控制箱NJ-1AL8-5-运行状态"},{"$nulls":16},{"$f":"IF(AI59=\"\",\"\",AI59)","v":"NJ-1AL8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL8-5","01H05","运行状态",{"$f":"AH59&\"-\"&AK59","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH59,List!$B$3:$D$445,2,FALSE)&AJ59&\"_\"&VLOOKUP(AK59,List!$K$2:$M$447,2,FALSE)","v":"LCB01H05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM59&\" \"&\"AT%I\"&B60*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J59&\"*)\",\" \")","v":"LLCB01H05_R AT%I176.0 :BOOL; (*照明控制箱NJ-1AL8-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59))),SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))))),\" \")","v":"LLCB01H05_R             AT%I176.0      :BOOL; (*照明控制箱NJ-1AL8-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM59","v":"L18\\L18LCB01H05_R"},{"$f":"J59","v":"照明控制箱NJ-1AL8-5-运行状态"},{"$f":"10000+($B60*16*8+F59-1)","v":11408}]
[null,11,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":1},2,null,3,4,"照明控制箱NJ-1AL8-5-自动状态",{"$nulls":16},"NJ-1AL8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL8-5","01H05","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"LCB01H05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%I\"&B60*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LLCB01H05_A AT%I176.1 :BOOL; (*照明控制箱NJ-1AL8-5-自动状态*)"},"LLCB01H05_A             AT%I176.1      :BOOL; (*照明控制箱NJ-1AL8-5-自动状态*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM60","v":"L18\\L18LCB01H05_A"},"照明控制箱NJ-1AL8-5-自动状态",{"$f":"AS59+1","v":11409}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":0},3,null,5,6,"风机盘管NJ-1AP(KT)8-运行状态",{"$nulls":16},"NJ-1AP(KT)8",{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)8","01H01","运行状态","风机盘管-运行状态",{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"FCU01H01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%I\"&B60*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LFCU01H01_R AT%I176.2 :BOOL; (*风机盘管NJ-1AP(KT)8-运行状态*)"},"LFCU01H01_R             AT%I176.2      :BOOL; (*风机盘管NJ-1AP(KT)8-运行状态*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM61","v":"L18\\L18FCU01H01_R"},"风机盘管NJ-1AP(KT)8-运行状态",11410]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},4,null,7,8,"风机盘管NJ-1AP(KT)8-自动状态",{"$nulls":16},"NJ-1AP(KT)8",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)8","01H01","自动状态","风机盘管-自动状态",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"FCU01H01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B60*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LFCU01H01_A AT%I176.3 :BOOL; (*风机盘管NJ-1AP(KT)8-自动状态*)"},"LFCU01H01_A             AT%I176.3      :BOOL; (*风机盘管NJ-1AP(KT)8-自动状态*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM62","v":"L18\\L18FCU01H01_A"},"风机盘管NJ-1AP(KT)8-自动状态",11411]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},5,null,9,10,"风机盘管电磁阀NJ-1AP(KT)8-电磁阀开启状态",{"$nulls":16},"NJ-1AP(KT)8",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管电磁阀","NJ-1AP(KT)8","01H01","电磁阀开启状态","风机盘管电磁阀-电磁阀开启状态",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"FCUV01H01_EVR"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B60*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LFCUV01H01_EVR AT%I176.4 :BOOL; (*风机盘管电磁阀NJ-1AP(KT)8-电磁阀开启状态*)"},"LFCUV01H01_EVR          AT%I176.4      :BOOL; (*风机盘管电磁阀NJ-1AP(KT)8-电磁阀开启状态*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM63","v":"L18\\L18FCUV01H01_EVR"},"风机盘管电磁阀NJ-1AP(KT)8-电磁阀开启状态",11412]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"风机盘管电磁阀NJ-1AP(KT)8-电磁阀自动状态",{"$nulls":16},"NJ-1AP(KT)8",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管电磁阀","NJ-1AP(KT)8","01H01","电磁阀自动状态","风机盘管电磁阀-电磁阀自动状态",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"FCUV01H01_EVA"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B60*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LFCUV01H01_EVA AT%I176.5 :BOOL; (*风机盘管电磁阀NJ-1AP(KT)8-电磁阀自动状态*)"},"LFCUV01H01_EVA          AT%I176.5      :BOOL; (*风机盘管电磁阀NJ-1AP(KT)8-电磁阀自动状态*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM64","v":"L18\\L18FCUV01H01_EVA"},"风机盘管电磁阀NJ-1AP(KT)8-电磁阀自动状态",11413]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B60*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM65","v":{"$error":"#N/A"}},"-",11414]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B60*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM66","v":{"$error":"#N/A"}},"-",11415]
[{"$nulls":5},9,null,17,18,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%I\"&B60*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM67","v":{"$error":"#N/A"}},"-",11416]
[{"$nulls":5},10,null,19,20,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%I\"&B60*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM68","v":{"$error":"#N/A"}},"-",11417]
[{"$nulls":5},11,null,21,22,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%I\"&B60*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM69","v":{"$error":"#N/A"}},"-",11418]
[{"$nulls":5},12,null,23,24,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%I\"&B60*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM70","v":{"$error":"#N/A"}},"-",11419]
[{"$nulls":5},13,null,25,26,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%I\"&B60*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM71","v":{"$error":"#N/A"}},"-",11420]
[{"$nulls":5},14,null,27,28,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%I\"&B60*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN72,SEARCH(\"AT%\",AN72),,REPT(\" \",30-SEARCH(\"AT%\",AN72))),SEARCH(\":\",REPLACE(AN72,SEARCH(\"AT%\",AN72),,REPT(\" \",30-SEARCH(\"AT%\",AN72)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN72,SEARCH(\"AT%\",AN72),,REPT(\" \",25-SEARCH(\"AT%\",AN72)))))),\" \")","v":" "},null,{"$f":"$B$2&\"\\\"&$B$2&AM72","v":{"$error":"#N/A"}},"-",11421]
[{"$nulls":5},15,null,29,30,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%I\"&B60*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM73","v":{"$error":"#N/A"}},"-",11422]
[".",{"$nulls":4},16,null,31,32,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%I\"&B60*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM74","v":{"$error":"#N/A"}},"-",11423]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B80&\"地址: \"&B77&\" *)\"","v":"(* IOM 1601D地址: 12 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH76&AA76&\"-\"&AK76","v":"空调机组NJ-1AP(KT)8-1-启停控制"},{"$nulls":16},{"$f":"IF(AI76=\"\",\"\",AI76)","v":"NJ-1AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-1","01H01","启停控制",{"$f":"AH76&\"-\"&AK76","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH76,List!$B$3:$D$445,2,FALSE)&AJ76&\"_\"&VLOOKUP(AK76,List!$K$2:$M$447,2,FALSE)","v":"AHU01H01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM76&\" \"&\"AT%Q\"&B77*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J76&\"*)\",\" \")","v":"LAHU01H01_C AT%Q192.0 :BOOL; (*空调机组NJ-1AP(KT)8-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN76,SEARCH(\"AT%\",AN76),,REPT(\" \",25-SEARCH(\"AT%\",AN76))),SEARCH(\":\",REPLACE(AN76,SEARCH(\"AT%\",AN76),,REPT(\" \",25-SEARCH(\"AT%\",AN76)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN76,SEARCH(\"AT%\",AN76),,REPT(\" \",25-SEARCH(\"AT%\",AN76)))))),\" \")","v":"LAHU01H01_C             AT%Q192.0      :BOOL; (*空调机组NJ-1AP(KT)8-1-启停控制*)"},null,{"$f":"AM76","v":"AHU01H01_C"},{"$f":"J76","v":"空调机组NJ-1AP(KT)8-1-启停控制"},{"$f":"($B77*16*8+F76-1)","v":1536}]
[null,12,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","空调机组NJ-1AP(KT)8-2-启停控制",{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-1AP(KT)8-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-2","01H02","启停控制",{"$f":"AH77&\"-\"&AK77","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"AHU01H02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%Q\"&B77*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LAHU01H02_C AT%Q192.1 :BOOL; (*空调机组NJ-1AP(KT)8-2-启停控制*)"},"LAHU01H02_C             AT%Q192.1      :BOOL; (*空调机组NJ-1AP(KT)8-2-启停控制*)",null,"AHU01H02_C",{"$f":"J77","v":"空调机组NJ-1AP(KT)8-2-启停控制"},{"$f":"AS76+1","v":1537}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-1AP(KT)8-3-启停控制",{"$nulls":16},"NJ-1AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-3","01H03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU01H03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B77*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU01H03_C AT%Q192.2 :BOOL; (*空调机组NJ-1AP(KT)8-3-启停控制*)"},"LAHU01H03_C             AT%Q192.2      :BOOL; (*空调机组NJ-1AP(KT)8-3-启停控制*)",null,"AHU01H03_C","空调机组NJ-1AP(KT)8-3-启停控制",{"$f":"AS77+1","v":1538}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","空调机组NJ-1AP(KT)8-4-启停控制",{"$nulls":16},"NJ-1AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-4","01H04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU01H04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B77*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU01H04_C AT%Q192.3 :BOOL; (*空调机组NJ-1AP(KT)8-4-启停控制*)"},"LAHU01H04_C             AT%Q192.3      :BOOL; (*空调机组NJ-1AP(KT)8-4-启停控制*)",null,"AHU01H04_C","空调机组NJ-1AP(KT)8-4-启停控制",1539]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-1AP(KT)8-5-启停控制",{"$nulls":16},"NJ-1AP(KT)8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-5","01H05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU01H05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B77*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU01H05_C AT%Q192.4 :BOOL; (*空调机组NJ-1AP(KT)8-5-启停控制*)"},"LAHU01H05_C             AT%Q192.4      :BOOL; (*空调机组NJ-1AP(KT)8-5-启停控制*)",null,"AHU01H05_C","空调机组NJ-1AP(KT)8-5-启停控制",1540]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-1AP(KT)8-6-启停控制",{"$nulls":16},"NJ-1AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-6","01H06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"AHU01H06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%Q\"&B77*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LAHU01H06_C AT%Q192.5 :BOOL; (*空调机组NJ-1AP(KT)8-6-启停控制*)"},"LAHU01H06_C             AT%Q192.5      :BOOL; (*空调机组NJ-1AP(KT)8-6-启停控制*)",null,"AHU01H06_C","空调机组NJ-1AP(KT)8-6-启停控制",1541]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","空调机组NJ-1AP(KT)8-7-启停控制",{"$nulls":16},"NJ-1AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-7","01H07","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":"AHU01H07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%Q\"&B77*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":"LAHU01H07_C AT%Q192.6 :BOOL; (*空调机组NJ-1AP(KT)8-7-启停控制*)"},"LAHU01H07_C             AT%Q192.6      :BOOL; (*空调机组NJ-1AP(KT)8-7-启停控制*)",null,"AHU01H07_C","空调机组NJ-1AP(KT)8-7-启停控制",1542]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","空调机组NJ-1AP(KT)8-8-启停控制",{"$nulls":16},"NJ-1AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-8","01H08","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":"AHU01H08_C"},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%Q\"&B77*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":"LAHU01H08_C AT%Q192.7 :BOOL; (*空调机组NJ-1AP(KT)8-8-启停控制*)"},"LAHU01H08_C             AT%Q192.7      :BOOL; (*空调机组NJ-1AP(KT)8-8-启停控制*)",null,"AHU01H08_C","空调机组NJ-1AP(KT)8-8-启停控制",1543]
[{"$nulls":5},9,null,"9+","9-","空调机组NJ-1AP(KT)8-9-启停控制",{"$nulls":16},"NJ-1AP(KT)8-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-9","01H09","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH84,List!$B$3:$D$445,2,FALSE)&AJ84&\"_\"&VLOOKUP(AK84,List!$K$2:$M$447,2,FALSE)","v":"AHU01H09_C"},{"$f":"_xlfn.IFNA(\"L\"&AM84&\" \"&\"AT%Q\"&B77*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J84&\"*)\",\" \")","v":"LAHU01H09_C AT%Q193.0 :BOOL; (*空调机组NJ-1AP(KT)8-9-启停控制*)"},"LAHU01H09_C             AT%Q193.0      :BOOL; (*空调机组NJ-1AP(KT)8-9-启停控制*)",null,"AHU01H09_C","空调机组NJ-1AP(KT)8-9-启停控制",1544]
[{"$nulls":5},10,null,"10+","10-","空调机组NJ-1AP(KT)8-10-启停控制",{"$nulls":16},{"$f":"IF(AI85=\"\",\"\",AI85)","v":"NJ-1AP(KT)8-10"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-1AP(KT)8-10","01H10","启停控制",{"$f":"AH85&\"-\"&AK85","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH85,List!$B$3:$D$445,2,FALSE)&AJ85&\"_\"&VLOOKUP(AK85,List!$K$2:$M$447,2,FALSE)","v":"AHU01H10_C"},{"$f":"_xlfn.IFNA(\"L\"&AM85&\" \"&\"AT%Q\"&B77*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J85&\"*)\",\" \")","v":"LAHU01H10_C AT%Q193.1 :BOOL; (*空调机组NJ-1AP(KT)8-10-启停控制*)"},"LAHU01H10_C             AT%Q193.1      :BOOL; (*空调机组NJ-1AP(KT)8-10-启停控制*)",null,"AHU01H10_C",{"$f":"J85","v":"空调机组NJ-1AP(KT)8-10-启停控制"},1545]
[{"$nulls":5},11,null,"11+","11-","照明控制箱NJ-1AL8-1-启停控制",{"$nulls":16},"NJ-1AL8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-1AL8-1","01H01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"LCB01H01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%Q\"&B77*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LLCB01H01_C AT%Q193.2 :BOOL; (*照明控制箱NJ-1AL8-1-启停控制*)"},"LLCB01H01_C             AT%Q193.2      :BOOL; (*照明控制箱NJ-1AL8-1-启停控制*)",null,"LCB01H01_C","照明控制箱NJ-1AL8-1-启停控制",1546]
[{"$nulls":5},12,null,"12+","12-","照明控制箱NJ-1AL8-2-启停控制",{"$nulls":16},"NJ-1AL8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL8-2","01H02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"LCB01H02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%Q\"&B77*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LLCB01H02_C AT%Q193.3 :BOOL; (*照明控制箱NJ-1AL8-2-启停控制*)"},"LLCB01H02_C             AT%Q193.3      :BOOL; (*照明控制箱NJ-1AL8-2-启停控制*)",null,"LCB01H02_C","照明控制箱NJ-1AL8-2-启停控制",1547]
[{"$nulls":5},13,null,"13+","13-","照明控制箱NJ-1AL8-3-启停控制",{"$nulls":16},"NJ-1AL8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL8-3","01H03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"LCB01H03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%Q\"&B77*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LLCB01H03_C AT%Q193.4 :BOOL; (*照明控制箱NJ-1AL8-3-启停控制*)"},"LLCB01H03_C             AT%Q193.4      :BOOL; (*照明控制箱NJ-1AL8-3-启停控制*)",null,"LCB01H03_C","照明控制箱NJ-1AL8-3-启停控制",1548]
[{"$nulls":5},14,null,"14+","14-","照明控制箱NJ-1AL8-4-启停控制",{"$nulls":16},"NJ-1AL8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL8-4","01H04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"LCB01H04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%Q\"&B77*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LLCB01H04_C AT%Q193.5 :BOOL; (*照明控制箱NJ-1AL8-4-启停控制*)"},"LLCB01H04_C             AT%Q193.5      :BOOL; (*照明控制箱NJ-1AL8-4-启停控制*)",null,"LCB01H04_C","照明控制箱NJ-1AL8-4-启停控制",1549]
[{"$nulls":5},15,null,"15+","15-","照明控制箱NJ-1AL8-5-启停控制",{"$nulls":16},"NJ-1AL8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-1AL8-5","01H05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":"LCB01H05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%Q\"&B77*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":"LLCB01H05_C AT%Q193.6 :BOOL; (*照明控制箱NJ-1AL8-5-启停控制*)"},"LLCB01H05_C             AT%Q193.6      :BOOL; (*照明控制箱NJ-1AL8-5-启停控制*)",null,"LCB01H05_C","照明控制箱NJ-1AL8-5-启停控制",1550]
[".",{"$nulls":4},16,null,"16+","16-","风机盘管NJ-1AP(KT)8-启停控制",{"$nulls":16},"NJ-1AP(KT)8",{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)8","01H01","启停控制","风机盘管-启停控制",{"$f":"VLOOKUP(AH91,List!$B$3:$D$445,2,FALSE)&AJ91&\"_\"&VLOOKUP(AK91,List!$K$2:$M$447,2,FALSE)","v":"FCU01H01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM91&\" \"&\"AT%Q\"&B77*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J91&\"*)\",\" \")","v":"LFCU01H01_C AT%Q193.7 :BOOL; (*风机盘管NJ-1AP(KT)8-启停控制*)"},"LFCU01H01_C             AT%Q193.7      :BOOL; (*风机盘管NJ-1AP(KT)8-启停控制*)",null,"FCU01H01_C","风机盘管NJ-1AP(KT)8-启停控制",1551]
[null,"IOM 0801D",{"$nulls":38},{"$f":"\"(* \"&B97&\"地址: \"&B94&\" *)\"","v":"(* IOM 0801D地址: 13 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH93&AA93&\"-\"&AK93","v":"风机盘管NJ-1AP(KT)8-电磁阀开关控制"},{"$nulls":16},{"$f":"IF(AI93=\"\",\"\",AI93)","v":"NJ-1AP(KT)8"},{"$f":"_xlfn.IFNA(VLOOKUP(AL93,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL93,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-1AP(KT)8","01H01","电磁阀开关控制",{"$f":"AH93&\"-\"&AK93","v":"风机盘管-电磁阀开关控制"},{"$f":"VLOOKUP(AH93,List!$B$3:$D$445,2,FALSE)&AJ93&\"_\"&VLOOKUP(AK93,List!$K$2:$M$447,2,FALSE)","v":"FCU01H01_EVC"},{"$f":"_xlfn.IFNA(\"L\"&AM93&\" \"&\"AT%Q\"&B94*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J93&\"*)\",\" \")","v":"LFCU01H01_EVC AT%Q208.0 :BOOL; (*风机盘管NJ-1AP(KT)8-电磁阀开关控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN93,SEARCH(\"AT%\",AN93),,REPT(\" \",25-SEARCH(\"AT%\",AN93))),SEARCH(\":\",REPLACE(AN93,SEARCH(\"AT%\",AN93),,REPT(\" \",25-SEARCH(\"AT%\",AN93)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN93,SEARCH(\"AT%\",AN93),,REPT(\" \",25-SEARCH(\"AT%\",AN93)))))),\" \")","v":"LFCU01H01_EVC           AT%Q208.0      :BOOL; (*风机盘管NJ-1AP(KT)8-电磁阀开关控制*)"},null,{"$f":"AM93","v":"FCU01H01_EVC"},{"$f":"J93","v":"风机盘管NJ-1AP(KT)8-电磁阀开关控制"},{"$f":"($B94*16*8+F93-1)","v":1664}]
[null,13,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","-",{"$nulls":16},{"$f":"IF(AI94=\"\",\"\",AI94)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},{"$f":"AH94&\"-\"&AK94","v":"-"},{"$f":"VLOOKUP(AH94,List!$B$3:$D$445,2,FALSE)&AJ94&\"_\"&VLOOKUP(AK94,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM94&\" \"&\"AT%Q\"&B94*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J94&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J94","v":"-"},{"$f":"AS93+1","v":1665}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%Q\"&B94*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS94+1","v":1666}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%Q\"&B94*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1667]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%Q\"&B94*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1668]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B96=20,1,IF(B96=50,10,IF(B96=125,11,IF(B96=250,100,IF(B96=500,101,IF(B96=800,110,IF(B96=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B96=20,1,IF(B96=50,10,IF(B96=125,11,IF(B96=250,100,IF(B96=500,101,IF(B96=800,110,IF(B96=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%Q\"&B94*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1669]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B96=20,1,IF(B96=50,10,IF(B96=125,11,IF(B96=250,100,IF(B96=500,101,IF(B96=800,110,IF(B96=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B96=20,1,IF(B96=50,10,IF(B96=125,11,IF(B96=250,100,IF(B96=500,101,IF(B96=800,110,IF(B96=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH99,List!$B$3:$D$445,2,FALSE)&AJ99&\"_\"&VLOOKUP(AK99,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM99&\" \"&\"AT%Q\"&B94*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J99&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1670]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B96=20,1,IF(B96=50,10,IF(B96=125,11,IF(B96=250,100,IF(B96=500,101,IF(B96=800,110,IF(B96=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B96=20,1,IF(B96=50,10,IF(B96=125,11,IF(B96=250,100,IF(B96=500,101,IF(B96=800,110,IF(B96=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH100,List!$B$3:$D$445,2,FALSE)&AJ100&\"_\"&VLOOKUP(AK100,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM100&\" \"&\"AT%Q\"&B94*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J100&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1671]
[null,{"$f":"B106","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B106&\"地址: \"&B103&\" *)\"","v":"(* IOM 0801U地址: 14 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH102&AA102&\"-\"&AK102","v":"空调机组-回风温度"},{"$nulls":16},{"$f":"IF(AI102=\"\",\"\",AI102)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL102,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL102,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H01","回风温度",{"$f":"AH102&\"-\"&AK102","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH102,List!$B$3:$D$445,2,FALSE)&AJ102&\"_\"&VLOOKUP(AK102,List!$K$2:$M$447,2,FALSE)","v":"AHU01H01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM102&\" \"&\"AT%I\"&B103*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J102&\"*)\",\" \")","v":"LAHU01H01_RT AT%I224.0 :INT ; (*空调机组-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN102,SEARCH(\"AT%\",AN102),,REPT(\" \",25-SEARCH(\"AT%\",AN102))),SEARCH(\":\",REPLACE(AN102,SEARCH(\"AT%\",AN102),,REPT(\" \",25-SEARCH(\"AT%\",AN102)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN102,SEARCH(\"AT%\",AN102),,REPT(\" \",25-SEARCH(\"AT%\",AN102)))))),\" \")","v":"LAHU01H01_RT            AT%I224.0      :INT ; (*空调机组-回风温度*)"},null,{"$f":"AM102","v":"AHU01H01_RT"},{"$f":"J102","v":"空调机组-回风温度"},{"$f":"30000+($B103*8+F102-1)","v":30112}]
[null,14,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组-水阀反馈",{"$nulls":16},{"$f":"IF(AI103=\"\",\"\",AI103)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H01","水阀反馈",{"$f":"AH103&\"-\"&AK103","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH103,List!$B$3:$D$445,2,FALSE)&AJ103&\"_\"&VLOOKUP(AK103,List!$K$2:$M$447,2,FALSE)","v":"AHU01H01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM103&\" \"&\"AT%I\"&B103*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J103&\"*)\",\" \")","v":"LAHU01H01_WVB AT%I226.0 :INT ; (*空调机组-水阀反馈*)"},"LAHU01H01_WVB           AT%I226.0      :INT ; (*空调机组-水阀反馈*)",null,"AHU01H01_WVB",{"$f":"J103","v":"空调机组-水阀反馈"},{"$f":"AS102+1","v":30113}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组-回风温度",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"AHU01H02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%I\"&B103*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LAHU01H02_RT AT%I228.0 :INT ; (*空调机组-回风温度*)"},"LAHU01H02_RT            AT%I228.0      :INT ; (*空调机组-回风温度*)",null,"AHU01H02_RT","空调机组-回风温度",{"$f":"AS103+1","v":30114}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组-水阀反馈",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"AHU01H02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%I\"&B103*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LAHU01H02_WVB AT%I230.0 :INT ; (*空调机组-水阀反馈*)"},"LAHU01H02_WVB           AT%I230.0      :INT ; (*空调机组-水阀反馈*)",null,"AHU01H02_WVB","空调机组-水阀反馈",30115]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组-回风温度",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":"AHU01H03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%I\"&B103*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":"LAHU01H03_RT AT%I232.0 :INT ; (*空调机组-回风温度*)"},"LAHU01H03_RT            AT%I232.0      :INT ; (*空调机组-回风温度*)",null,"AHU01H03_RT","空调机组-回风温度",30116]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B105=20,1,IF(B105=50,10,IF(B105=125,11,IF(B105=250,100,IF(B105=500,101,IF(B105=800,110,IF(B105=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B105=20,1,IF(B105=50,10,IF(B105=125,11,IF(B105=250,100,IF(B105=500,101,IF(B105=800,110,IF(B105=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组-水阀反馈",{"$nulls":16},{"$f":"IF(AI107=\"\",\"\",AI107)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH107,List!$B$3:$D$445,2,FALSE)&AJ107&\"_\"&VLOOKUP(AK107,List!$K$2:$M$447,2,FALSE)","v":"AHU01H03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM107&\" \"&\"AT%I\"&B103*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J107&\"*)\",\" \")","v":"LAHU01H03_WVB AT%I234.0 :INT ; (*空调机组-水阀反馈*)"},"LAHU01H03_WVB           AT%I234.0      :INT ; (*空调机组-水阀反馈*)",null,"AHU01H03_WVB",{"$f":"J107","v":"空调机组-水阀反馈"},30117]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B105=20,1,IF(B105=50,10,IF(B105=125,11,IF(B105=250,100,IF(B105=500,101,IF(B105=800,110,IF(B105=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B105=20,1,IF(B105=50,10,IF(B105=125,11,IF(B105=250,100,IF(B105=500,101,IF(B105=800,110,IF(B105=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组-回风温度",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH108,List!$B$3:$D$445,2,FALSE)&AJ108&\"_\"&VLOOKUP(AK108,List!$K$2:$M$447,2,FALSE)","v":"AHU01H04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM108&\" \"&\"AT%I\"&B103*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J108&\"*)\",\" \")","v":"LAHU01H04_RT AT%I236.0 :INT ; (*空调机组-回风温度*)"},"LAHU01H04_RT            AT%I236.0      :INT ; (*空调机组-回风温度*)",null,"AHU01H04_RT","空调机组-回风温度",30118]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B105=20,1,IF(B105=50,10,IF(B105=125,11,IF(B105=250,100,IF(B105=500,101,IF(B105=800,110,IF(B105=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B105=20,1,IF(B105=50,10,IF(B105=125,11,IF(B105=250,100,IF(B105=500,101,IF(B105=800,110,IF(B105=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组-水阀反馈",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH109,List!$B$3:$D$445,2,FALSE)&AJ109&\"_\"&VLOOKUP(AK109,List!$K$2:$M$447,2,FALSE)","v":"AHU01H04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM109&\" \"&\"AT%I\"&B103*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J109&\"*)\",\" \")","v":"LAHU01H04_WVB AT%I238.0 :INT ; (*空调机组-水阀反馈*)"},"LAHU01H04_WVB           AT%I238.0      :INT ; (*空调机组-水阀反馈*)",null,"AHU01H04_WVB","空调机组-水阀反馈",30119]
[null,{"$f":"B115","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B115&\"地址: \"&B112&\" *)\"","v":"(* IOM 0801U地址: 15 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH111&AA111&\"-\"&AK111","v":"空调机组-回风温度"},{"$nulls":16},{"$f":"IF(AI111=\"\",\"\",AI111)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL111,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL111,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H05","回风温度",{"$f":"AH111&\"-\"&AK111","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH111,List!$B$3:$D$445,2,FALSE)&AJ111&\"_\"&VLOOKUP(AK111,List!$K$2:$M$447,2,FALSE)","v":"AHU01H05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM111&\" \"&\"AT%I\"&B112*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J111&\"*)\",\" \")","v":"LAHU01H05_RT AT%I240.0 :INT ; (*空调机组-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN111,SEARCH(\"AT%\",AN111),,REPT(\" \",25-SEARCH(\"AT%\",AN111))),SEARCH(\":\",REPLACE(AN111,SEARCH(\"AT%\",AN111),,REPT(\" \",25-SEARCH(\"AT%\",AN111)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN111,SEARCH(\"AT%\",AN111),,REPT(\" \",25-SEARCH(\"AT%\",AN111)))))),\" \")","v":"LAHU01H05_RT            AT%I240.0      :INT ; (*空调机组-回风温度*)"},null,{"$f":"AM111","v":"AHU01H05_RT"},{"$f":"J111","v":"空调机组-回风温度"},{"$f":"30000+($B112*8+F111-1)","v":30120}]
[null,15,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组-水阀反馈",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H05","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH112,List!$B$3:$D$445,2,FALSE)&AJ112&\"_\"&VLOOKUP(AK112,List!$K$2:$M$447,2,FALSE)","v":"AHU01H05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM112&\" \"&\"AT%I\"&B112*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J112&\"*)\",\" \")","v":"LAHU01H05_WVB AT%I242.0 :INT ; (*空调机组-水阀反馈*)"},"LAHU01H05_WVB           AT%I242.0      :INT ; (*空调机组-水阀反馈*)",null,"AHU01H05_WVB","空调机组-水阀反馈",{"$f":"AS111+1","v":30121}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组-回风温度",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH113,List!$B$3:$D$445,2,FALSE)&AJ113&\"_\"&VLOOKUP(AK113,List!$K$2:$M$447,2,FALSE)","v":"AHU01H06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM113&\" \"&\"AT%I\"&B112*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J113&\"*)\",\" \")","v":"LAHU01H06_RT AT%I244.0 :INT ; (*空调机组-回风温度*)"},"LAHU01H06_RT            AT%I244.0      :INT ; (*空调机组-回风温度*)",null,"AHU01H06_RT","空调机组-回风温度",30122]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组-水阀反馈",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH114,List!$B$3:$D$445,2,FALSE)&AJ114&\"_\"&VLOOKUP(AK114,List!$K$2:$M$447,2,FALSE)","v":"AHU01H06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM114&\" \"&\"AT%I\"&B112*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J114&\"*)\",\" \")","v":"LAHU01H06_WVB AT%I246.0 :INT ; (*空调机组-水阀反馈*)"},"LAHU01H06_WVB           AT%I246.0      :INT ; (*空调机组-水阀反馈*)",null,"AHU01H06_WVB","空调机组-水阀反馈",30123]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组-回风温度",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H07","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH115,List!$B$3:$D$445,2,FALSE)&AJ115&\"_\"&VLOOKUP(AK115,List!$K$2:$M$447,2,FALSE)","v":"AHU01H07_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM115&\" \"&\"AT%I\"&B112*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J115&\"*)\",\" \")","v":"LAHU01H07_RT AT%I248.0 :INT ; (*空调机组-回风温度*)"},"LAHU01H07_RT            AT%I248.0      :INT ; (*空调机组-回风温度*)",null,"AHU01H07_RT","空调机组-回风温度",30124]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B114=20,1,IF(B114=50,10,IF(B114=125,11,IF(B114=250,100,IF(B114=500,101,IF(B114=800,110,IF(B114=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B114=20,1,IF(B114=50,10,IF(B114=125,11,IF(B114=250,100,IF(B114=500,101,IF(B114=800,110,IF(B114=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组-水阀反馈",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H07","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH116,List!$B$3:$D$445,2,FALSE)&AJ116&\"_\"&VLOOKUP(AK116,List!$K$2:$M$447,2,FALSE)","v":"AHU01H07_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM116&\" \"&\"AT%I\"&B112*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J116&\"*)\",\" \")","v":"LAHU01H07_WVB AT%I250.0 :INT ; (*空调机组-水阀反馈*)"},"LAHU01H07_WVB           AT%I250.0      :INT ; (*空调机组-水阀反馈*)",null,"AHU01H07_WVB","空调机组-水阀反馈",30125]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B114=20,1,IF(B114=50,10,IF(B114=125,11,IF(B114=250,100,IF(B114=500,101,IF(B114=800,110,IF(B114=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B114=20,1,IF(B114=50,10,IF(B114=125,11,IF(B114=250,100,IF(B114=500,101,IF(B114=800,110,IF(B114=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组-回风温度",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL117,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL117,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H08","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH117,List!$B$3:$D$445,2,FALSE)&AJ117&\"_\"&VLOOKUP(AK117,List!$K$2:$M$447,2,FALSE)","v":"AHU01H08_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM117&\" \"&\"AT%I\"&B112*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J117&\"*)\",\" \")","v":"LAHU01H08_RT AT%I252.0 :INT ; (*空调机组-回风温度*)"},"LAHU01H08_RT            AT%I252.0      :INT ; (*空调机组-回风温度*)",null,"AHU01H08_RT","空调机组-回风温度",30126]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B114=20,1,IF(B114=50,10,IF(B114=125,11,IF(B114=250,100,IF(B114=500,101,IF(B114=800,110,IF(B114=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B114=20,1,IF(B114=50,10,IF(B114=125,11,IF(B114=250,100,IF(B114=500,101,IF(B114=800,110,IF(B114=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组-水阀反馈",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL118,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL118,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H08","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH118,List!$B$3:$D$445,2,FALSE)&AJ118&\"_\"&VLOOKUP(AK118,List!$K$2:$M$447,2,FALSE)","v":"AHU01H08_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM118&\" \"&\"AT%I\"&B112*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J118&\"*)\",\" \")","v":"LAHU01H08_WVB AT%I254.0 :INT ; (*空调机组-水阀反馈*)"},"LAHU01H08_WVB           AT%I254.0      :INT ; (*空调机组-水阀反馈*)",null,"AHU01H08_WVB","空调机组-水阀反馈",30127]
[null,{"$f":"B124","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B124&\"地址: \"&B121&\" *)\"","v":"(* IOM 0801U地址: 16 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH120&AA120&\"-\"&AK120","v":"空调机组-回风温度"},{"$nulls":16},{"$f":"IF(AI120=\"\",\"\",AI120)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL120,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL120,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H09","回风温度",{"$f":"AH120&\"-\"&AK120","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH120,List!$B$3:$D$445,2,FALSE)&AJ120&\"_\"&VLOOKUP(AK120,List!$K$2:$M$447,2,FALSE)","v":"AHU01H09_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM120&\" \"&\"AT%I\"&B121*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J120&\"*)\",\" \")","v":"LAHU01H09_RT AT%I256.0 :INT ; (*空调机组-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN120,SEARCH(\"AT%\",AN120),,REPT(\" \",25-SEARCH(\"AT%\",AN120))),SEARCH(\":\",REPLACE(AN120,SEARCH(\"AT%\",AN120),,REPT(\" \",25-SEARCH(\"AT%\",AN120)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN120,SEARCH(\"AT%\",AN120),,REPT(\" \",25-SEARCH(\"AT%\",AN120)))))),\" \")","v":"LAHU01H09_RT            AT%I256.0      :INT ; (*空调机组-回风温度*)"},null,{"$f":"AM120","v":"AHU01H09_RT"},{"$f":"J120","v":"空调机组-回风温度"},{"$f":"30000+($B121*8+F120-1)","v":30128}]
[null,16,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组-水阀反馈",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H09","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH121,List!$B$3:$D$445,2,FALSE)&AJ121&\"_\"&VLOOKUP(AK121,List!$K$2:$M$447,2,FALSE)","v":"AHU01H09_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM121&\" \"&\"AT%I\"&B121*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J121&\"*)\",\" \")","v":"LAHU01H09_WVB AT%I258.0 :INT ; (*空调机组-水阀反馈*)"},"LAHU01H09_WVB           AT%I258.0      :INT ; (*空调机组-水阀反馈*)",null,"AHU01H09_WVB","空调机组-水阀反馈",{"$f":"AS120+1","v":30129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组-回风温度",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H10","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH122,List!$B$3:$D$445,2,FALSE)&AJ122&\"_\"&VLOOKUP(AK122,List!$K$2:$M$447,2,FALSE)","v":"AHU01H10_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM122&\" \"&\"AT%I\"&B121*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J122&\"*)\",\" \")","v":"LAHU01H10_RT AT%I260.0 :INT ; (*空调机组-回风温度*)"},"LAHU01H10_RT            AT%I260.0      :INT ; (*空调机组-回风温度*)",null,"AHU01H10_RT","空调机组-回风温度",30130]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组-水阀反馈",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H10","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH123,List!$B$3:$D$445,2,FALSE)&AJ123&\"_\"&VLOOKUP(AK123,List!$K$2:$M$447,2,FALSE)","v":"AHU01H10_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM123&\" \"&\"AT%I\"&B121*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J123&\"*)\",\" \")","v":"LAHU01H10_WVB AT%I262.0 :INT ; (*空调机组-水阀反馈*)"},"LAHU01H10_WVB           AT%I262.0      :INT ; (*空调机组-水阀反馈*)",null,"AHU01H10_WVB","空调机组-水阀反馈",30131]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),1,1))","v":1},5,null,5,"0V","风机盘管-温度状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管",null,"01H01","温度状态","风机盘管-温度状态",{"$f":"VLOOKUP(AH124,List!$B$3:$D$445,2,FALSE)&AJ124&\"_\"&VLOOKUP(AK124,List!$K$2:$M$447,2,FALSE)","v":"FCU01H01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM124&\" \"&\"AT%I\"&B121*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J124&\"*)\",\" \")","v":"LFCU01H01_T AT%I264.0 :INT ; (*风机盘管-温度状态*)"},"LFCU01H01_T             AT%I264.0      :INT ; (*风机盘管-温度状态*)",null,"FCU01H01_T","风机盘管-温度状态",30132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B123=20,1,IF(B123=50,10,IF(B123=125,11,IF(B123=250,100,IF(B123=500,101,IF(B123=800,110,IF(B123=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B123=20,1,IF(B123=50,10,IF(B123=125,11,IF(B123=250,100,IF(B123=500,101,IF(B123=800,110,IF(B123=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH125,List!$B$3:$D$445,2,FALSE)&AJ125&\"_\"&VLOOKUP(AK125,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM125&\" \"&\"AT%I\"&B121*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J125&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B123=20,1,IF(B123=50,10,IF(B123=125,11,IF(B123=250,100,IF(B123=500,101,IF(B123=800,110,IF(B123=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B123=20,1,IF(B123=50,10,IF(B123=125,11,IF(B123=250,100,IF(B123=500,101,IF(B123=800,110,IF(B123=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL126,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL126,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH126,List!$B$3:$D$445,2,FALSE)&AJ126&\"_\"&VLOOKUP(AK126,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM126&\" \"&\"AT%I\"&B121*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J126&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30134]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B123=20,1,IF(B123=50,10,IF(B123=125,11,IF(B123=250,100,IF(B123=500,101,IF(B123=800,110,IF(B123=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B123=20,1,IF(B123=50,10,IF(B123=125,11,IF(B123=250,100,IF(B123=500,101,IF(B123=800,110,IF(B123=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL127,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL127,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH127,List!$B$3:$D$445,2,FALSE)&AJ127&\"_\"&VLOOKUP(AK127,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM127&\" \"&\"AT%I\"&B121*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J127&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30135]
[null,{"$f":"B133","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B133&\"地址: \"&B130&\" *)\"","v":"(* IOM 0401A地址: 17 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH129&AA129&\"-\"&AK129","v":"空调机组-水阀控制"},{"$nulls":16},{"$f":"IF(AI129=\"\",\"\",AI129)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL129,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL129,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H01","水阀控制",{"$f":"AH129&\"-\"&AK129","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH129,List!$B$3:$D$445,2,FALSE)&AJ129&\"_\"&VLOOKUP(AK129,List!$K$2:$M$447,2,FALSE)","v":"AHU01H01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM129&\" \"&\"AT%Q\"&B130*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J129&\"*)\",\" \")","v":"LAHU01H01_WVC AT%Q272.0 :INT ; (*空调机组-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN129,SEARCH(\"AT%\",AN129),,REPT(\" \",25-SEARCH(\"AT%\",AN129))),SEARCH(\":\",REPLACE(AN129,SEARCH(\"AT%\",AN129),,REPT(\" \",25-SEARCH(\"AT%\",AN129)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN129,SEARCH(\"AT%\",AN129),,REPT(\" \",25-SEARCH(\"AT%\",AN129)))))),\" \")","v":"LAHU01H01_WVC           AT%Q272.0      :INT ; (*空调机组-水阀控制*)"},null,{"$f":"AM129","v":"AHU01H01_WVC"},{"$f":"J129","v":"空调机组-水阀控制"},{"$f":"40000+($B130*8+F129-1)","v":40136}]
[null,17,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH130&AA130&\"-\"&AK130","v":"空调机组-水阀控制"},{"$nulls":16},{"$f":"IF(AI130=\"\",\"\",AI130)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL130,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL130,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H02","水阀控制",{"$f":"AH130&\"-\"&AK130","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH130,List!$B$3:$D$445,2,FALSE)&AJ130&\"_\"&VLOOKUP(AK130,List!$K$2:$M$447,2,FALSE)","v":"AHU01H02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM130&\" \"&\"AT%Q\"&B130*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J130&\"*)\",\" \")","v":"LAHU01H02_WVC AT%Q274.0 :INT ; (*空调机组-水阀控制*)"},"LAHU01H02_WVC           AT%Q274.0      :INT ; (*空调机组-水阀控制*)",null,"AHU01H02_WVC",{"$f":"J130","v":"空调机组-水阀控制"},{"$f":"AS129+1","v":40137}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH131&AA131&\"-\"&AK131","v":"空调机组-水阀控制"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL131,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL131,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH131,List!$B$3:$D$445,2,FALSE)&AJ131&\"_\"&VLOOKUP(AK131,List!$K$2:$M$447,2,FALSE)","v":"AHU01H03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM131&\" \"&\"AT%Q\"&B130*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J131&\"*)\",\" \")","v":"LAHU01H03_WVC AT%Q276.0 :INT ; (*空调机组-水阀控制*)"},"LAHU01H03_WVC           AT%Q276.0      :INT ; (*空调机组-水阀控制*)",null,"AHU01H03_WVC","空调机组-水阀控制",{"$f":"AS130+1","v":40138}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH132&AA132&\"-\"&AK132","v":"空调机组-水阀控制"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL132,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL132,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH132,List!$B$3:$D$445,2,FALSE)&AJ132&\"_\"&VLOOKUP(AK132,List!$K$2:$M$447,2,FALSE)","v":"AHU01H04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM132&\" \"&\"AT%Q\"&B130*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J132&\"*)\",\" \")","v":"LAHU01H04_WVC AT%Q278.0 :INT ; (*空调机组-水阀控制*)"},"LAHU01H04_WVC           AT%Q278.0      :INT ; (*空调机组-水阀控制*)",null,"AHU01H04_WVC","空调机组-水阀控制",40139]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B132=20,1,IF(B132=50,10,IF(B132=125,11,IF(B132=250,100,IF(B132=500,101,IF(B132=800,110,IF(B132=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B132=20,1,IF(B132=50,10,IF(B132=125,11,IF(B132=250,100,IF(B132=500,101,IF(B132=800,110,IF(B132=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B132=20,1,IF(B132=50,10,IF(B132=125,11,IF(B132=250,100,IF(B132=500,101,IF(B132=800,110,IF(B132=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B132=20,1,IF(B132=50,10,IF(B132=125,11,IF(B132=250,100,IF(B132=500,101,IF(B132=800,110,IF(B132=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B132=20,1,IF(B132=50,10,IF(B132=125,11,IF(B132=250,100,IF(B132=500,101,IF(B132=800,110,IF(B132=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B132=20,1,IF(B132=50,10,IF(B132=125,11,IF(B132=250,100,IF(B132=500,101,IF(B132=800,110,IF(B132=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B142","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B142&\"地址: \"&B139&\" *)\"","v":"(* IOM 0401A地址: 18 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH138&AA138&\"-\"&AK138","v":"空调机组-水阀控制"},{"$nulls":16},{"$f":"IF(AI138=\"\",\"\",AI138)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL138,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL138,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H05","水阀控制",{"$f":"AH138&\"-\"&AK138","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH138,List!$B$3:$D$445,2,FALSE)&AJ138&\"_\"&VLOOKUP(AK138,List!$K$2:$M$447,2,FALSE)","v":"AHU01H05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM138&\" \"&\"AT%Q\"&B139*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J138&\"*)\",\" \")","v":"LAHU01H05_WVC AT%Q288.0 :INT ; (*空调机组-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN138,SEARCH(\"AT%\",AN138),,REPT(\" \",25-SEARCH(\"AT%\",AN138))),SEARCH(\":\",REPLACE(AN138,SEARCH(\"AT%\",AN138),,REPT(\" \",25-SEARCH(\"AT%\",AN138)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN138,SEARCH(\"AT%\",AN138),,REPT(\" \",25-SEARCH(\"AT%\",AN138)))))),\" \")","v":"LAHU01H05_WVC           AT%Q288.0      :INT ; (*空调机组-水阀控制*)"},null,{"$f":"AM138","v":"AHU01H05_WVC"},{"$f":"J138","v":"空调机组-水阀控制"},{"$f":"40000+($B139*8+F138-1)","v":40144}]
[null,18,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH139&AA139&\"-\"&AK139","v":"空调机组-水阀控制"},{"$nulls":16},{"$f":"IF(AI139=\"\",\"\",AI139)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL139,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL139,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H06","水阀控制",{"$f":"AH139&\"-\"&AK139","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH139,List!$B$3:$D$445,2,FALSE)&AJ139&\"_\"&VLOOKUP(AK139,List!$K$2:$M$447,2,FALSE)","v":"AHU01H06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM139&\" \"&\"AT%Q\"&B139*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J139&\"*)\",\" \")","v":"LAHU01H06_WVC AT%Q290.0 :INT ; (*空调机组-水阀控制*)"},"LAHU01H06_WVC           AT%Q290.0      :INT ; (*空调机组-水阀控制*)",null,"AHU01H06_WVC",{"$f":"J139","v":"空调机组-水阀控制"},{"$f":"AS138+1","v":40145}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH140&AA140&\"-\"&AK140","v":"空调机组-水阀控制"},{"$nulls":16},{"$f":"IF(AI140=\"\",\"\",AI140)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL140,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL140,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H07","水阀控制",{"$f":"AH140&\"-\"&AK140","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH140,List!$B$3:$D$445,2,FALSE)&AJ140&\"_\"&VLOOKUP(AK140,List!$K$2:$M$447,2,FALSE)","v":"AHU01H07_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM140&\" \"&\"AT%Q\"&B139*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J140&\"*)\",\" \")","v":"LAHU01H07_WVC AT%Q292.0 :INT ; (*空调机组-水阀控制*)"},"LAHU01H07_WVC           AT%Q292.0      :INT ; (*空调机组-水阀控制*)",null,"AHU01H07_WVC","空调机组-水阀控制",{"$f":"AS139+1","v":40146}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH141&AA141&\"-\"&AK141","v":"空调机组-水阀控制"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL141,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL141,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H08","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH141,List!$B$3:$D$445,2,FALSE)&AJ141&\"_\"&VLOOKUP(AK141,List!$K$2:$M$447,2,FALSE)","v":"AHU01H08_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM141&\" \"&\"AT%Q\"&B139*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J141&\"*)\",\" \")","v":"LAHU01H08_WVC AT%Q294.0 :INT ; (*空调机组-水阀控制*)"},"LAHU01H08_WVC           AT%Q294.0      :INT ; (*空调机组-水阀控制*)",null,"AHU01H08_WVC","空调机组-水阀控制",40147]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B141=20,1,IF(B141=50,10,IF(B141=125,11,IF(B141=250,100,IF(B141=500,101,IF(B141=800,110,IF(B141=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B141=20,1,IF(B141=50,10,IF(B141=125,11,IF(B141=250,100,IF(B141=500,101,IF(B141=800,110,IF(B141=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B141=20,1,IF(B141=50,10,IF(B141=125,11,IF(B141=250,100,IF(B141=500,101,IF(B141=800,110,IF(B141=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B141=20,1,IF(B141=50,10,IF(B141=125,11,IF(B141=250,100,IF(B141=500,101,IF(B141=800,110,IF(B141=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B141=20,1,IF(B141=50,10,IF(B141=125,11,IF(B141=250,100,IF(B141=500,101,IF(B141=800,110,IF(B141=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B141=20,1,IF(B141=50,10,IF(B141=125,11,IF(B141=250,100,IF(B141=500,101,IF(B141=800,110,IF(B141=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B151","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B151&\"地址: \"&B148&\" *)\"","v":"(* IOM 0401A地址: 19 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH147&AA147&\"-\"&AK147","v":"空调机组-水阀控制"},{"$nulls":16},{"$f":"IF(AI147=\"\",\"\",AI147)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL147,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL147,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H09","水阀控制",{"$f":"AH147&\"-\"&AK147","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH147,List!$B$3:$D$445,2,FALSE)&AJ147&\"_\"&VLOOKUP(AK147,List!$K$2:$M$447,2,FALSE)","v":"AHU01H09_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM147&\" \"&\"AT%Q\"&B148*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J147&\"*)\",\" \")","v":"LAHU01H09_WVC AT%Q304.0 :INT ; (*空调机组-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN147,SEARCH(\"AT%\",AN147),,REPT(\" \",25-SEARCH(\"AT%\",AN147))),SEARCH(\":\",REPLACE(AN147,SEARCH(\"AT%\",AN147),,REPT(\" \",25-SEARCH(\"AT%\",AN147)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN147,SEARCH(\"AT%\",AN147),,REPT(\" \",25-SEARCH(\"AT%\",AN147)))))),\" \")","v":"LAHU01H09_WVC           AT%Q304.0      :INT ; (*空调机组-水阀控制*)"},null,{"$f":"AM147","v":"AHU01H09_WVC"},{"$f":"J147","v":"空调机组-水阀控制"},{"$f":"40000+($B148*8+F147-1)","v":40152}]
[null,19,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),4,1))","v":1},2,null,3,4,"空调机组-水阀控制",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL148,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL148,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组",null,"01H10","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH148,List!$B$3:$D$445,2,FALSE)&AJ148&\"_\"&VLOOKUP(AK148,List!$K$2:$M$447,2,FALSE)","v":"AHU01H10_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM148&\" \"&\"AT%Q\"&B148*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J148&\"*)\",\" \")","v":"LAHU01H10_WVC AT%Q306.0 :INT ; (*空调机组-水阀控制*)"},"LAHU01H10_WVC           AT%Q306.0      :INT ; (*空调机组-水阀控制*)",null,"AHU01H10_WVC","空调机组-水阀控制",{"$f":"AS147+1","v":40153}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),3,1))","v":0},3,null,5,6,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL149,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL149,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH149,List!$B$3:$D$445,2,FALSE)&AJ149&\"_\"&VLOOKUP(AK149,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM149&\" \"&\"AT%Q\"&B148*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J149&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40154]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),2,1))","v":0},4,null,7,8,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL150,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL150,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH150,List!$B$3:$D$445,2,FALSE)&AJ150&\"_\"&VLOOKUP(AK150,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM150&\" \"&\"AT%Q\"&B148*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J150&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40155]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B150=20,1,IF(B150=50,10,IF(B150=125,11,IF(B150=250,100,IF(B150=500,101,IF(B150=800,110,IF(B150=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B150=20,1,IF(B150=50,10,IF(B150=125,11,IF(B150=250,100,IF(B150=500,101,IF(B150=800,110,IF(B150=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B150=20,1,IF(B150=50,10,IF(B150=125,11,IF(B150=250,100,IF(B150=500,101,IF(B150=800,110,IF(B150=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B150=20,1,IF(B150=50,10,IF(B150=125,11,IF(B150=250,100,IF(B150=500,101,IF(B150=800,110,IF(B150=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B150=20,1,IF(B150=50,10,IF(B150=125,11,IF(B150=250,100,IF(B150=500,101,IF(B150=800,110,IF(B150=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B150=20,1,IF(B150=50,10,IF(B150=125,11,IF(B150=250,100,IF(B150=500,101,IF(B150=800,110,IF(B150=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L301","index":21,"n_rows":120,"n_cols":45,"rows_kept":120,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[6,1,6,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[92,5,92,6],[92,9,92,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[101,5,101,6],[101,9,101,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[109,5,109,6],[109,9,109,25],[110,5,110,6],[110,9,110,25],[112,5,112,6],[112,9,112,25],[113,5,113,6],[113,9,113,25],[114,5,114,6],[114,9,114,25],[115,5,115,6],[115,9,115,25],[116,5,116,6],[116,9,116,25],[117,5,117,6],[117,9,117,25],[118,5,118,6],[118,9,118,25],[119,5,119,6],[119,9,119,25],[4,1,5,1],[12,1,23,1],[29,1,40,1],[46,1,57,1],[63,1,74,1],[80,1,83,1],[89,1,92,1],[98,1,101,1],[107,1,110,1],[116,1,119,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[16,2,23,4],[33,2,40,4],[50,2,57,4],[67,2,74,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L19",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"EXC-1000"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B13&\"地址: \"&B10&\" *)\"","v":"(* IOM 1601R地址: 0 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH9&AA9&\"-\"&AK9","v":"空调机组NJ-3AP(KT)1-1-运行状态"},{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-3AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-1","03A01","运行状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU03A01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B10*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU03A01_R AT%I0.0 :BOOL; (*空调机组NJ-3AP(KT)1-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9))),SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))))),\" \")","v":"LAHU03A01_R             AT%I0.0        :BOOL; (*空调机组NJ-3AP(KT)1-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM9","v":"L19\\L19AHU03A01_R"},{"$f":"J9","v":"空调机组NJ-3AP(KT)1-1-运行状态"},{"$f":"10000+($B10*16*8+F9-1)","v":10000}]
[null,0,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-3AP(KT)1-1-故障状态",{"$nulls":16},{"$f":"IF(AI10=\"\",\"\",AI10)","v":"NJ-3AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-1","03A01","故障状态",{"$f":"AH10&\"-\"&AK10","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU03A01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B10*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU03A01_F AT%I0.1 :BOOL; (*空调机组NJ-3AP(KT)1-1-故障状态*)"},"LAHU03A01_F             AT%I0.1        :BOOL; (*空调机组NJ-3AP(KT)1-1-故障状态*)",null,"L19\\L19AHU03A01_F",{"$f":"J10","v":"空调机组NJ-3AP(KT)1-1-故障状态"},{"$f":"AS9+1","v":10001}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)1-1-自动状态",{"$nulls":16},"NJ-3AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-1","03A01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU03A01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B10*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU03A01_A AT%I0.2 :BOOL; (*空调机组NJ-3AP(KT)1-1-自动状态*)"},"LAHU03A01_A             AT%I0.2        :BOOL; (*空调机组NJ-3AP(KT)1-1-自动状态*)",null,"L19\\L19AHU03A01_A","空调机组NJ-3AP(KT)1-1-自动状态",{"$f":"AS10+1","v":10002}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)1-1-风机压差",{"$nulls":16},"NJ-3AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-1","03A01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU03A01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B10*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU03A01_FPS AT%I0.3 :BOOL; (*空调机组NJ-3AP(KT)1-1-风机压差*)"},"LAHU03A01_FPS           AT%I0.3        :BOOL; (*空调机组NJ-3AP(KT)1-1-风机压差*)",null,"L19\\L19AHU03A01_FPS","空调机组NJ-3AP(KT)1-1-风机压差",10003]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)1-2-运行状态",{"$nulls":16},"NJ-3AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-2","03A02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU03A02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B10*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU03A02_R AT%I0.4 :BOOL; (*空调机组NJ-3AP(KT)1-2-运行状态*)"},"LAHU03A02_R             AT%I0.4        :BOOL; (*空调机组NJ-3AP(KT)1-2-运行状态*)",null,"L19\\L19AHU03A02_R","空调机组NJ-3AP(KT)1-2-运行状态",10004]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)1-2-故障状态",{"$nulls":16},"NJ-3AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-2","03A02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU03A02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B10*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU03A02_F AT%I0.5 :BOOL; (*空调机组NJ-3AP(KT)1-2-故障状态*)"},"LAHU03A02_F             AT%I0.5        :BOOL; (*空调机组NJ-3AP(KT)1-2-故障状态*)",null,"L19\\L19AHU03A02_F","空调机组NJ-3AP(KT)1-2-故障状态",10005]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)1-2-自动状态",{"$nulls":16},"NJ-3AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-2","03A02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU03A02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B10*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU03A02_A AT%I0.6 :BOOL; (*空调机组NJ-3AP(KT)1-2-自动状态*)"},"LAHU03A02_A             AT%I0.6        :BOOL; (*空调机组NJ-3AP(KT)1-2-自动状态*)",null,"L19\\L19AHU03A02_A","空调机组NJ-3AP(KT)1-2-自动状态",10006]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)1-2-风机压差",{"$nulls":16},"NJ-3AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-2","03A02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU03A02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B10*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU03A02_FPS AT%I0.7 :BOOL; (*空调机组NJ-3AP(KT)1-2-风机压差*)"},"LAHU03A02_FPS           AT%I0.7        :BOOL; (*空调机组NJ-3AP(KT)1-2-风机压差*)",null,"L19\\L19AHU03A02_FPS","空调机组NJ-3AP(KT)1-2-风机压差",10007]
[{"$nulls":5},9,null,17,18,"空调机组NJ-3AP(KT)1-3-运行状态",{"$nulls":16},"NJ-3AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-3","03A03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU03A03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B10*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU03A03_R AT%I1.0 :BOOL; (*空调机组NJ-3AP(KT)1-3-运行状态*)"},"LAHU03A03_R             AT%I1.0        :BOOL; (*空调机组NJ-3AP(KT)1-3-运行状态*)",null,"L19\\L19AHU03A03_R","空调机组NJ-3AP(KT)1-3-运行状态",10008]
[{"$nulls":5},10,null,19,20,"空调机组NJ-3AP(KT)1-3-故障状态",{"$nulls":16},{"$f":"IF(AI18=\"\",\"\",AI18)","v":"NJ-3AP(KT)1-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-3","03A03","故障状态",{"$f":"AH18&\"-\"&AK18","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU03A03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B10*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU03A03_F AT%I1.1 :BOOL; (*空调机组NJ-3AP(KT)1-3-故障状态*)"},"LAHU03A03_F             AT%I1.1        :BOOL; (*空调机组NJ-3AP(KT)1-3-故障状态*)",null,"L19\\L19AHU03A03_F","空调机组NJ-3AP(KT)1-3-故障状态",10009]
[{"$nulls":5},11,null,21,22,"空调机组NJ-3AP(KT)1-3-自动状态",{"$nulls":16},"NJ-3AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-3","03A03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU03A03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B10*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU03A03_A AT%I1.2 :BOOL; (*空调机组NJ-3AP(KT)1-3-自动状态*)"},"LAHU03A03_A             AT%I1.2        :BOOL; (*空调机组NJ-3AP(KT)1-3-自动状态*)",null,"L19\\L19AHU03A03_A","空调机组NJ-3AP(KT)1-3-自动状态",10010]
[{"$nulls":5},12,null,23,24,"空调机组NJ-3AP(KT)1-3-风机压差",{"$nulls":16},"NJ-3AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-3","03A03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU03A03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B10*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU03A03_FPS AT%I1.3 :BOOL; (*空调机组NJ-3AP(KT)1-3-风机压差*)"},"LAHU03A03_FPS           AT%I1.3        :BOOL; (*空调机组NJ-3AP(KT)1-3-风机压差*)",null,"L19\\L19AHU03A03_FPS","空调机组NJ-3AP(KT)1-3-风机压差",10011]
[{"$nulls":5},13,null,25,26,"空调机组NJ-3AP(KT)1-4-运行状态",{"$nulls":16},"NJ-3AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-4","03A04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU03A04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B10*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU03A04_R AT%I1.4 :BOOL; (*空调机组NJ-3AP(KT)1-4-运行状态*)"},"LAHU03A04_R             AT%I1.4        :BOOL; (*空调机组NJ-3AP(KT)1-4-运行状态*)",null,"L19\\L19AHU03A04_R","空调机组NJ-3AP(KT)1-4-运行状态",10012]
[{"$nulls":5},14,null,27,28,"空调机组NJ-3AP(KT)1-4-故障状态",{"$nulls":16},"NJ-3AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-4","03A04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU03A04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B10*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU03A04_F AT%I1.5 :BOOL; (*空调机组NJ-3AP(KT)1-4-故障状态*)"},"LAHU03A04_F             AT%I1.5        :BOOL; (*空调机组NJ-3AP(KT)1-4-故障状态*)",null,"L19\\L19AHU03A04_F","空调机组NJ-3AP(KT)1-4-故障状态",10013]
[{"$nulls":5},15,null,29,30,"空调机组NJ-3AP(KT)1-4-自动状态",{"$nulls":16},"NJ-3AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-4","03A04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU03A04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B10*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU03A04_A AT%I1.6 :BOOL; (*空调机组NJ-3AP(KT)1-4-自动状态*)"},"LAHU03A04_A             AT%I1.6        :BOOL; (*空调机组NJ-3AP(KT)1-4-自动状态*)",null,"L19\\L19AHU03A04_A","空调机组NJ-3AP(KT)1-4-自动状态",10014]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-3AP(KT)1-4-风机压差",{"$nulls":16},"NJ-3AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-4","03A04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH24,List!$B$3:$D$445,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,List!$K$2:$M$447,2,FALSE)","v":"AHU03A04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%I\"&B10*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":"LAHU03A04_FPS AT%I1.7 :BOOL; (*空调机组NJ-3AP(KT)1-4-风机压差*)"},"LAHU03A04_FPS           AT%I1.7        :BOOL; (*空调机组NJ-3AP(KT)1-4-风机压差*)",null,"L19\\L19AHU03A04_FPS","空调机组NJ-3AP(KT)1-4-风机压差",10015]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 1601R地址: 1 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH26&AA26&\"-\"&AK26","v":"空调机组NJ-3AP(KT)1-5-运行状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-3AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-5","03A05","运行状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU03A05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU03A05_R AT%I16.0 :BOOL; (*空调机组NJ-3AP(KT)1-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LAHU03A05_R             AT%I16.0       :BOOL; (*空调机组NJ-3AP(KT)1-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L19\\L19AHU03A05_R"},{"$f":"J26","v":"空调机组NJ-3AP(KT)1-5-运行状态"},{"$f":"10000+($B27*16*8+F26-1)","v":10128}]
[null,1,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-3AP(KT)1-5-故障状态",{"$nulls":16},{"$f":"IF(AI27=\"\",\"\",AI27)","v":"NJ-3AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-5","03A05","故障状态",{"$f":"AH27&\"-\"&AK27","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU03A05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU03A05_F AT%I16.1 :BOOL; (*空调机组NJ-3AP(KT)1-5-故障状态*)"},"LAHU03A05_F             AT%I16.1       :BOOL; (*空调机组NJ-3AP(KT)1-5-故障状态*)",null,"L19\\L19AHU03A05_F",{"$f":"J27","v":"空调机组NJ-3AP(KT)1-5-故障状态"},{"$f":"AS26+1","v":10129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)1-5-自动状态",{"$nulls":16},"NJ-3AP(KT)1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-5","03A05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU03A05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU03A05_A AT%I16.2 :BOOL; (*空调机组NJ-3AP(KT)1-5-自动状态*)"},"LAHU03A05_A             AT%I16.2       :BOOL; (*空调机组NJ-3AP(KT)1-5-自动状态*)",null,"L19\\L19AHU03A05_A","空调机组NJ-3AP(KT)1-5-自动状态",{"$f":"AS27+1","v":10130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)1-5-风机压差",{"$nulls":16},"NJ-3AP(KT)1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-5","03A05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU03A05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU03A05_FPS AT%I16.3 :BOOL; (*空调机组NJ-3AP(KT)1-5-风机压差*)"},"LAHU03A05_FPS           AT%I16.3       :BOOL; (*空调机组NJ-3AP(KT)1-5-风机压差*)",null,"L19\\L19AHU03A05_FPS","空调机组NJ-3AP(KT)1-5-风机压差",10131]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)1-6-运行状态",{"$nulls":16},"NJ-3AP(KT)1-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-6","03A06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU03A06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B27*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU03A06_R AT%I16.4 :BOOL; (*空调机组NJ-3AP(KT)1-6-运行状态*)"},"LAHU03A06_R             AT%I16.4       :BOOL; (*空调机组NJ-3AP(KT)1-6-运行状态*)",null,"L19\\L19AHU03A06_R","空调机组NJ-3AP(KT)1-6-运行状态",10132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)1-6-故障状态",{"$nulls":16},"NJ-3AP(KT)1-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-6","03A06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU03A06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B27*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU03A06_F AT%I16.5 :BOOL; (*空调机组NJ-3AP(KT)1-6-故障状态*)"},"LAHU03A06_F             AT%I16.5       :BOOL; (*空调机组NJ-3AP(KT)1-6-故障状态*)",null,"L19\\L19AHU03A06_F","空调机组NJ-3AP(KT)1-6-故障状态",10133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)1-6-自动状态",{"$nulls":16},"NJ-3AP(KT)1-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-6","03A06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU03A06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B27*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU03A06_A AT%I16.6 :BOOL; (*空调机组NJ-3AP(KT)1-6-自动状态*)"},"LAHU03A06_A             AT%I16.6       :BOOL; (*空调机组NJ-3AP(KT)1-6-自动状态*)",null,"L19\\L19AHU03A06_A","空调机组NJ-3AP(KT)1-6-自动状态",10134]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)1-6-风机压差",{"$nulls":16},"NJ-3AP(KT)1-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-6","03A06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU03A06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B27*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU03A06_FPS AT%I16.7 :BOOL; (*空调机组NJ-3AP(KT)1-6-风机压差*)"},"LAHU03A06_FPS           AT%I16.7       :BOOL; (*空调机组NJ-3AP(KT)1-6-风机压差*)",null,"L19\\L19AHU03A06_FPS","空调机组NJ-3AP(KT)1-6-风机压差",10135]
[{"$nulls":5},9,null,17,18,"空调机组NJ-3AP(KT)1-7-运行状态",{"$nulls":16},"NJ-3AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-7","03A07","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU03A07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B27*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU03A07_R AT%I17.0 :BOOL; (*空调机组NJ-3AP(KT)1-7-运行状态*)"},"LAHU03A07_R             AT%I17.0       :BOOL; (*空调机组NJ-3AP(KT)1-7-运行状态*)",null,"L19\\L19AHU03A07_R","空调机组NJ-3AP(KT)1-7-运行状态",10136]
[{"$nulls":5},10,null,19,20,"空调机组NJ-3AP(KT)1-7-故障状态",{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-3AP(KT)1-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-7","03A07","故障状态",{"$f":"AH35&\"-\"&AK35","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU03A07_F"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B27*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU03A07_F AT%I17.1 :BOOL; (*空调机组NJ-3AP(KT)1-7-故障状态*)"},"LAHU03A07_F             AT%I17.1       :BOOL; (*空调机组NJ-3AP(KT)1-7-故障状态*)",null,"L19\\L19AHU03A07_F",{"$f":"J35","v":"空调机组NJ-3AP(KT)1-7-故障状态"},10137]
[{"$nulls":5},11,null,21,22,"空调机组NJ-3AP(KT)1-7-自动状态",{"$nulls":16},"NJ-3AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-7","03A07","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU03A07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B27*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU03A07_A AT%I17.2 :BOOL; (*空调机组NJ-3AP(KT)1-7-自动状态*)"},"LAHU03A07_A             AT%I17.2       :BOOL; (*空调机组NJ-3AP(KT)1-7-自动状态*)",null,"L19\\L19AHU03A07_A","空调机组NJ-3AP(KT)1-7-自动状态",10138]
[{"$nulls":5},12,null,23,24,"空调机组NJ-3AP(KT)1-7-风机压差",{"$nulls":16},"NJ-3AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-7","03A07","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"AHU03A07_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B27*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LAHU03A07_FPS AT%I17.3 :BOOL; (*空调机组NJ-3AP(KT)1-7-风机压差*)"},"LAHU03A07_FPS           AT%I17.3       :BOOL; (*空调机组NJ-3AP(KT)1-7-风机压差*)",null,"L19\\L19AHU03A07_FPS","空调机组NJ-3AP(KT)1-7-风机压差",10139]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-3AL1-1-运行状态",{"$nulls":16},"NJ-3AL1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL1-1","03A01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB03A01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B27*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB03A01_R AT%I17.4 :BOOL; (*照明控制箱NJ-3AL1-1-运行状态*)"},"LLCB03A01_R             AT%I17.4       :BOOL; (*照明控制箱NJ-3AL1-1-运行状态*)",null,"L19\\L19LCB03A01_R","照明控制箱NJ-3AL1-1-运行状态",10140]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-3AL1-1-自动状态",{"$nulls":16},"NJ-3AL1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL1-1","03A01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB03A01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B27*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB03A01_A AT%I17.5 :BOOL; (*照明控制箱NJ-3AL1-1-自动状态*)"},"LLCB03A01_A             AT%I17.5       :BOOL; (*照明控制箱NJ-3AL1-1-自动状态*)",null,"L19\\L19LCB03A01_A","照明控制箱NJ-3AL1-1-自动状态",10141]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-3AL1-2-运行状态",{"$nulls":16},"NJ-3AL1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL1-2","03A02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"LCB03A02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B27*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LLCB03A02_R AT%I17.6 :BOOL; (*照明控制箱NJ-3AL1-2-运行状态*)"},"LLCB03A02_R             AT%I17.6       :BOOL; (*照明控制箱NJ-3AL1-2-运行状态*)",null,"L19\\L19LCB03A02_R","照明控制箱NJ-3AL1-2-运行状态",10142]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-3AL1-2-自动状态",{"$nulls":16},"NJ-3AL1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL1-2","03A02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":"LCB03A02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%I\"&B27*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":"LLCB03A02_A AT%I17.7 :BOOL; (*照明控制箱NJ-3AL1-2-自动状态*)"},"LLCB03A02_A             AT%I17.7       :BOOL; (*照明控制箱NJ-3AL1-2-自动状态*)",null,"L19\\L19LCB03A02_A","照明控制箱NJ-3AL1-2-自动状态",10143]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 1601R地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH43&AA43&\"-\"&AK43","v":"照明控制箱NJ-3AL1-3-运行状态"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-3AL1-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL1-3","03A03","运行状态",{"$f":"AH43&\"-\"&AK43","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"LCB03A03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B44*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LLCB03A03_R AT%I32.0 :BOOL; (*照明控制箱NJ-3AL1-3-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LLCB03A03_R             AT%I32.0       :BOOL; (*照明控制箱NJ-3AL1-3-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM43","v":"L19\\L19LCB03A03_R"},{"$f":"J43","v":"照明控制箱NJ-3AL1-3-运行状态"},{"$f":"10000+($B44*16*8+F43-1)","v":10256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},2,null,3,4,"照明控制箱NJ-3AL1-3-自动状态",{"$nulls":16},{"$f":"IF(AI44=\"\",\"\",AI44)","v":"NJ-3AL1-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL1-3","03A03","自动状态",{"$f":"AH44&\"-\"&AK44","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"LCB03A03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B44*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LLCB03A03_A AT%I32.1 :BOOL; (*照明控制箱NJ-3AL1-3-自动状态*)"},"LLCB03A03_A             AT%I32.1       :BOOL; (*照明控制箱NJ-3AL1-3-自动状态*)",null,"L19\\L19LCB03A03_A",{"$f":"J44","v":"照明控制箱NJ-3AL1-3-自动状态"},{"$f":"AS43+1","v":10257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,5,6,"照明控制箱NJ-3AL1-4-运行状态",{"$nulls":16},"NJ-3AL1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL1-4","03A04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"LCB03A04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B44*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LLCB03A04_R AT%I32.2 :BOOL; (*照明控制箱NJ-3AL1-4-运行状态*)"},"LLCB03A04_R             AT%I32.2       :BOOL; (*照明控制箱NJ-3AL1-4-运行状态*)",null,"L19\\L19LCB03A04_R","照明控制箱NJ-3AL1-4-运行状态",{"$f":"AS44+1","v":10258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},4,null,7,8,"照明控制箱NJ-3AL1-4-自动状态",{"$nulls":16},"NJ-3AL1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL1-4","03A04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"LCB03A04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B44*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LLCB03A04_A AT%I32.3 :BOOL; (*照明控制箱NJ-3AL1-4-自动状态*)"},"LLCB03A04_A             AT%I32.3       :BOOL; (*照明控制箱NJ-3AL1-4-自动状态*)",null,"L19\\L19LCB03A04_A","照明控制箱NJ-3AL1-4-自动状态",10259]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-3AL1-5-运行状态",{"$nulls":16},"NJ-3AL1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL1-5","03A05","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"LCB03A05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B44*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LLCB03A05_R AT%I32.4 :BOOL; (*照明控制箱NJ-3AL1-5-运行状态*)"},"LLCB03A05_R             AT%I32.4       :BOOL; (*照明控制箱NJ-3AL1-5-运行状态*)",null,"L19\\L19LCB03A05_R","照明控制箱NJ-3AL1-5-运行状态",10260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-3AL1-5-自动状态",{"$nulls":16},"NJ-3AL1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-3AL1-5","03A05","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"LCB03A05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B44*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LLCB03A05_A AT%I32.5 :BOOL; (*照明控制箱NJ-3AL1-5-自动状态*)"},"LLCB03A05_A             AT%I32.5       :BOOL; (*照明控制箱NJ-3AL1-5-自动状态*)",null,"L19\\L19LCB03A05_A","照明控制箱NJ-3AL1-5-自动状态",10261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"照明控制箱NJ-3AL(GG)1-1-运行状态",{"$nulls":16},"NJ-3AL(GG)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)1-1","03A06","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"LCB03A06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B44*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LLCB03A06_R AT%I32.6 :BOOL; (*照明控制箱NJ-3AL(GG)1-1-运行状态*)"},"LLCB03A06_R             AT%I32.6       :BOOL; (*照明控制箱NJ-3AL(GG)1-1-运行状态*)",null,"L19\\L19LCB03A06_R","照明控制箱NJ-3AL(GG)1-1-运行状态",10262]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"照明控制箱NJ-3AL(GG)1-1-自动状态",{"$nulls":16},"NJ-3AL(GG)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)1-1","03A06","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"LCB03A06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B44*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LLCB03A06_A AT%I32.7 :BOOL; (*照明控制箱NJ-3AL(GG)1-1-自动状态*)"},"LLCB03A06_A             AT%I32.7       :BOOL; (*照明控制箱NJ-3AL(GG)1-1-自动状态*)",null,"L19\\L19LCB03A06_A","照明控制箱NJ-3AL(GG)1-1-自动状态",10263]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-3AL(GG)1-2-运行状态",{"$nulls":16},"NJ-3AL(GG)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)1-2","03A07","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"LCB03A07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B44*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LLCB03A07_R AT%I33.0 :BOOL; (*照明控制箱NJ-3AL(GG)1-2-运行状态*)"},"LLCB03A07_R             AT%I33.0       :BOOL; (*照明控制箱NJ-3AL(GG)1-2-运行状态*)",null,"L19\\L19LCB03A07_R","照明控制箱NJ-3AL(GG)1-2-运行状态",10264]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-3AL(GG)1-2-自动状态",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-3AL(GG)1-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)1-2","03A07","自动状态",{"$f":"AH52&\"-\"&AK52","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"LCB03A07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%I\"&B44*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LLCB03A07_A AT%I33.1 :BOOL; (*照明控制箱NJ-3AL(GG)1-2-自动状态*)"},"LLCB03A07_A             AT%I33.1       :BOOL; (*照明控制箱NJ-3AL(GG)1-2-自动状态*)",null,"L19\\L19LCB03A07_A",{"$f":"J52","v":"照明控制箱NJ-3AL(GG)1-2-自动状态"},10265]
[{"$nulls":5},11,null,21,22,"照明控制箱NJ-3AL(GG)1-3-运行状态",{"$nulls":16},"NJ-3AL(GG)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)1-3","03A08","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"LCB03A08_R"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%I\"&B44*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LLCB03A08_R AT%I33.2 :BOOL; (*照明控制箱NJ-3AL(GG)1-3-运行状态*)"},"LLCB03A08_R             AT%I33.2       :BOOL; (*照明控制箱NJ-3AL(GG)1-3-运行状态*)",null,"L19\\L19LCB03A08_R","照明控制箱NJ-3AL(GG)1-3-运行状态",10266]
[{"$nulls":5},12,null,23,24,"照明控制箱NJ-3AL(GG)1-3-自动状态",{"$nulls":16},"NJ-3AL(GG)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)1-3","03A08","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"LCB03A08_A"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%I\"&B44*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LLCB03A08_A AT%I33.3 :BOOL; (*照明控制箱NJ-3AL(GG)1-3-自动状态*)"},"LLCB03A08_A             AT%I33.3       :BOOL; (*照明控制箱NJ-3AL(GG)1-3-自动状态*)",null,"L19\\L19LCB03A08_A","照明控制箱NJ-3AL(GG)1-3-自动状态",10267]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-3AL(GG)1-4-运行状态",{"$nulls":16},"NJ-3AL(GG)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)1-4","03A09","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"LCB03A09_R"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%I\"&B44*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LLCB03A09_R AT%I33.4 :BOOL; (*照明控制箱NJ-3AL(GG)1-4-运行状态*)"},"LLCB03A09_R             AT%I33.4       :BOOL; (*照明控制箱NJ-3AL(GG)1-4-运行状态*)",null,"L19\\L19LCB03A09_R","照明控制箱NJ-3AL(GG)1-4-运行状态",10268]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-3AL(GG)1-4-自动状态",{"$nulls":16},"NJ-3AL(GG)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)1-4","03A09","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"LCB03A09_A"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%I\"&B44*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LLCB03A09_A AT%I33.5 :BOOL; (*照明控制箱NJ-3AL(GG)1-4-自动状态*)"},"LLCB03A09_A             AT%I33.5       :BOOL; (*照明控制箱NJ-3AL(GG)1-4-自动状态*)",null,"L19\\L19LCB03A09_A","照明控制箱NJ-3AL(GG)1-4-自动状态",10269]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-3AL(GG)1-5-运行状态",{"$nulls":16},"NJ-3AL(GG)1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)1-5","03A10","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"LCB03A10_R"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%I\"&B44*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LLCB03A10_R AT%I33.6 :BOOL; (*照明控制箱NJ-3AL(GG)1-5-运行状态*)"},"LLCB03A10_R             AT%I33.6       :BOOL; (*照明控制箱NJ-3AL(GG)1-5-运行状态*)",null,"L19\\L19LCB03A10_R","照明控制箱NJ-3AL(GG)1-5-运行状态",10270]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-3AL(GG)1-5-自动状态",{"$nulls":16},"NJ-3AL(GG)1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)1-5","03A10","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":"LCB03A10_A"},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%I\"&B44*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":"LLCB03A10_A AT%I33.7 :BOOL; (*照明控制箱NJ-3AL(GG)1-5-自动状态*)"},"LLCB03A10_A             AT%I33.7       :BOOL; (*照明控制箱NJ-3AL(GG)1-5-自动状态*)",null,"L19\\L19LCB03A10_A","照明控制箱NJ-3AL(GG)1-5-自动状态",10271]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B64&\"地址: \"&B61&\" *)\"","v":"(* IOM 1601D地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH60&AA60&\"-\"&AK60","v":"空调机组NJ-3AP(KT)1-1-启停控制"},{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-3AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-1","03A01","启停控制",{"$f":"AH60&\"-\"&AK60","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"AHU03A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%Q\"&B61*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LAHU03A01_C AT%Q48.0 :BOOL; (*空调机组NJ-3AP(KT)1-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60))),SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))))),\" \")","v":"LAHU03A01_C             AT%Q48.0       :BOOL; (*空调机组NJ-3AP(KT)1-1-启停控制*)"},null,{"$f":"AM60","v":"AHU03A01_C"},{"$f":"J60","v":"空调机组NJ-3AP(KT)1-1-启停控制"},{"$f":"($B61*16*8+F60-1)","v":384}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-3AP(KT)1-2-启停控制",{"$nulls":16},{"$f":"IF(AI61=\"\",\"\",AI61)","v":"NJ-3AP(KT)1-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-2","03A02","启停控制",{"$f":"AH61&\"-\"&AK61","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"AHU03A02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%Q\"&B61*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LAHU03A02_C AT%Q48.1 :BOOL; (*空调机组NJ-3AP(KT)1-2-启停控制*)"},"LAHU03A02_C             AT%Q48.1       :BOOL; (*空调机组NJ-3AP(KT)1-2-启停控制*)",null,"AHU03A02_C",{"$f":"J61","v":"空调机组NJ-3AP(KT)1-2-启停控制"},{"$f":"AS60+1","v":385}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","空调机组NJ-3AP(KT)1-3-启停控制",{"$nulls":16},"NJ-3AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-3","03A03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"AHU03A03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%Q\"&B61*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LAHU03A03_C AT%Q48.2 :BOOL; (*空调机组NJ-3AP(KT)1-3-启停控制*)"},"LAHU03A03_C             AT%Q48.2       :BOOL; (*空调机组NJ-3AP(KT)1-3-启停控制*)",null,"AHU03A03_C","空调机组NJ-3AP(KT)1-3-启停控制",{"$f":"AS61+1","v":386}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","空调机组NJ-3AP(KT)1-4-启停控制",{"$nulls":16},"NJ-3AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-4","03A04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"AHU03A04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%Q\"&B61*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LAHU03A04_C AT%Q48.3 :BOOL; (*空调机组NJ-3AP(KT)1-4-启停控制*)"},"LAHU03A04_C             AT%Q48.3       :BOOL; (*空调机组NJ-3AP(KT)1-4-启停控制*)",null,"AHU03A04_C","空调机组NJ-3AP(KT)1-4-启停控制",387]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-3AP(KT)1-5-启停控制",{"$nulls":16},"NJ-3AP(KT)1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-5","03A05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"AHU03A05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%Q\"&B61*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LAHU03A05_C AT%Q48.4 :BOOL; (*空调机组NJ-3AP(KT)1-5-启停控制*)"},"LAHU03A05_C             AT%Q48.4       :BOOL; (*空调机组NJ-3AP(KT)1-5-启停控制*)",null,"AHU03A05_C","空调机组NJ-3AP(KT)1-5-启停控制",388]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-3AP(KT)1-6-启停控制",{"$nulls":16},"NJ-3AP(KT)1-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-6","03A06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":"AHU03A06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%Q\"&B61*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":"LAHU03A06_C AT%Q48.5 :BOOL; (*空调机组NJ-3AP(KT)1-6-启停控制*)"},"LAHU03A06_C             AT%Q48.5       :BOOL; (*空调机组NJ-3AP(KT)1-6-启停控制*)",null,"AHU03A06_C","空调机组NJ-3AP(KT)1-6-启停控制",389]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","空调机组NJ-3AP(KT)1-7-启停控制",{"$nulls":16},"NJ-3AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-7","03A07","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":"AHU03A07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%Q\"&B61*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":"LAHU03A07_C AT%Q48.6 :BOOL; (*空调机组NJ-3AP(KT)1-7-启停控制*)"},"LAHU03A07_C             AT%Q48.6       :BOOL; (*空调机组NJ-3AP(KT)1-7-启停控制*)",null,"AHU03A07_C","空调机组NJ-3AP(KT)1-7-启停控制",390]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-3AL1-1-启停控制",{"$nulls":16},"NJ-3AL1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL1-1","03A01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":"LCB03A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%Q\"&B61*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":"LLCB03A01_C AT%Q48.7 :BOOL; (*照明控制箱NJ-3AL1-1-启停控制*)"},"LLCB03A01_C             AT%Q48.7       :BOOL; (*照明控制箱NJ-3AL1-1-启停控制*)",null,"LCB03A01_C","照明控制箱NJ-3AL1-1-启停控制",391]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-3AL1-2-启停控制",{"$nulls":16},"NJ-3AL1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL1-2","03A02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"LCB03A02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%Q\"&B61*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LLCB03A02_C AT%Q49.0 :BOOL; (*照明控制箱NJ-3AL1-2-启停控制*)"},"LLCB03A02_C             AT%Q49.0       :BOOL; (*照明控制箱NJ-3AL1-2-启停控制*)",null,"LCB03A02_C","照明控制箱NJ-3AL1-2-启停控制",392]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-3AL1-3-启停控制",{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-3AL1-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL1-3","03A03","启停控制",{"$f":"AH69&\"-\"&AK69","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"LCB03A03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%Q\"&B61*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LLCB03A03_C AT%Q49.1 :BOOL; (*照明控制箱NJ-3AL1-3-启停控制*)"},"LLCB03A03_C             AT%Q49.1       :BOOL; (*照明控制箱NJ-3AL1-3-启停控制*)",null,"LCB03A03_C",{"$f":"J69","v":"照明控制箱NJ-3AL1-3-启停控制"},393]
[{"$nulls":5},11,null,"11+","11-","照明控制箱NJ-3AL1-4-启停控制",{"$nulls":16},"NJ-3AL1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-3AL1-4","03A04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"LCB03A04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%Q\"&B61*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LLCB03A04_C AT%Q49.2 :BOOL; (*照明控制箱NJ-3AL1-4-启停控制*)"},"LLCB03A04_C             AT%Q49.2       :BOOL; (*照明控制箱NJ-3AL1-4-启停控制*)",null,"LCB03A04_C","照明控制箱NJ-3AL1-4-启停控制",394]
[{"$nulls":5},12,null,"12+","12-","照明控制箱NJ-3AL1-5-启停控制",{"$nulls":16},"NJ-3AL1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL1-5","03A05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"LCB03A05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%Q\"&B61*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LLCB03A05_C AT%Q49.3 :BOOL; (*照明控制箱NJ-3AL1-5-启停控制*)"},"LLCB03A05_C             AT%Q49.3       :BOOL; (*照明控制箱NJ-3AL1-5-启停控制*)",null,"LCB03A05_C","照明控制箱NJ-3AL1-5-启停控制",395]
[{"$nulls":5},13,null,"13+","13-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%Q\"&B61*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",396]
[{"$nulls":5},14,null,"14+","14-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%Q\"&B61*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",397]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%Q\"&B61*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",398]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%Q\"&B61*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",399]
[null,"IOM 0801D",{"$nulls":38},{"$f":"\"(* \"&B81&\"地址: \"&B78&\" *)\"","v":"(* IOM 0801D地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH77&AA77&\"-\"&AK77","v":"照明控制箱NJ-3AL(GG)1-1-启停控制"},{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-3AL(GG)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)1-1","03A06","启停控制",{"$f":"AH77&\"-\"&AK77","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"LCB03A06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%Q\"&B78*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LLCB03A06_C AT%Q64.0 :BOOL; (*照明控制箱NJ-3AL(GG)1-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77))),SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))))),\" \")","v":"LLCB03A06_C             AT%Q64.0       :BOOL; (*照明控制箱NJ-3AL(GG)1-1-启停控制*)"},null,{"$f":"AM77","v":"LCB03A06_C"},{"$f":"J77","v":"照明控制箱NJ-3AL(GG)1-1-启停控制"},{"$f":"($B78*16*8+F77-1)","v":512}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","照明控制箱NJ-3AL(GG)1-2-启停控制",{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-3AL(GG)1-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)1-2","03A07","启停控制",{"$f":"AH78&\"-\"&AK78","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"LCB03A07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B78*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LLCB03A07_C AT%Q64.1 :BOOL; (*照明控制箱NJ-3AL(GG)1-2-启停控制*)"},"LLCB03A07_C             AT%Q64.1       :BOOL; (*照明控制箱NJ-3AL(GG)1-2-启停控制*)",null,"LCB03A07_C",{"$f":"J78","v":"照明控制箱NJ-3AL(GG)1-2-启停控制"},{"$f":"AS77+1","v":513}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","照明控制箱NJ-3AL(GG)1-3-启停控制",{"$nulls":16},"NJ-3AL(GG)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)1-3","03A08","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"LCB03A08_C"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B78*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LLCB03A08_C AT%Q64.2 :BOOL; (*照明控制箱NJ-3AL(GG)1-3-启停控制*)"},"LLCB03A08_C             AT%Q64.2       :BOOL; (*照明控制箱NJ-3AL(GG)1-3-启停控制*)",null,"LCB03A08_C","照明控制箱NJ-3AL(GG)1-3-启停控制",{"$f":"AS78+1","v":514}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","照明控制箱NJ-3AL(GG)1-4-启停控制",{"$nulls":16},"NJ-3AL(GG)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)1-4","03A09","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"LCB03A09_C"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B78*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LLCB03A09_C AT%Q64.3 :BOOL; (*照明控制箱NJ-3AL(GG)1-4-启停控制*)"},"LLCB03A09_C             AT%Q64.3       :BOOL; (*照明控制箱NJ-3AL(GG)1-4-启停控制*)",null,"LCB03A09_C","照明控制箱NJ-3AL(GG)1-4-启停控制",515]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","照明控制箱NJ-3AL(GG)1-5-启停控制",{"$nulls":16},"NJ-3AL(GG)1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)1-5","03A10","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"LCB03A10_C"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%Q\"&B78*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LLCB03A10_C AT%Q64.4 :BOOL; (*照明控制箱NJ-3AL(GG)1-5-启停控制*)"},"LLCB03A10_C             AT%Q64.4       :BOOL; (*照明控制箱NJ-3AL(GG)1-5-启停控制*)",null,"LCB03A10_C","照明控制箱NJ-3AL(GG)1-5-启停控制",516]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%Q\"&B78*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",517]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%Q\"&B78*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",518]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH84,List!$B$3:$D$445,2,FALSE)&AJ84&\"_\"&VLOOKUP(AK84,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM84&\" \"&\"AT%Q\"&B78*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J84&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",519]
[null,{"$f":"B90","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B90&\"地址: \"&B87&\" *)\"","v":"(* IOM 0801U地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH86&AA86&\"-\"&AK86","v":"空调机组NJ-3AP(KT)1-1-回风温度"},{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-3AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-1","03A01","回风温度",{"$f":"AH86&\"-\"&AK86","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"AHU03A01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%I\"&B87*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LAHU03A01_RT AT%I80.0 :INT ; (*空调机组NJ-3AP(KT)1-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86))),SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))))),\" \")","v":"LAHU03A01_RT            AT%I80.0       :INT ; (*空调机组NJ-3AP(KT)1-1-回风温度*)"},null,{"$f":"AM86","v":"AHU03A01_RT"},{"$f":"J86","v":"空调机组NJ-3AP(KT)1-1-回风温度"},{"$f":"30000+($B87*8+F86-1)","v":30040}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-3AP(KT)1-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI87=\"\",\"\",AI87)","v":"NJ-3AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-1","03A01","水阀反馈",{"$f":"AH87&\"-\"&AK87","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"AHU03A01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%I\"&B87*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LAHU03A01_WVB AT%I82.0 :INT ; (*空调机组NJ-3AP(KT)1-1-水阀反馈*)"},"LAHU03A01_WVB           AT%I82.0       :INT ; (*空调机组NJ-3AP(KT)1-1-水阀反馈*)",null,"AHU03A01_WVB",{"$f":"J87","v":"空调机组NJ-3AP(KT)1-1-水阀反馈"},{"$f":"AS86+1","v":30041}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)1-2-回风温度",{"$nulls":16},"NJ-3AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-2","03A02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"AHU03A02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%I\"&B87*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LAHU03A02_RT AT%I84.0 :INT ; (*空调机组NJ-3AP(KT)1-2-回风温度*)"},"LAHU03A02_RT            AT%I84.0       :INT ; (*空调机组NJ-3AP(KT)1-2-回风温度*)",null,"AHU03A02_RT","空调机组NJ-3AP(KT)1-2-回风温度",{"$f":"AS87+1","v":30042}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-3AP(KT)1-2-水阀反馈",{"$nulls":16},"NJ-3AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-2","03A02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"AHU03A02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%I\"&B87*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LAHU03A02_WVB AT%I86.0 :INT ; (*空调机组NJ-3AP(KT)1-2-水阀反馈*)"},"LAHU03A02_WVB           AT%I86.0       :INT ; (*空调机组NJ-3AP(KT)1-2-水阀反馈*)",null,"AHU03A02_WVB","空调机组NJ-3AP(KT)1-2-水阀反馈",30043]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-3AP(KT)1-3-回风温度",{"$nulls":16},"NJ-3AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-3","03A03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":"AHU03A03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%I\"&B87*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":"LAHU03A03_RT AT%I88.0 :INT ; (*空调机组NJ-3AP(KT)1-3-回风温度*)"},"LAHU03A03_RT            AT%I88.0       :INT ; (*空调机组NJ-3AP(KT)1-3-回风温度*)",null,"AHU03A03_RT","空调机组NJ-3AP(KT)1-3-回风温度",30044]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-3AP(KT)1-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI91=\"\",\"\",AI91)","v":"NJ-3AP(KT)1-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-3","03A03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH91,List!$B$3:$D$445,2,FALSE)&AJ91&\"_\"&VLOOKUP(AK91,List!$K$2:$M$447,2,FALSE)","v":"AHU03A03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM91&\" \"&\"AT%I\"&B87*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J91&\"*)\",\" \")","v":"LAHU03A03_WVB AT%I90.0 :INT ; (*空调机组NJ-3AP(KT)1-3-水阀反馈*)"},"LAHU03A03_WVB           AT%I90.0       :INT ; (*空调机组NJ-3AP(KT)1-3-水阀反馈*)",null,"AHU03A03_WVB",{"$f":"J91","v":"空调机组NJ-3AP(KT)1-3-水阀反馈"},30045]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-3AP(KT)1-4-回风温度",{"$nulls":16},"NJ-3AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-4","03A04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH92,List!$B$3:$D$445,2,FALSE)&AJ92&\"_\"&VLOOKUP(AK92,List!$K$2:$M$447,2,FALSE)","v":"AHU03A04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM92&\" \"&\"AT%I\"&B87*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J92&\"*)\",\" \")","v":"LAHU03A04_RT AT%I92.0 :INT ; (*空调机组NJ-3AP(KT)1-4-回风温度*)"},"LAHU03A04_RT            AT%I92.0       :INT ; (*空调机组NJ-3AP(KT)1-4-回风温度*)",null,"AHU03A04_RT","空调机组NJ-3AP(KT)1-4-回风温度",30046]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-3AP(KT)1-4-水阀反馈",{"$nulls":16},"NJ-3AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL93,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL93,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-4","03A04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH93,List!$B$3:$D$445,2,FALSE)&AJ93&\"_\"&VLOOKUP(AK93,List!$K$2:$M$447,2,FALSE)","v":"AHU03A04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM93&\" \"&\"AT%I\"&B87*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J93&\"*)\",\" \")","v":"LAHU03A04_WVB AT%I94.0 :INT ; (*空调机组NJ-3AP(KT)1-4-水阀反馈*)"},"LAHU03A04_WVB           AT%I94.0       :INT ; (*空调机组NJ-3AP(KT)1-4-水阀反馈*)",null,"AHU03A04_WVB","空调机组NJ-3AP(KT)1-4-水阀反馈",30047]
[null,{"$f":"B99","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B99&\"地址: \"&B96&\" *)\"","v":"(* IOM 0801U地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH95&AA95&\"-\"&AK95","v":"空调机组NJ-3AP(KT)1-5-回风温度"},{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-3AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-5","03A05","回风温度",{"$f":"AH95&\"-\"&AK95","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"AHU03A05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%I\"&B96*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LAHU03A05_RT AT%I96.0 :INT ; (*空调机组NJ-3AP(KT)1-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95))),SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))))),\" \")","v":"LAHU03A05_RT            AT%I96.0       :INT ; (*空调机组NJ-3AP(KT)1-5-回风温度*)"},null,{"$f":"AM95","v":"AHU03A05_RT"},{"$f":"J95","v":"空调机组NJ-3AP(KT)1-5-回风温度"},{"$f":"30000+($B96*8+F95-1)","v":30048}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-3AP(KT)1-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI96=\"\",\"\",AI96)","v":"NJ-3AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-5","03A05","水阀反馈",{"$f":"AH96&\"-\"&AK96","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"AHU03A05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%I\"&B96*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LAHU03A05_WVB AT%I98.0 :INT ; (*空调机组NJ-3AP(KT)1-5-水阀反馈*)"},"LAHU03A05_WVB           AT%I98.0       :INT ; (*空调机组NJ-3AP(KT)1-5-水阀反馈*)",null,"AHU03A05_WVB",{"$f":"J96","v":"空调机组NJ-3AP(KT)1-5-水阀反馈"},{"$f":"AS95+1","v":30049}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)1-6-回风温度",{"$nulls":16},"NJ-3AP(KT)1-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-6","03A06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":"AHU03A06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%I\"&B96*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":"LAHU03A06_RT AT%I100.0 :INT ; (*空调机组NJ-3AP(KT)1-6-回风温度*)"},"LAHU03A06_RT            AT%I100.0      :INT ; (*空调机组NJ-3AP(KT)1-6-回风温度*)",null,"AHU03A06_RT","空调机组NJ-3AP(KT)1-6-回风温度",{"$f":"AS96+1","v":30050}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-3AP(KT)1-6-水阀反馈",{"$nulls":16},"NJ-3AP(KT)1-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-6","03A06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":"AHU03A06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%I\"&B96*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":"LAHU03A06_WVB AT%I102.0 :INT ; (*空调机组NJ-3AP(KT)1-6-水阀反馈*)"},"LAHU03A06_WVB           AT%I102.0      :INT ; (*空调机组NJ-3AP(KT)1-6-水阀反馈*)",null,"AHU03A06_WVB","空调机组NJ-3AP(KT)1-6-水阀反馈",30051]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-3AP(KT)1-7-回风温度",{"$nulls":16},"NJ-3AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-7","03A07","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH99,List!$B$3:$D$445,2,FALSE)&AJ99&\"_\"&VLOOKUP(AK99,List!$K$2:$M$447,2,FALSE)","v":"AHU03A07_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM99&\" \"&\"AT%I\"&B96*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J99&\"*)\",\" \")","v":"LAHU03A07_RT AT%I104.0 :INT ; (*空调机组NJ-3AP(KT)1-7-回风温度*)"},"LAHU03A07_RT            AT%I104.0      :INT ; (*空调机组NJ-3AP(KT)1-7-回风温度*)",null,"AHU03A07_RT","空调机组NJ-3AP(KT)1-7-回风温度",30052]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-3AP(KT)1-7-水阀反馈",{"$nulls":16},"NJ-3AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-7","03A07","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH100,List!$B$3:$D$445,2,FALSE)&AJ100&\"_\"&VLOOKUP(AK100,List!$K$2:$M$447,2,FALSE)","v":"AHU03A07_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM100&\" \"&\"AT%I\"&B96*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J100&\"*)\",\" \")","v":"LAHU03A07_WVB AT%I106.0 :INT ; (*空调机组NJ-3AP(KT)1-7-水阀反馈*)"},"LAHU03A07_WVB           AT%I106.0      :INT ; (*空调机组NJ-3AP(KT)1-7-水阀反馈*)",null,"AHU03A07_WVB",{"$f":"J100","v":"空调机组NJ-3AP(KT)1-7-水阀反馈"},30053]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH101,List!$B$3:$D$445,2,FALSE)&AJ101&\"_\"&VLOOKUP(AK101,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM101&\" \"&\"AT%I\"&B96*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J101&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30054]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},{"$f":"IF(AI102=\"\",\"\",AI102)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL102,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL102,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH102,List!$B$3:$D$445,2,FALSE)&AJ102&\"_\"&VLOOKUP(AK102,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM102&\" \"&\"AT%I\"&B96*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J102&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30055]
[null,{"$f":"B108","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B108&\"地址: \"&B105&\" *)\"","v":"(* IOM 0401A地址: 7 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH104&AA104&\"-\"&AK104","v":"空调机组NJ-3AP(KT)1-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI104=\"\",\"\",AI104)","v":"NJ-3AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-1","03A01","水阀控制",{"$f":"AH104&\"-\"&AK104","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"AHU03A01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%Q\"&B105*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LAHU03A01_WVC AT%Q112.0 :INT ; (*空调机组NJ-3AP(KT)1-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104))),SEARCH(\":\",REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104)))))),\" \")","v":"LAHU03A01_WVC           AT%Q112.0      :INT ; (*空调机组NJ-3AP(KT)1-1-水阀控制*)"},null,{"$f":"AM104","v":"AHU03A01_WVC"},{"$f":"J104","v":"空调机组NJ-3AP(KT)1-1-水阀控制"},{"$f":"40000+($B105*8+F104-1)","v":40056}]
[null,7,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH105&AA105&\"-\"&AK105","v":"空调机组NJ-3AP(KT)1-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI105=\"\",\"\",AI105)","v":"NJ-3AP(KT)1-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-2","03A02","水阀控制",{"$f":"AH105&\"-\"&AK105","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"AHU03A02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%Q\"&B105*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LAHU03A02_WVC AT%Q114.0 :INT ; (*空调机组NJ-3AP(KT)1-2-水阀控制*)"},"LAHU03A02_WVC           AT%Q114.0      :INT ; (*空调机组NJ-3AP(KT)1-2-水阀控制*)",null,"AHU03A02_WVC",{"$f":"J105","v":"空调机组NJ-3AP(KT)1-2-水阀控制"},{"$f":"AS104+1","v":40057}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH106&AA106&\"-\"&AK106","v":"空调机组NJ-3AP(KT)1-3-水阀控制"},{"$nulls":16},"NJ-3AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-3","03A03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":"AHU03A03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%Q\"&B105*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":"LAHU03A03_WVC AT%Q116.0 :INT ; (*空调机组NJ-3AP(KT)1-3-水阀控制*)"},"LAHU03A03_WVC           AT%Q116.0      :INT ; (*空调机组NJ-3AP(KT)1-3-水阀控制*)",null,"AHU03A03_WVC","空调机组NJ-3AP(KT)1-3-水阀控制",{"$f":"AS105+1","v":40058}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH107&AA107&\"-\"&AK107","v":"空调机组NJ-3AP(KT)1-4-水阀控制"},{"$nulls":16},"NJ-3AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-4","03A04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH107,List!$B$3:$D$445,2,FALSE)&AJ107&\"_\"&VLOOKUP(AK107,List!$K$2:$M$447,2,FALSE)","v":"AHU03A04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM107&\" \"&\"AT%Q\"&B105*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J107&\"*)\",\" \")","v":"LAHU03A04_WVC AT%Q118.0 :INT ; (*空调机组NJ-3AP(KT)1-4-水阀控制*)"},"LAHU03A04_WVC           AT%Q118.0      :INT ; (*空调机组NJ-3AP(KT)1-4-水阀控制*)",null,"AHU03A04_WVC","空调机组NJ-3AP(KT)1-4-水阀控制",40059]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B117","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B117&\"地址: \"&B114&\" *)\"","v":"(* IOM 0401A地址: 8 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH113&AA113&\"-\"&AK113","v":"空调机组NJ-3AP(KT)1-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI113=\"\",\"\",AI113)","v":"NJ-3AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-5","03A05","水阀控制",{"$f":"AH113&\"-\"&AK113","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH113,List!$B$3:$D$445,2,FALSE)&AJ113&\"_\"&VLOOKUP(AK113,List!$K$2:$M$447,2,FALSE)","v":"AHU03A05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM113&\" \"&\"AT%Q\"&B114*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J113&\"*)\",\" \")","v":"LAHU03A05_WVC AT%Q128.0 :INT ; (*空调机组NJ-3AP(KT)1-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN113,SEARCH(\"AT%\",AN113),,REPT(\" \",25-SEARCH(\"AT%\",AN113))),SEARCH(\":\",REPLACE(AN113,SEARCH(\"AT%\",AN113),,REPT(\" \",25-SEARCH(\"AT%\",AN113)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN113,SEARCH(\"AT%\",AN113),,REPT(\" \",25-SEARCH(\"AT%\",AN113)))))),\" \")","v":"LAHU03A05_WVC           AT%Q128.0      :INT ; (*空调机组NJ-3AP(KT)1-5-水阀控制*)"},null,{"$f":"AM113","v":"AHU03A05_WVC"},{"$f":"J113","v":"空调机组NJ-3AP(KT)1-5-水阀控制"},{"$f":"40000+($B114*8+F113-1)","v":40064}]
[null,8,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH114&AA114&\"-\"&AK114","v":"空调机组NJ-3AP(KT)1-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI114=\"\",\"\",AI114)","v":"NJ-3AP(KT)1-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-6","03A06","水阀控制",{"$f":"AH114&\"-\"&AK114","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH114,List!$B$3:$D$445,2,FALSE)&AJ114&\"_\"&VLOOKUP(AK114,List!$K$2:$M$447,2,FALSE)","v":"AHU03A06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM114&\" \"&\"AT%Q\"&B114*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J114&\"*)\",\" \")","v":"LAHU03A06_WVC AT%Q130.0 :INT ; (*空调机组NJ-3AP(KT)1-6-水阀控制*)"},"LAHU03A06_WVC           AT%Q130.0      :INT ; (*空调机组NJ-3AP(KT)1-6-水阀控制*)",null,"AHU03A06_WVC",{"$f":"J114","v":"空调机组NJ-3AP(KT)1-6-水阀控制"},{"$f":"AS113+1","v":40065}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH115&AA115&\"-\"&AK115","v":"空调机组NJ-3AP(KT)1-7-水阀控制"},{"$nulls":16},"NJ-3AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)1-7","03A07","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH115,List!$B$3:$D$445,2,FALSE)&AJ115&\"_\"&VLOOKUP(AK115,List!$K$2:$M$447,2,FALSE)","v":"AHU03A07_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM115&\" \"&\"AT%Q\"&B114*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J115&\"*)\",\" \")","v":"LAHU03A07_WVC AT%Q132.0 :INT ; (*空调机组NJ-3AP(KT)1-7-水阀控制*)"},"LAHU03A07_WVC           AT%Q132.0      :INT ; (*空调机组NJ-3AP(KT)1-7-水阀控制*)",null,"AHU03A07_WVC","空调机组NJ-3AP(KT)1-7-水阀控制",{"$f":"AS114+1","v":40066}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH116&AA116&\"-\"&AK116","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH116,List!$B$3:$D$445,2,FALSE)&AJ116&\"_\"&VLOOKUP(AK116,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM116&\" \"&\"AT%Q\"&B114*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J116&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40067]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L401","index":22,"n_rows":119,"n_cols":45,"rows_kept":119,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[41,5,41,6],[41,9,41,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[75,5,75,6],[75,9,75,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[84,5,84,6],[84,9,84,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[93,5,93,6],[93,9,93,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[102,5,102,6],[102,9,102,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[109,5,109,6],[109,9,109,25],[111,5,111,6],[111,9,111,25],[112,5,112,6],[112,9,112,25],[113,5,113,6],[113,9,113,25],[114,5,114,6],[114,9,114,25],[115,5,115,6],[115,9,115,25],[116,5,116,6],[116,9,116,25],[117,5,117,6],[117,9,117,25],[118,5,118,6],[118,9,118,25],[4,1,5,1],[11,1,22,1],[28,1,39,1],[45,1,56,1],[62,1,73,1],[79,1,82,1],[88,1,91,1],[97,1,100,1],[106,1,109,1],[115,1,118,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4],[32,2,39,4],[49,2,56,4],[66,2,73,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L19",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 9 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH8&AA8&\"-\"&AK8","v":"空调机组NJ-4AP(KT)1-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-4AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-1","04A01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH8,List!$B$3:$D$445,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,List!$K$2:$M$447,2,FALSE)","v":"AHU04A01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LAHU04A01_R AT%I144.0 :BOOL; (*空调机组NJ-4AP(KT)1-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LAHU04A01_R             AT%I144.0      :BOOL; (*空调机组NJ-4AP(KT)1-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L19\\L19AHU04A01_R"},{"$f":"J8","v":"空调机组NJ-4AP(KT)1-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":11152}]
[null,9,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-4AP(KT)1-1-故障状态",{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-4AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-1","04A01","故障状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU04A01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU04A01_F AT%I144.1 :BOOL; (*空调机组NJ-4AP(KT)1-1-故障状态*)"},"LAHU04A01_F             AT%I144.1      :BOOL; (*空调机组NJ-4AP(KT)1-1-故障状态*)",null,"L19\\L19AHU04A01_F",{"$f":"J9","v":"空调机组NJ-4AP(KT)1-1-故障状态"},{"$f":"AS8+1","v":11153}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-4AP(KT)1-1-自动状态",{"$nulls":16},"NJ-4AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-1","04A01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU04A01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU04A01_A AT%I144.2 :BOOL; (*空调机组NJ-4AP(KT)1-1-自动状态*)"},"LAHU04A01_A             AT%I144.2      :BOOL; (*空调机组NJ-4AP(KT)1-1-自动状态*)",null,"L19\\L19AHU04A01_A","空调机组NJ-4AP(KT)1-1-自动状态",{"$f":"AS9+1","v":11154}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-4AP(KT)1-1-风机压差",{"$nulls":16},"NJ-4AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-1","04A01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU04A01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU04A01_FPS AT%I144.3 :BOOL; (*空调机组NJ-4AP(KT)1-1-风机压差*)"},"LAHU04A01_FPS           AT%I144.3      :BOOL; (*空调机组NJ-4AP(KT)1-1-风机压差*)",null,"L19\\L19AHU04A01_FPS","空调机组NJ-4AP(KT)1-1-风机压差",11155]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-4AP(KT)1-2-运行状态",{"$nulls":16},"NJ-4AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-2","04A02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU04A02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU04A02_R AT%I144.4 :BOOL; (*空调机组NJ-4AP(KT)1-2-运行状态*)"},"LAHU04A02_R             AT%I144.4      :BOOL; (*空调机组NJ-4AP(KT)1-2-运行状态*)",null,"L19\\L19AHU04A02_R","空调机组NJ-4AP(KT)1-2-运行状态",11156]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-4AP(KT)1-2-故障状态",{"$nulls":16},"NJ-4AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-2","04A02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU04A02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU04A02_F AT%I144.5 :BOOL; (*空调机组NJ-4AP(KT)1-2-故障状态*)"},"LAHU04A02_F             AT%I144.5      :BOOL; (*空调机组NJ-4AP(KT)1-2-故障状态*)",null,"L19\\L19AHU04A02_F","空调机组NJ-4AP(KT)1-2-故障状态",11157]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-4AP(KT)1-2-自动状态",{"$nulls":16},"NJ-4AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-2","04A02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU04A02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU04A02_A AT%I144.6 :BOOL; (*空调机组NJ-4AP(KT)1-2-自动状态*)"},"LAHU04A02_A             AT%I144.6      :BOOL; (*空调机组NJ-4AP(KT)1-2-自动状态*)",null,"L19\\L19AHU04A02_A","空调机组NJ-4AP(KT)1-2-自动状态",11158]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-4AP(KT)1-2-风机压差",{"$nulls":16},"NJ-4AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-2","04A02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU04A02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU04A02_FPS AT%I144.7 :BOOL; (*空调机组NJ-4AP(KT)1-2-风机压差*)"},"LAHU04A02_FPS           AT%I144.7      :BOOL; (*空调机组NJ-4AP(KT)1-2-风机压差*)",null,"L19\\L19AHU04A02_FPS","空调机组NJ-4AP(KT)1-2-风机压差",11159]
[{"$nulls":5},9,null,17,18,"空调机组NJ-4AP(KT)1-3-运行状态",{"$nulls":16},"NJ-4AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-3","04A03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU04A03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU04A03_R AT%I145.0 :BOOL; (*空调机组NJ-4AP(KT)1-3-运行状态*)"},"LAHU04A03_R             AT%I145.0      :BOOL; (*空调机组NJ-4AP(KT)1-3-运行状态*)",null,"L19\\L19AHU04A03_R","空调机组NJ-4AP(KT)1-3-运行状态",11160]
[{"$nulls":5},10,null,19,20,"空调机组NJ-4AP(KT)1-3-故障状态",{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-4AP(KT)1-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-3","04A03","故障状态",{"$f":"AH17&\"-\"&AK17","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU04A03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU04A03_F AT%I145.1 :BOOL; (*空调机组NJ-4AP(KT)1-3-故障状态*)"},"LAHU04A03_F             AT%I145.1      :BOOL; (*空调机组NJ-4AP(KT)1-3-故障状态*)",null,"L19\\L19AHU04A03_F","空调机组NJ-4AP(KT)1-3-故障状态",11161]
[{"$nulls":5},11,null,21,22,"空调机组NJ-4AP(KT)1-3-自动状态",{"$nulls":16},"NJ-4AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-3","04A03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU04A03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU04A03_A AT%I145.2 :BOOL; (*空调机组NJ-4AP(KT)1-3-自动状态*)"},"LAHU04A03_A             AT%I145.2      :BOOL; (*空调机组NJ-4AP(KT)1-3-自动状态*)",null,"L19\\L19AHU04A03_A","空调机组NJ-4AP(KT)1-3-自动状态",11162]
[{"$nulls":5},12,null,23,24,"空调机组NJ-4AP(KT)1-3-风机压差",{"$nulls":16},"NJ-4AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-3","04A03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU04A03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU04A03_FPS AT%I145.3 :BOOL; (*空调机组NJ-4AP(KT)1-3-风机压差*)"},"LAHU04A03_FPS           AT%I145.3      :BOOL; (*空调机组NJ-4AP(KT)1-3-风机压差*)",null,"L19\\L19AHU04A03_FPS","空调机组NJ-4AP(KT)1-3-风机压差",11163]
[{"$nulls":5},13,null,25,26,"空调机组NJ-4AP(KT)1-4-运行状态",{"$nulls":16},"NJ-4AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-4","04A04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU04A04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU04A04_R AT%I145.4 :BOOL; (*空调机组NJ-4AP(KT)1-4-运行状态*)"},"LAHU04A04_R             AT%I145.4      :BOOL; (*空调机组NJ-4AP(KT)1-4-运行状态*)",null,"L19\\L19AHU04A04_R","空调机组NJ-4AP(KT)1-4-运行状态",11164]
[{"$nulls":5},14,null,27,28,"空调机组NJ-4AP(KT)1-4-故障状态",{"$nulls":16},"NJ-4AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-4","04A04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU04A04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU04A04_F AT%I145.5 :BOOL; (*空调机组NJ-4AP(KT)1-4-故障状态*)"},"LAHU04A04_F             AT%I145.5      :BOOL; (*空调机组NJ-4AP(KT)1-4-故障状态*)",null,"L19\\L19AHU04A04_F","空调机组NJ-4AP(KT)1-4-故障状态",11165]
[{"$nulls":5},15,null,29,30,"空调机组NJ-4AP(KT)1-4-自动状态",{"$nulls":16},"NJ-4AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-4","04A04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU04A04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU04A04_A AT%I145.6 :BOOL; (*空调机组NJ-4AP(KT)1-4-自动状态*)"},"LAHU04A04_A             AT%I145.6      :BOOL; (*空调机组NJ-4AP(KT)1-4-自动状态*)",null,"L19\\L19AHU04A04_A","空调机组NJ-4AP(KT)1-4-自动状态",11166]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-4AP(KT)1-4-风机压差",{"$nulls":16},"NJ-4AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-4","04A04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU04A04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU04A04_FPS AT%I145.7 :BOOL; (*空调机组NJ-4AP(KT)1-4-风机压差*)"},"LAHU04A04_FPS           AT%I145.7      :BOOL; (*空调机组NJ-4AP(KT)1-4-风机压差*)",null,"L19\\L19AHU04A04_FPS","空调机组NJ-4AP(KT)1-4-风机压差",11167]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 1601R地址: 10 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH25&AA25&\"-\"&AK25","v":"空调机组NJ-4AP(KT)1-5-运行状态"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-4AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-5","04A05","运行状态",{"$f":"AH25&\"-\"&AK25","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"AHU04A05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LAHU04A05_R AT%I160.0 :BOOL; (*空调机组NJ-4AP(KT)1-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LAHU04A05_R             AT%I160.0      :BOOL; (*空调机组NJ-4AP(KT)1-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L19\\L19AHU04A05_R"},{"$f":"J25","v":"空调机组NJ-4AP(KT)1-5-运行状态"},{"$f":"10000+($B26*16*8+F25-1)","v":11280}]
[null,10,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},2,null,3,4,"空调机组NJ-4AP(KT)1-5-故障状态",{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-4AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-5","04A05","故障状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU04A05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU04A05_F AT%I160.1 :BOOL; (*空调机组NJ-4AP(KT)1-5-故障状态*)"},"LAHU04A05_F             AT%I160.1      :BOOL; (*空调机组NJ-4AP(KT)1-5-故障状态*)",null,"L19\\L19AHU04A05_F",{"$f":"J26","v":"空调机组NJ-4AP(KT)1-5-故障状态"},{"$f":"AS25+1","v":11281}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-4AP(KT)1-5-自动状态",{"$nulls":16},"NJ-4AP(KT)1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-5","04A05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU04A05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU04A05_A AT%I160.2 :BOOL; (*空调机组NJ-4AP(KT)1-5-自动状态*)"},"LAHU04A05_A             AT%I160.2      :BOOL; (*空调机组NJ-4AP(KT)1-5-自动状态*)",null,"L19\\L19AHU04A05_A","空调机组NJ-4AP(KT)1-5-自动状态",{"$f":"AS26+1","v":11282}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-4AP(KT)1-5-风机压差",{"$nulls":16},"NJ-4AP(KT)1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-5","04A05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU04A05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU04A05_FPS AT%I160.3 :BOOL; (*空调机组NJ-4AP(KT)1-5-风机压差*)"},"LAHU04A05_FPS           AT%I160.3      :BOOL; (*空调机组NJ-4AP(KT)1-5-风机压差*)",null,"L19\\L19AHU04A05_FPS","空调机组NJ-4AP(KT)1-5-风机压差",11283]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-4AP(KT)1-6-运行状态",{"$nulls":16},"NJ-4AP(KT)1-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-6","04A06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU04A06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU04A06_R AT%I160.4 :BOOL; (*空调机组NJ-4AP(KT)1-6-运行状态*)"},"LAHU04A06_R             AT%I160.4      :BOOL; (*空调机组NJ-4AP(KT)1-6-运行状态*)",null,"L19\\L19AHU04A06_R","空调机组NJ-4AP(KT)1-6-运行状态",11284]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-4AP(KT)1-6-故障状态",{"$nulls":16},"NJ-4AP(KT)1-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-6","04A06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU04A06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU04A06_F AT%I160.5 :BOOL; (*空调机组NJ-4AP(KT)1-6-故障状态*)"},"LAHU04A06_F             AT%I160.5      :BOOL; (*空调机组NJ-4AP(KT)1-6-故障状态*)",null,"L19\\L19AHU04A06_F","空调机组NJ-4AP(KT)1-6-故障状态",11285]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-4AP(KT)1-6-自动状态",{"$nulls":16},"NJ-4AP(KT)1-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-6","04A06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU04A06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU04A06_A AT%I160.6 :BOOL; (*空调机组NJ-4AP(KT)1-6-自动状态*)"},"LAHU04A06_A             AT%I160.6      :BOOL; (*空调机组NJ-4AP(KT)1-6-自动状态*)",null,"L19\\L19AHU04A06_A","空调机组NJ-4AP(KT)1-6-自动状态",11286]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-4AP(KT)1-6-风机压差",{"$nulls":16},"NJ-4AP(KT)1-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-6","04A06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU04A06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU04A06_FPS AT%I160.7 :BOOL; (*空调机组NJ-4AP(KT)1-6-风机压差*)"},"LAHU04A06_FPS           AT%I160.7      :BOOL; (*空调机组NJ-4AP(KT)1-6-风机压差*)",null,"L19\\L19AHU04A06_FPS","空调机组NJ-4AP(KT)1-6-风机压差",11287]
[{"$nulls":5},9,null,17,18,"空调机组NJ-4AP(KT)1-7-运行状态",{"$nulls":16},"NJ-4AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-7","04A07","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU04A07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B26*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU04A07_R AT%I161.0 :BOOL; (*空调机组NJ-4AP(KT)1-7-运行状态*)"},"LAHU04A07_R             AT%I161.0      :BOOL; (*空调机组NJ-4AP(KT)1-7-运行状态*)",null,"L19\\L19AHU04A07_R","空调机组NJ-4AP(KT)1-7-运行状态",11288]
[{"$nulls":5},10,null,19,20,"空调机组NJ-4AP(KT)1-7-故障状态",{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-4AP(KT)1-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-7","04A07","故障状态",{"$f":"AH34&\"-\"&AK34","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU04A07_F"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B26*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU04A07_F AT%I161.1 :BOOL; (*空调机组NJ-4AP(KT)1-7-故障状态*)"},"LAHU04A07_F             AT%I161.1      :BOOL; (*空调机组NJ-4AP(KT)1-7-故障状态*)",null,"L19\\L19AHU04A07_F",{"$f":"J34","v":"空调机组NJ-4AP(KT)1-7-故障状态"},11289]
[{"$nulls":5},11,null,21,22,"空调机组NJ-4AP(KT)1-7-自动状态",{"$nulls":16},"NJ-4AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-7","04A07","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU04A07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B26*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU04A07_A AT%I161.2 :BOOL; (*空调机组NJ-4AP(KT)1-7-自动状态*)"},"LAHU04A07_A             AT%I161.2      :BOOL; (*空调机组NJ-4AP(KT)1-7-自动状态*)",null,"L19\\L19AHU04A07_A","空调机组NJ-4AP(KT)1-7-自动状态",11290]
[{"$nulls":5},12,null,23,24,"空调机组NJ-4AP(KT)1-7-风机压差",{"$nulls":16},"NJ-4AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-7","04A07","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU04A07_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B26*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU04A07_FPS AT%I161.3 :BOOL; (*空调机组NJ-4AP(KT)1-7-风机压差*)"},"LAHU04A07_FPS           AT%I161.3      :BOOL; (*空调机组NJ-4AP(KT)1-7-风机压差*)",null,"L19\\L19AHU04A07_FPS","空调机组NJ-4AP(KT)1-7-风机压差",11291]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-4AL1-1-运行状态",{"$nulls":16},"NJ-4AL1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL1-1","04A01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"LCB04A01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B26*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LLCB04A01_R AT%I161.4 :BOOL; (*照明控制箱NJ-4AL1-1-运行状态*)"},"LLCB04A01_R             AT%I161.4      :BOOL; (*照明控制箱NJ-4AL1-1-运行状态*)",null,"L19\\L19LCB04A01_R","照明控制箱NJ-4AL1-1-运行状态",11292]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-4AL1-1-自动状态",{"$nulls":16},"NJ-4AL1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL1-1","04A01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB04A01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B26*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB04A01_A AT%I161.5 :BOOL; (*照明控制箱NJ-4AL1-1-自动状态*)"},"LLCB04A01_A             AT%I161.5      :BOOL; (*照明控制箱NJ-4AL1-1-自动状态*)",null,"L19\\L19LCB04A01_A","照明控制箱NJ-4AL1-1-自动状态",11293]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-4AL1-2-运行状态",{"$nulls":16},"NJ-4AL1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL1-2","04A02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB04A02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B26*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB04A02_R AT%I161.6 :BOOL; (*照明控制箱NJ-4AL1-2-运行状态*)"},"LLCB04A02_R             AT%I161.6      :BOOL; (*照明控制箱NJ-4AL1-2-运行状态*)",null,"L19\\L19LCB04A02_R","照明控制箱NJ-4AL1-2-运行状态",11294]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-4AL1-2-自动状态",{"$nulls":16},"NJ-4AL1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL1-2","04A02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"LCB04A02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B26*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LLCB04A02_A AT%I161.7 :BOOL; (*照明控制箱NJ-4AL1-2-自动状态*)"},"LLCB04A02_A             AT%I161.7      :BOOL; (*照明控制箱NJ-4AL1-2-自动状态*)",null,"L19\\L19LCB04A02_A","照明控制箱NJ-4AL1-2-自动状态",11295]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B46&\"地址: \"&B43&\" *)\"","v":"(* IOM 1601R地址: 11 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH42&AA42&\"-\"&AK42","v":"照明控制箱NJ-4AL1-3-运行状态"},{"$nulls":16},{"$f":"IF(AI42=\"\",\"\",AI42)","v":"NJ-4AL1-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL1-3","04A03","运行状态",{"$f":"AH42&\"-\"&AK42","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":"LCB04A03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%I\"&B43*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":"LLCB04A03_R AT%I176.0 :BOOL; (*照明控制箱NJ-4AL1-3-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42))),SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))))),\" \")","v":"LLCB04A03_R             AT%I176.0      :BOOL; (*照明控制箱NJ-4AL1-3-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM42","v":"L19\\L19LCB04A03_R"},{"$f":"J42","v":"照明控制箱NJ-4AL1-3-运行状态"},{"$f":"10000+($B43*16*8+F42-1)","v":11408}]
[null,11,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},2,null,3,4,"照明控制箱NJ-4AL1-3-自动状态",{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-4AL1-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL1-3","04A03","自动状态",{"$f":"AH43&\"-\"&AK43","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"LCB04A03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B43*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LLCB04A03_A AT%I176.1 :BOOL; (*照明控制箱NJ-4AL1-3-自动状态*)"},"LLCB04A03_A             AT%I176.1      :BOOL; (*照明控制箱NJ-4AL1-3-自动状态*)",null,"L19\\L19LCB04A03_A",{"$f":"J43","v":"照明控制箱NJ-4AL1-3-自动状态"},{"$f":"AS42+1","v":11409}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":0},3,null,5,6,"照明控制箱NJ-4AL1-4-运行状态",{"$nulls":16},"NJ-4AL1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL1-4","04A04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"LCB04A04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B43*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LLCB04A04_R AT%I176.2 :BOOL; (*照明控制箱NJ-4AL1-4-运行状态*)"},"LLCB04A04_R             AT%I176.2      :BOOL; (*照明控制箱NJ-4AL1-4-运行状态*)",null,"L19\\L19LCB04A04_R","照明控制箱NJ-4AL1-4-运行状态",{"$f":"AS43+1","v":11410}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},4,null,7,8,"照明控制箱NJ-4AL1-4-自动状态",{"$nulls":16},"NJ-4AL1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL1-4","04A04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"LCB04A04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B43*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LLCB04A04_A AT%I176.3 :BOOL; (*照明控制箱NJ-4AL1-4-自动状态*)"},"LLCB04A04_A             AT%I176.3      :BOOL; (*照明控制箱NJ-4AL1-4-自动状态*)",null,"L19\\L19LCB04A04_A","照明控制箱NJ-4AL1-4-自动状态",11411]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-4AL1-5-运行状态",{"$nulls":16},"NJ-4AL1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL1-5","04A05","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"LCB04A05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B43*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LLCB04A05_R AT%I176.4 :BOOL; (*照明控制箱NJ-4AL1-5-运行状态*)"},"LLCB04A05_R             AT%I176.4      :BOOL; (*照明控制箱NJ-4AL1-5-运行状态*)",null,"L19\\L19LCB04A05_R","照明控制箱NJ-4AL1-5-运行状态",11412]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-4AL1-5-自动状态",{"$nulls":16},"NJ-4AL1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL1-5","04A05","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"LCB04A05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B43*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LLCB04A05_A AT%I176.5 :BOOL; (*照明控制箱NJ-4AL1-5-自动状态*)"},"LLCB04A05_A             AT%I176.5      :BOOL; (*照明控制箱NJ-4AL1-5-自动状态*)",null,"L19\\L19LCB04A05_A","照明控制箱NJ-4AL1-5-自动状态",11413]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"排风机NJ-4AP(KT)1-1-运行状态",{"$nulls":16},"NJ-4AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)1-1","04A01","运行状态","排风机-运行状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"EAF04A01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B43*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LEAF04A01_R AT%I176.6 :BOOL; (*排风机NJ-4AP(KT)1-1-运行状态*)"},"LEAF04A01_R             AT%I176.6      :BOOL; (*排风机NJ-4AP(KT)1-1-运行状态*)",null,"L19\\L19EAF04A01_R","排风机NJ-4AP(KT)1-1-运行状态",11414]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"排风机NJ-4AP(KT)1-1-故障状态",{"$nulls":16},"NJ-4AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)1-1","04A01","故障状态","排风机-故障状态",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"EAF04A01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B43*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LEAF04A01_F AT%I176.7 :BOOL; (*排风机NJ-4AP(KT)1-1-故障状态*)"},"LEAF04A01_F             AT%I176.7      :BOOL; (*排风机NJ-4AP(KT)1-1-故障状态*)",null,"L19\\L19EAF04A01_F","排风机NJ-4AP(KT)1-1-故障状态",11415]
[{"$nulls":5},9,null,17,18,"排风机NJ-4AP(KT)1-1-自动状态",{"$nulls":16},"NJ-4AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)1-1","04A01","自动状态","排风机-自动状态",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"EAF04A01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B43*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LEAF04A01_A AT%I177.0 :BOOL; (*排风机NJ-4AP(KT)1-1-自动状态*)"},"LEAF04A01_A             AT%I177.0      :BOOL; (*排风机NJ-4AP(KT)1-1-自动状态*)",null,"L19\\L19EAF04A01_A","排风机NJ-4AP(KT)1-1-自动状态",11416]
[{"$nulls":5},10,null,19,20,"遮阳帘-运行状态",{"$nulls":16},{"$f":"IF(AI51=\"\",\"\",AI51)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04A01","运行状态",{"$f":"AH51&\"-\"&AK51","v":"遮阳帘-运行状态"},{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"SSC04A01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B43*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LSSC04A01_R AT%I177.1 :BOOL; (*遮阳帘-运行状态*)"},"LSSC04A01_R             AT%I177.1      :BOOL; (*遮阳帘-运行状态*)",null,"L19\\L19SSC04A01_R",{"$f":"J51","v":"遮阳帘-运行状态"},11417]
[{"$nulls":5},11,null,21,22,"遮阳帘-自动状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04A01","自动状态","遮阳帘-自动状态",{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"SSC04A01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%I\"&B43*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LSSC04A01_A AT%I177.2 :BOOL; (*遮阳帘-自动状态*)"},"LSSC04A01_A             AT%I177.2      :BOOL; (*遮阳帘-自动状态*)",null,"L19\\L19SSC04A01_A","遮阳帘-自动状态",11418]
[{"$nulls":5},12,null,23,24,"遮阳帘-运行状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04A02","运行状态","遮阳帘-运行状态",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"SSC04A02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%I\"&B43*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LSSC04A02_R AT%I177.3 :BOOL; (*遮阳帘-运行状态*)"},"LSSC04A02_R             AT%I177.3      :BOOL; (*遮阳帘-运行状态*)",null,"L19\\L19SSC04A02_R","遮阳帘-运行状态",11419]
[{"$nulls":5},13,null,25,26,"遮阳帘-自动状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04A02","自动状态","遮阳帘-自动状态",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"SSC04A02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%I\"&B43*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LSSC04A02_A AT%I177.4 :BOOL; (*遮阳帘-自动状态*)"},"LSSC04A02_A             AT%I177.4      :BOOL; (*遮阳帘-自动状态*)",null,"L19\\L19SSC04A02_A","遮阳帘-自动状态",11420]
[{"$nulls":5},14,null,27,28,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%I\"&B43*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN55,SEARCH(\"AT%\",AN55),,REPT(\" \",30-SEARCH(\"AT%\",AN55))),SEARCH(\":\",REPLACE(AN55,SEARCH(\"AT%\",AN55),,REPT(\" \",30-SEARCH(\"AT%\",AN55)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN55,SEARCH(\"AT%\",AN55),,REPT(\" \",25-SEARCH(\"AT%\",AN55)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",11421]
[{"$nulls":5},15,null,29,30,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%I\"&B43*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11422]
[".",{"$nulls":4},16,null,31,32,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%I\"&B43*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11423]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B63&\"地址: \"&B60&\" *)\"","v":"(* IOM 1601D地址: 12 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH59&AA59&\"-\"&AK59","v":"空调机组NJ-4AP(KT)1-1-启停控制"},{"$nulls":16},{"$f":"IF(AI59=\"\",\"\",AI59)","v":"NJ-4AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-1","04A01","启停控制",{"$f":"AH59&\"-\"&AK59","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH59,List!$B$3:$D$445,2,FALSE)&AJ59&\"_\"&VLOOKUP(AK59,List!$K$2:$M$447,2,FALSE)","v":"AHU04A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM59&\" \"&\"AT%Q\"&B60*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J59&\"*)\",\" \")","v":"LAHU04A01_C AT%Q192.0 :BOOL; (*空调机组NJ-4AP(KT)1-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59))),SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))))),\" \")","v":"LAHU04A01_C             AT%Q192.0      :BOOL; (*空调机组NJ-4AP(KT)1-1-启停控制*)"},null,{"$f":"AM59","v":"AHU04A01_C"},{"$f":"J59","v":"空调机组NJ-4AP(KT)1-1-启停控制"},{"$f":"($B60*16*8+F59-1)","v":1536}]
[null,12,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","空调机组NJ-4AP(KT)1-2-启停控制",{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-4AP(KT)1-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-2","04A02","启停控制",{"$f":"AH60&\"-\"&AK60","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"AHU04A02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%Q\"&B60*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LAHU04A02_C AT%Q192.1 :BOOL; (*空调机组NJ-4AP(KT)1-2-启停控制*)"},"LAHU04A02_C             AT%Q192.1      :BOOL; (*空调机组NJ-4AP(KT)1-2-启停控制*)",null,"AHU04A02_C",{"$f":"J60","v":"空调机组NJ-4AP(KT)1-2-启停控制"},{"$f":"AS59+1","v":1537}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-4AP(KT)1-3-启停控制",{"$nulls":16},"NJ-4AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-3","04A03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"AHU04A03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%Q\"&B60*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LAHU04A03_C AT%Q192.2 :BOOL; (*空调机组NJ-4AP(KT)1-3-启停控制*)"},"LAHU04A03_C             AT%Q192.2      :BOOL; (*空调机组NJ-4AP(KT)1-3-启停控制*)",null,"AHU04A03_C","空调机组NJ-4AP(KT)1-3-启停控制",{"$f":"AS60+1","v":1538}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","空调机组NJ-4AP(KT)1-4-启停控制",{"$nulls":16},"NJ-4AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-4","04A04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"AHU04A04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%Q\"&B60*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LAHU04A04_C AT%Q192.3 :BOOL; (*空调机组NJ-4AP(KT)1-4-启停控制*)"},"LAHU04A04_C             AT%Q192.3      :BOOL; (*空调机组NJ-4AP(KT)1-4-启停控制*)",null,"AHU04A04_C","空调机组NJ-4AP(KT)1-4-启停控制",1539]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-4AP(KT)1-5-启停控制",{"$nulls":16},"NJ-4AP(KT)1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-5","04A05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"AHU04A05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%Q\"&B60*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LAHU04A05_C AT%Q192.4 :BOOL; (*空调机组NJ-4AP(KT)1-5-启停控制*)"},"LAHU04A05_C             AT%Q192.4      :BOOL; (*空调机组NJ-4AP(KT)1-5-启停控制*)",null,"AHU04A05_C","空调机组NJ-4AP(KT)1-5-启停控制",1540]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-4AP(KT)1-6-启停控制",{"$nulls":16},"NJ-4AP(KT)1-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-6","04A06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"AHU04A06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%Q\"&B60*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LAHU04A06_C AT%Q192.5 :BOOL; (*空调机组NJ-4AP(KT)1-6-启停控制*)"},"LAHU04A06_C             AT%Q192.5      :BOOL; (*空调机组NJ-4AP(KT)1-6-启停控制*)",null,"AHU04A06_C","空调机组NJ-4AP(KT)1-6-启停控制",1541]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","空调机组NJ-4AP(KT)1-7-启停控制",{"$nulls":16},"NJ-4AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-7","04A07","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":"AHU04A07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%Q\"&B60*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":"LAHU04A07_C AT%Q192.6 :BOOL; (*空调机组NJ-4AP(KT)1-7-启停控制*)"},"LAHU04A07_C             AT%Q192.6      :BOOL; (*空调机组NJ-4AP(KT)1-7-启停控制*)",null,"AHU04A07_C","空调机组NJ-4AP(KT)1-7-启停控制",1542]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-4AL1-1-启停控制",{"$nulls":16},"NJ-4AL1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL1-1","04A01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":"LCB04A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%Q\"&B60*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":"LLCB04A01_C AT%Q192.7 :BOOL; (*照明控制箱NJ-4AL1-1-启停控制*)"},"LLCB04A01_C             AT%Q192.7      :BOOL; (*照明控制箱NJ-4AL1-1-启停控制*)",null,"LCB04A01_C","照明控制箱NJ-4AL1-1-启停控制",1543]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-4AL1-2-启停控制",{"$nulls":16},"NJ-4AL1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL1-2","04A02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":"LCB04A02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%Q\"&B60*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":"LLCB04A02_C AT%Q193.0 :BOOL; (*照明控制箱NJ-4AL1-2-启停控制*)"},"LLCB04A02_C             AT%Q193.0      :BOOL; (*照明控制箱NJ-4AL1-2-启停控制*)",null,"LCB04A02_C","照明控制箱NJ-4AL1-2-启停控制",1544]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-4AL1-3-启停控制",{"$nulls":16},{"$f":"IF(AI68=\"\",\"\",AI68)","v":"NJ-4AL1-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL1-3","04A03","启停控制",{"$f":"AH68&\"-\"&AK68","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"LCB04A03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%Q\"&B60*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LLCB04A03_C AT%Q193.1 :BOOL; (*照明控制箱NJ-4AL1-3-启停控制*)"},"LLCB04A03_C             AT%Q193.1      :BOOL; (*照明控制箱NJ-4AL1-3-启停控制*)",null,"LCB04A03_C",{"$f":"J68","v":"照明控制箱NJ-4AL1-3-启停控制"},1545]
[{"$nulls":5},11,null,"11+","11-","照明控制箱NJ-4AL1-4-启停控制",{"$nulls":16},"NJ-4AL1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL1-4","04A04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"LCB04A04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%Q\"&B60*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LLCB04A04_C AT%Q193.2 :BOOL; (*照明控制箱NJ-4AL1-4-启停控制*)"},"LLCB04A04_C             AT%Q193.2      :BOOL; (*照明控制箱NJ-4AL1-4-启停控制*)",null,"LCB04A04_C","照明控制箱NJ-4AL1-4-启停控制",1546]
[{"$nulls":5},12,null,"12+","12-","照明控制箱NJ-4AL1-5-启停控制",{"$nulls":16},"NJ-4AL1-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL1-5","04A05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"LCB04A05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%Q\"&B60*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LLCB04A05_C AT%Q193.3 :BOOL; (*照明控制箱NJ-4AL1-5-启停控制*)"},"LLCB04A05_C             AT%Q193.3      :BOOL; (*照明控制箱NJ-4AL1-5-启停控制*)",null,"LCB04A05_C","照明控制箱NJ-4AL1-5-启停控制",1547]
[{"$nulls":5},13,null,"13+","13-","排风机NJ-4AP(KT)1-1-启停控制",{"$nulls":16},"NJ-4AP(KT)1-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)1-1","04A01","启停控制","排风机-启停控制",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"EAF04A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%Q\"&B60*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LEAF04A01_C AT%Q193.4 :BOOL; (*排风机NJ-4AP(KT)1-1-启停控制*)"},"LEAF04A01_C             AT%Q193.4      :BOOL; (*排风机NJ-4AP(KT)1-1-启停控制*)",null,"EAF04A01_C","排风机NJ-4AP(KT)1-1-启停控制",1548]
[{"$nulls":5},14,null,"14+","14-","遮阳帘-启停控制",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04A01","启停控制","遮阳帘-启停控制",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"SSC04A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%Q\"&B60*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LSSC04A01_C AT%Q193.5 :BOOL; (*遮阳帘-启停控制*)"},"LSSC04A01_C             AT%Q193.5      :BOOL; (*遮阳帘-启停控制*)",null,"SSC04A01_C","遮阳帘-启停控制",1549]
[{"$nulls":5},15,null,"15+","15-","遮阳帘-启停控制",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04A02","启停控制","遮阳帘-启停控制",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"SSC04A02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%Q\"&B60*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LSSC04A02_C AT%Q193.6 :BOOL; (*遮阳帘-启停控制*)"},"LSSC04A02_C             AT%Q193.6      :BOOL; (*遮阳帘-启停控制*)",null,"SSC04A02_C","遮阳帘-启停控制",1550]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%Q\"&B60*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1551]
[null,{"$f":"B80","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B80&\"地址: \"&B77&\" *)\"","v":"(* IOM 0801U地址: 13 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH76&AA76&\"-\"&AK76","v":"空调机组NJ-4AP(KT)1-1-回风温度"},{"$nulls":16},{"$f":"IF(AI76=\"\",\"\",AI76)","v":"NJ-4AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-1","04A01","回风温度",{"$f":"AH76&\"-\"&AK76","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH76,List!$B$3:$D$445,2,FALSE)&AJ76&\"_\"&VLOOKUP(AK76,List!$K$2:$M$447,2,FALSE)","v":"AHU04A01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM76&\" \"&\"AT%I\"&B77*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J76&\"*)\",\" \")","v":"LAHU04A01_RT AT%I208.0 :INT ; (*空调机组NJ-4AP(KT)1-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN76,SEARCH(\"AT%\",AN76),,REPT(\" \",25-SEARCH(\"AT%\",AN76))),SEARCH(\":\",REPLACE(AN76,SEARCH(\"AT%\",AN76),,REPT(\" \",25-SEARCH(\"AT%\",AN76)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN76,SEARCH(\"AT%\",AN76),,REPT(\" \",25-SEARCH(\"AT%\",AN76)))))),\" \")","v":"LAHU04A01_RT            AT%I208.0      :INT ; (*空调机组NJ-4AP(KT)1-1-回风温度*)"},null,{"$f":"AM76","v":"AHU04A01_RT"},{"$f":"J76","v":"空调机组NJ-4AP(KT)1-1-回风温度"},{"$f":"30000+($B77*8+F76-1)","v":30104}]
[null,13,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-4AP(KT)1-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-4AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-1","04A01","水阀反馈",{"$f":"AH77&\"-\"&AK77","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"AHU04A01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%I\"&B77*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LAHU04A01_WVB AT%I210.0 :INT ; (*空调机组NJ-4AP(KT)1-1-水阀反馈*)"},"LAHU04A01_WVB           AT%I210.0      :INT ; (*空调机组NJ-4AP(KT)1-1-水阀反馈*)",null,"AHU04A01_WVB",{"$f":"J77","v":"空调机组NJ-4AP(KT)1-1-水阀反馈"},{"$f":"AS76+1","v":30105}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-4AP(KT)1-2-回风温度",{"$nulls":16},"NJ-4AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-2","04A02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU04A02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%I\"&B77*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU04A02_RT AT%I212.0 :INT ; (*空调机组NJ-4AP(KT)1-2-回风温度*)"},"LAHU04A02_RT            AT%I212.0      :INT ; (*空调机组NJ-4AP(KT)1-2-回风温度*)",null,"AHU04A02_RT","空调机组NJ-4AP(KT)1-2-回风温度",{"$f":"AS77+1","v":30106}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-4AP(KT)1-2-水阀反馈",{"$nulls":16},"NJ-4AP(KT)1-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-2","04A02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU04A02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%I\"&B77*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU04A02_WVB AT%I214.0 :INT ; (*空调机组NJ-4AP(KT)1-2-水阀反馈*)"},"LAHU04A02_WVB           AT%I214.0      :INT ; (*空调机组NJ-4AP(KT)1-2-水阀反馈*)",null,"AHU04A02_WVB","空调机组NJ-4AP(KT)1-2-水阀反馈",30107]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-4AP(KT)1-3-回风温度",{"$nulls":16},"NJ-4AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-3","04A03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU04A03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%I\"&B77*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU04A03_RT AT%I216.0 :INT ; (*空调机组NJ-4AP(KT)1-3-回风温度*)"},"LAHU04A03_RT            AT%I216.0      :INT ; (*空调机组NJ-4AP(KT)1-3-回风温度*)",null,"AHU04A03_RT","空调机组NJ-4AP(KT)1-3-回风温度",30108]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-4AP(KT)1-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI81=\"\",\"\",AI81)","v":"NJ-4AP(KT)1-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-3","04A03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"AHU04A03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%I\"&B77*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LAHU04A03_WVB AT%I218.0 :INT ; (*空调机组NJ-4AP(KT)1-3-水阀反馈*)"},"LAHU04A03_WVB           AT%I218.0      :INT ; (*空调机组NJ-4AP(KT)1-3-水阀反馈*)",null,"AHU04A03_WVB",{"$f":"J81","v":"空调机组NJ-4AP(KT)1-3-水阀反馈"},30109]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-4AP(KT)1-4-回风温度",{"$nulls":16},"NJ-4AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-4","04A04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":"AHU04A04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%I\"&B77*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":"LAHU04A04_RT AT%I220.0 :INT ; (*空调机组NJ-4AP(KT)1-4-回风温度*)"},"LAHU04A04_RT            AT%I220.0      :INT ; (*空调机组NJ-4AP(KT)1-4-回风温度*)",null,"AHU04A04_RT","空调机组NJ-4AP(KT)1-4-回风温度",30110]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-4AP(KT)1-4-水阀反馈",{"$nulls":16},"NJ-4AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-4","04A04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":"AHU04A04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%I\"&B77*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":"LAHU04A04_WVB AT%I222.0 :INT ; (*空调机组NJ-4AP(KT)1-4-水阀反馈*)"},"LAHU04A04_WVB           AT%I222.0      :INT ; (*空调机组NJ-4AP(KT)1-4-水阀反馈*)",null,"AHU04A04_WVB","空调机组NJ-4AP(KT)1-4-水阀反馈",30111]
[null,{"$f":"B89","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B89&\"地址: \"&B86&\" *)\"","v":"(* IOM 0801U地址: 14 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH85&AA85&\"-\"&AK85","v":"空调机组NJ-4AP(KT)1-5-回风温度"},{"$nulls":16},{"$f":"IF(AI85=\"\",\"\",AI85)","v":"NJ-4AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-5","04A05","回风温度",{"$f":"AH85&\"-\"&AK85","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH85,List!$B$3:$D$445,2,FALSE)&AJ85&\"_\"&VLOOKUP(AK85,List!$K$2:$M$447,2,FALSE)","v":"AHU04A05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM85&\" \"&\"AT%I\"&B86*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J85&\"*)\",\" \")","v":"LAHU04A05_RT AT%I224.0 :INT ; (*空调机组NJ-4AP(KT)1-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN85,SEARCH(\"AT%\",AN85),,REPT(\" \",25-SEARCH(\"AT%\",AN85))),SEARCH(\":\",REPLACE(AN85,SEARCH(\"AT%\",AN85),,REPT(\" \",25-SEARCH(\"AT%\",AN85)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN85,SEARCH(\"AT%\",AN85),,REPT(\" \",25-SEARCH(\"AT%\",AN85)))))),\" \")","v":"LAHU04A05_RT            AT%I224.0      :INT ; (*空调机组NJ-4AP(KT)1-5-回风温度*)"},null,{"$f":"AM85","v":"AHU04A05_RT"},{"$f":"J85","v":"空调机组NJ-4AP(KT)1-5-回风温度"},{"$f":"30000+($B86*8+F85-1)","v":30112}]
[null,14,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-4AP(KT)1-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-4AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-5","04A05","水阀反馈",{"$f":"AH86&\"-\"&AK86","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"AHU04A05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%I\"&B86*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LAHU04A05_WVB AT%I226.0 :INT ; (*空调机组NJ-4AP(KT)1-5-水阀反馈*)"},"LAHU04A05_WVB           AT%I226.0      :INT ; (*空调机组NJ-4AP(KT)1-5-水阀反馈*)",null,"AHU04A05_WVB",{"$f":"J86","v":"空调机组NJ-4AP(KT)1-5-水阀反馈"},{"$f":"AS85+1","v":30113}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-4AP(KT)1-6-回风温度",{"$nulls":16},"NJ-4AP(KT)1-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-6","04A06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"AHU04A06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%I\"&B86*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LAHU04A06_RT AT%I228.0 :INT ; (*空调机组NJ-4AP(KT)1-6-回风温度*)"},"LAHU04A06_RT            AT%I228.0      :INT ; (*空调机组NJ-4AP(KT)1-6-回风温度*)",null,"AHU04A06_RT","空调机组NJ-4AP(KT)1-6-回风温度",{"$f":"AS86+1","v":30114}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-4AP(KT)1-6-水阀反馈",{"$nulls":16},"NJ-4AP(KT)1-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-6","04A06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"AHU04A06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%I\"&B86*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LAHU04A06_WVB AT%I230.0 :INT ; (*空调机组NJ-4AP(KT)1-6-水阀反馈*)"},"LAHU04A06_WVB           AT%I230.0      :INT ; (*空调机组NJ-4AP(KT)1-6-水阀反馈*)",null,"AHU04A06_WVB","空调机组NJ-4AP(KT)1-6-水阀反馈",30115]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-4AP(KT)1-7-回风温度",{"$nulls":16},"NJ-4AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-7","04A07","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"AHU04A07_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%I\"&B86*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LAHU04A07_RT AT%I232.0 :INT ; (*空调机组NJ-4AP(KT)1-7-回风温度*)"},"LAHU04A07_RT            AT%I232.0      :INT ; (*空调机组NJ-4AP(KT)1-7-回风温度*)",null,"AHU04A07_RT","空调机组NJ-4AP(KT)1-7-回风温度",30116]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-4AP(KT)1-7-水阀反馈",{"$nulls":16},"NJ-4AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-7","04A07","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":"AHU04A07_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%I\"&B86*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":"LAHU04A07_WVB AT%I234.0 :INT ; (*空调机组NJ-4AP(KT)1-7-水阀反馈*)"},"LAHU04A07_WVB           AT%I234.0      :INT ; (*空调机组NJ-4AP(KT)1-7-水阀反馈*)",null,"AHU04A07_WVB",{"$f":"J90","v":"空调机组NJ-4AP(KT)1-7-水阀反馈"},30117]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH91,List!$B$3:$D$445,2,FALSE)&AJ91&\"_\"&VLOOKUP(AK91,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM91&\" \"&\"AT%I\"&B86*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J91&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30118]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},{"$f":"IF(AI92=\"\",\"\",AI92)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH92,List!$B$3:$D$445,2,FALSE)&AJ92&\"_\"&VLOOKUP(AK92,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM92&\" \"&\"AT%I\"&B86*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J92&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30119]
[null,{"$f":"B98","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B98&\"地址: \"&B95&\" *)\"","v":"(* IOM 0401U地址: 15 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH94&AA94&\"-\"&AK94","v":"室内环境状态T-01-温度状态"},{"$nulls":16},{"$f":"IF(AI94=\"\",\"\",AI94)","v":"T-01"},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","T-01","04A01","温度状态",{"$f":"AH94&\"-\"&AK94","v":"室内环境状态-温度状态"},{"$f":"VLOOKUP(AH94,List!$B$3:$D$445,2,FALSE)&AJ94&\"_\"&VLOOKUP(AK94,List!$K$2:$M$447,2,FALSE)","v":"IES04A01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM94&\" \"&\"AT%I\"&B95*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J94&\"*)\",\" \")","v":"LIES04A01_T AT%I240.0 :INT ; (*室内环境状态T-01-温度状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94))),SEARCH(\":\",REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94)))))),\" \")","v":"LIES04A01_T             AT%I240.0      :INT ; (*室内环境状态T-01-温度状态*)"},null,{"$f":"AM94","v":"IES04A01_T"},{"$f":"J94","v":"室内环境状态T-01-温度状态"},{"$f":"30000+($B95*8+F94-1)","v":30120}]
[null,15,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),4,1))","v":1},2,null,2,"0V","室内环境状态T-02-温度状态",{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"T-02"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","T-02","04A02","温度状态",{"$f":"AH95&\"-\"&AK95","v":"室内环境状态-温度状态"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"IES04A02_T"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%I\"&B95*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LIES04A02_T AT%I242.0 :INT ; (*室内环境状态T-02-温度状态*)"},"LIES04A02_T             AT%I242.0      :INT ; (*室内环境状态T-02-温度状态*)",null,"IES04A02_T",{"$f":"J95","v":"室内环境状态T-02-温度状态"},{"$f":"AS94+1","v":30121}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),3,1))","v":1},3,null,3,"0V","室内环境状态CO2-01-二氧化碳浓度状态",{"$nulls":16},"CO2-01",{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","CO2-01","04A01","二氧化碳浓度状态","室内环境状态-二氧化碳浓度状态",{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"IES04A01_CO2"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%I\"&B95*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LIES04A01_CO2 AT%I244.0 :INT ; (*室内环境状态CO2-01-二氧化碳浓度状态*)"},"LIES04A01_CO2           AT%I244.0      :INT ; (*室内环境状态CO2-01-二氧化碳浓度状态*)",null,"IES04A01_CO2","室内环境状态CO2-01-二氧化碳浓度状态",{"$f":"AS95+1","v":30122}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),2,1))","v":1},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%I\"&B95*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30123]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),1,1))","v":0}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B107","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B107&\"地址: \"&B104&\" *)\"","v":"(* IOM 0401A地址: 16 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH103&AA103&\"-\"&AK103","v":"空调机组NJ-4AP(KT)1-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI103=\"\",\"\",AI103)","v":"NJ-4AP(KT)1-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-1","04A01","水阀控制",{"$f":"AH103&\"-\"&AK103","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH103,List!$B$3:$D$445,2,FALSE)&AJ103&\"_\"&VLOOKUP(AK103,List!$K$2:$M$447,2,FALSE)","v":"AHU04A01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM103&\" \"&\"AT%Q\"&B104*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J103&\"*)\",\" \")","v":"LAHU04A01_WVC AT%Q256.0 :INT ; (*空调机组NJ-4AP(KT)1-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103))),SEARCH(\":\",REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103)))))),\" \")","v":"LAHU04A01_WVC           AT%Q256.0      :INT ; (*空调机组NJ-4AP(KT)1-1-水阀控制*)"},null,{"$f":"AM103","v":"AHU04A01_WVC"},{"$f":"J103","v":"空调机组NJ-4AP(KT)1-1-水阀控制"},{"$f":"40000+($B104*8+F103-1)","v":40128}]
[null,16,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH104&AA104&\"-\"&AK104","v":"空调机组NJ-4AP(KT)1-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI104=\"\",\"\",AI104)","v":"NJ-4AP(KT)1-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-2","04A02","水阀控制",{"$f":"AH104&\"-\"&AK104","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"AHU04A02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%Q\"&B104*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LAHU04A02_WVC AT%Q258.0 :INT ; (*空调机组NJ-4AP(KT)1-2-水阀控制*)"},"LAHU04A02_WVC           AT%Q258.0      :INT ; (*空调机组NJ-4AP(KT)1-2-水阀控制*)",null,"AHU04A02_WVC",{"$f":"J104","v":"空调机组NJ-4AP(KT)1-2-水阀控制"},{"$f":"AS103+1","v":40129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH105&AA105&\"-\"&AK105","v":"空调机组NJ-4AP(KT)1-3-水阀控制"},{"$nulls":16},"NJ-4AP(KT)1-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-3","04A03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"AHU04A03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%Q\"&B104*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LAHU04A03_WVC AT%Q260.0 :INT ; (*空调机组NJ-4AP(KT)1-3-水阀控制*)"},"LAHU04A03_WVC           AT%Q260.0      :INT ; (*空调机组NJ-4AP(KT)1-3-水阀控制*)",null,"AHU04A03_WVC","空调机组NJ-4AP(KT)1-3-水阀控制",{"$f":"AS104+1","v":40130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH106&AA106&\"-\"&AK106","v":"空调机组NJ-4AP(KT)1-4-水阀控制"},{"$nulls":16},"NJ-4AP(KT)1-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-4","04A04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":"AHU04A04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%Q\"&B104*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":"LAHU04A04_WVC AT%Q262.0 :INT ; (*空调机组NJ-4AP(KT)1-4-水阀控制*)"},"LAHU04A04_WVC           AT%Q262.0      :INT ; (*空调机组NJ-4AP(KT)1-4-水阀控制*)",null,"AHU04A04_WVC","空调机组NJ-4AP(KT)1-4-水阀控制",40131]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B116","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B116&\"地址: \"&B113&\" *)\"","v":"(* IOM 0401A地址: 17 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH112&AA112&\"-\"&AK112","v":"空调机组NJ-4AP(KT)1-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI112=\"\",\"\",AI112)","v":"NJ-4AP(KT)1-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-5","04A05","水阀控制",{"$f":"AH112&\"-\"&AK112","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH112,List!$B$3:$D$445,2,FALSE)&AJ112&\"_\"&VLOOKUP(AK112,List!$K$2:$M$447,2,FALSE)","v":"AHU04A05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM112&\" \"&\"AT%Q\"&B113*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J112&\"*)\",\" \")","v":"LAHU04A05_WVC AT%Q272.0 :INT ; (*空调机组NJ-4AP(KT)1-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112))),SEARCH(\":\",REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112)))))),\" \")","v":"LAHU04A05_WVC           AT%Q272.0      :INT ; (*空调机组NJ-4AP(KT)1-5-水阀控制*)"},null,{"$f":"AM112","v":"AHU04A05_WVC"},{"$f":"J112","v":"空调机组NJ-4AP(KT)1-5-水阀控制"},{"$f":"40000+($B113*8+F112-1)","v":40136}]
[null,17,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH113&AA113&\"-\"&AK113","v":"空调机组NJ-4AP(KT)1-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI113=\"\",\"\",AI113)","v":"NJ-4AP(KT)1-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-6","04A06","水阀控制",{"$f":"AH113&\"-\"&AK113","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH113,List!$B$3:$D$445,2,FALSE)&AJ113&\"_\"&VLOOKUP(AK113,List!$K$2:$M$447,2,FALSE)","v":"AHU04A06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM113&\" \"&\"AT%Q\"&B113*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J113&\"*)\",\" \")","v":"LAHU04A06_WVC AT%Q274.0 :INT ; (*空调机组NJ-4AP(KT)1-6-水阀控制*)"},"LAHU04A06_WVC           AT%Q274.0      :INT ; (*空调机组NJ-4AP(KT)1-6-水阀控制*)",null,"AHU04A06_WVC",{"$f":"J113","v":"空调机组NJ-4AP(KT)1-6-水阀控制"},{"$f":"AS112+1","v":40137}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH114&AA114&\"-\"&AK114","v":"空调机组NJ-4AP(KT)1-7-水阀控制"},{"$nulls":16},"NJ-4AP(KT)1-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)1-7","04A07","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH114,List!$B$3:$D$445,2,FALSE)&AJ114&\"_\"&VLOOKUP(AK114,List!$K$2:$M$447,2,FALSE)","v":"AHU04A07_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM114&\" \"&\"AT%Q\"&B113*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J114&\"*)\",\" \")","v":"LAHU04A07_WVC AT%Q276.0 :INT ; (*空调机组NJ-4AP(KT)1-7-水阀控制*)"},"LAHU04A07_WVC           AT%Q276.0      :INT ; (*空调机组NJ-4AP(KT)1-7-水阀控制*)",null,"AHU04A07_WVC","空调机组NJ-4AP(KT)1-7-水阀控制",{"$f":"AS113+1","v":40138}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH115&AA115&\"-\"&AK115","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH115,List!$B$3:$D$445,2,FALSE)&AJ115&\"_\"&VLOOKUP(AK115,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM115&\" \"&\"AT%Q\"&B113*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J115&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40139]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L508","index":23,"n_rows":120,"n_cols":45,"rows_kept":120,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[41,5,41,6],[41,9,41,25],[4,1,5,1],[11,1,14,1],[20,1,23,1],[29,1,32,1],[38,1,41,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L01",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 0801R地址: 18 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH8&AA8&\"-\"&AK8","v":"F新风机组NJ-5AP(KT)1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-5AP(KT)1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)1","05H01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"F新风机组-运行状态"},{"$f":"VLOOKUP(AH8,[1]List!$D$3:$F$527,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05H01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LFAU05H01_R AT%I288.0 :BOOL; (*F新风机组NJ-5AP(KT)1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LFAU05H01_R             AT%I288.0      :BOOL; (*F新风机组NJ-5AP(KT)1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L01\\L01FAU05H01_R"},{"$f":"J8","v":"F新风机组NJ-5AP(KT)1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":12304}]
[null,18,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},2,null,2,"C","F新风机组NJ-5AP(KT)1-故障状态",{"$nulls":16},"NJ-5AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)1","05H01","故障状态","F新风机组-故障状态",{"$f":"VLOOKUP(AH9,[1]List!$D$3:$F$527,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05H01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LFAU05H01_F AT%I288.1 :BOOL; (*F新风机组NJ-5AP(KT)1-故障状态*)"},"LFAU05H01_F             AT%I288.1      :BOOL; (*F新风机组NJ-5AP(KT)1-故障状态*)",null,"L01\\L01FAU05H01_F","F新风机组NJ-5AP(KT)1-故障状态",{"$f":"AS8+1","v":12305}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},3,null,3,"C","F新风机组NJ-5AP(KT)1-自动状态",{"$nulls":16},"NJ-5AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)1","05H01","自动状态","F新风机组-自动状态",{"$f":"VLOOKUP(AH10,[1]List!$D$3:$F$527,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05H01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LFAU05H01_A AT%I288.2 :BOOL; (*F新风机组NJ-5AP(KT)1-自动状态*)"},"LFAU05H01_A             AT%I288.2      :BOOL; (*F新风机组NJ-5AP(KT)1-自动状态*)",null,"L01\\L01FAU05H01_A","F新风机组NJ-5AP(KT)1-自动状态",12306]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},4,null,4,"C","F新风机组NJ-5AP(KT)1-风机压差",{"$nulls":16},"NJ-5AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)1","05H01","风机压差","F新风机组-风机压差",{"$f":"VLOOKUP(AH11,[1]List!$D$3:$F$527,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05H01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LFAU05H01_FPS AT%I288.3 :BOOL; (*F新风机组NJ-5AP(KT)1-风机压差*)"},"LFAU05H01_FPS           AT%I288.3      :BOOL; (*F新风机组NJ-5AP(KT)1-风机压差*)",null,"L01\\L01FAU05H01_FPS","F新风机组NJ-5AP(KT)1-风机压差",12307]
[null,"IOM 0801R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},5,null,5,"C","F新风机组NJ-5AP(KT)1-初效滤网压差",{"$nulls":16},"NJ-5AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)1","05H01","初效滤网压差","F新风机组-初效滤网压差",{"$f":"VLOOKUP(AH12,[1]List!$D$3:$F$527,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05H01_IPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LFAU05H01_IPS AT%I288.4 :BOOL; (*F新风机组NJ-5AP(KT)1-初效滤网压差*)"},"LFAU05H01_IPS           AT%I288.4      :BOOL; (*F新风机组NJ-5AP(KT)1-初效滤网压差*)",null,"L01\\L01FAU05H01_IPS","F新风机组NJ-5AP(KT)1-初效滤网压差",12308]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","F新风机组NJ-5AP(KT)1-低温断路开关",{"$nulls":16},"NJ-5AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)1","05H01","低温断路开关","F新风机组-低温断路开关",{"$f":"VLOOKUP(AH13,[1]List!$D$3:$F$527,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05H01_AFS"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LFAU05H01_AFS AT%I288.5 :BOOL; (*F新风机组NJ-5AP(KT)1-低温断路开关*)"},"LFAU05H01_AFS           AT%I288.5      :BOOL; (*F新风机组NJ-5AP(KT)1-低温断路开关*)",null,"L01\\L01FAU05H01_AFS","F新风机组NJ-5AP(KT)1-低温断路开关",12309]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","F新风机组NJ-5AP(KT)1-新风阀开状态",{"$nulls":16},"NJ-5AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)1","05H01","新风阀开状态","F新风机组-新风阀开状态",{"$f":"VLOOKUP(AH14,[1]List!$D$3:$F$527,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05H01_FDOB"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LFAU05H01_FDOB AT%I288.6 :BOOL; (*F新风机组NJ-5AP(KT)1-新风阀开状态*)"},"LFAU05H01_FDOB          AT%I288.6      :BOOL; (*F新风机组NJ-5AP(KT)1-新风阀开状态*)",null,"L01\\L01FAU05H01_FDOB","F新风机组NJ-5AP(KT)1-新风阀开状态",12310]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","F新风机组NJ-5AP(KT)1-新风阀关状态",{"$nulls":16},"NJ-5AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)1","05H01","新风阀关状态","F新风机组-新风阀关状态",{"$f":"VLOOKUP(AH15,[1]List!$D$3:$F$527,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05H01_FDSB"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LFAU05H01_FDSB AT%I288.7 :BOOL; (*F新风机组NJ-5AP(KT)1-新风阀关状态*)"},"LFAU05H01_FDSB          AT%I288.7      :BOOL; (*F新风机组NJ-5AP(KT)1-新风阀关状态*)",null,"L01\\L01FAU05H01_FDSB","F新风机组NJ-5AP(KT)1-新风阀关状态",12311]
[null,{"$f":"B21","v":"IOM 0801D"},{"$nulls":38},{"$f":"\"(* \"&B21&\"地址: \"&B18&\" *)\"","v":"(* IOM 0801D地址: 19 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH17&AA17&\"-\"&AK17","v":"F新风机组NJ-5AP(KT)1-启停控制"},{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-5AP(KT)1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)1","05H01","启停控制",{"$f":"AH17&\"-\"&AK17","v":"F新风机组-启停控制"},{"$f":"VLOOKUP(AH17,[1]List!$D$3:$F$527,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05H01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%Q\"&B18*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LFAU05H01_C AT%Q304.0 :BOOL; (*F新风机组NJ-5AP(KT)1-启停控制*)"},"LFAU05H01_C             AT%Q304.0      :BOOL; (*F新风机组NJ-5AP(KT)1-启停控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM17","v":"L01\\L01FAU05H01_C"},{"$f":"J17","v":"F新风机组NJ-5AP(KT)1-启停控制"},{"$f":"($B18*16*8+F17-1)","v":2432}]
[null,19,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","F新风机组NJ-5AP(KT)1-新风阀开控制",{"$nulls":16},"NJ-5AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)1","05H01","新风阀开控制","F新风机组-新风阀开控制",{"$f":"VLOOKUP(AH18,[1]List!$D$3:$F$527,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05H01_FDOC"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%Q\"&B18*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LFAU05H01_FDOC AT%Q304.1 :BOOL; (*F新风机组NJ-5AP(KT)1-新风阀开控制*)"},"LFAU05H01_FDOC          AT%Q304.1      :BOOL; (*F新风机组NJ-5AP(KT)1-新风阀开控制*)",null,"L01\\L01FAU05H01_FDOC","F新风机组NJ-5AP(KT)1-新风阀开控制",{"$f":"AS17+1","v":2433}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","F新风机组NJ-5AP(KT)1-新风阀关控制",{"$nulls":16},"NJ-5AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)1","05H01","新风阀关控制","F新风机组-新风阀关控制",{"$f":"VLOOKUP(AH19,[1]List!$D$3:$F$527,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05H01_FDSC"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%Q\"&B18*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LFAU05H01_FDSC AT%Q304.2 :BOOL; (*F新风机组NJ-5AP(KT)1-新风阀关控制*)"},"LFAU05H01_FDSC          AT%Q304.2      :BOOL; (*F新风机组NJ-5AP(KT)1-新风阀关控制*)",null,"L01\\L01FAU05H01_FDSC","F新风机组NJ-5AP(KT)1-新风阀关控制",2434]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH20,[1]List!$D$3:$F$527,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%Q\"&B18*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN20,SEARCH(\"AT%\",AN20),,REPT(\" \",30-SEARCH(\"AT%\",AN20))),SEARCH(\":\",REPLACE(AN20,SEARCH(\"AT%\",AN20),,REPT(\" \",30-SEARCH(\"AT%\",AN20)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN20,SEARCH(\"AT%\",AN20),,REPT(\" \",25-SEARCH(\"AT%\",AN20)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",2435]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),1,1))","v":1},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH21,[1]List!$D$3:$F$527,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%Q\"&B18*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2436]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH22,[1]List!$D$3:$F$527,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%Q\"&B18*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2437]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH23,[1]List!$D$3:$F$527,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%Q\"&B18*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2438]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH24,[1]List!$D$3:$F$527,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%Q\"&B18*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2439]
[null,{"$f":"B30","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 0401U地址: 20 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH26&AA26&\"-\"&AK26","v":"F新风机组NJ-5AP(KT)1-送风温度"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-5AP(KT)1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)1","05H01","送风温度",{"$f":"AH26&\"-\"&AK26","v":"F新风机组-送风温度"},{"$f":"VLOOKUP(AH26,[1]List!$D$3:$F$527,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05H01_ST"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LFAU05H01_ST AT%I320.0 :INT; (*F新风机组NJ-5AP(KT)1-送风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LFAU05H01_ST            AT%I320.0      :INT; (*F新风机组NJ-5AP(KT)1-送风温度*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L01\\L01FAU05H01_ST"},{"$f":"J26","v":"F新风机组NJ-5AP(KT)1-送风温度"},{"$f":"30000+($B27*8+F26-1)","v":30160}]
[null,20,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,2,"0V","F新风机组NJ-5AP(KT)1-水阀反馈",{"$nulls":16},"NJ-5AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)1","05H01","水阀反馈","F新风机组-水阀反馈",{"$f":"VLOOKUP(AH27,[1]List!$D$3:$F$527,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05H01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LFAU05H01_WVB AT%I322.0 :INT; (*F新风机组NJ-5AP(KT)1-水阀反馈*)"},"LFAU05H01_WVB           AT%I322.0      :INT; (*F新风机组NJ-5AP(KT)1-水阀反馈*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM27","v":"L01\\L01FAU05H01_WVB"},"F新风机组NJ-5AP(KT)1-水阀反馈",{"$f":"AS26+1","v":30161}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":1},3,null,3,"0V","F新风机组NJ-5AP(KT)1-变频器频率反馈",{"$nulls":16},"NJ-5AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)1","05H01","变频器频率反馈","F新风机组-变频器频率反馈",{"$f":"VLOOKUP(AH28,[1]List!$D$3:$F$527,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05H01_VFB"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LFAU05H01_VFB AT%I324.0 :INT; (*F新风机组NJ-5AP(KT)1-变频器频率反馈*)"},"LFAU05H01_VFB           AT%I324.0      :INT; (*F新风机组NJ-5AP(KT)1-变频器频率反馈*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM28","v":"L01\\L01FAU05H01_VFB"},"F新风机组NJ-5AP(KT)1-变频器频率反馈",30162]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH29,[1]List!$D$3:$F$527,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM29","v":{"$error":"#N/A"}},"-",30163]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":1}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B39","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B39&\"地址: \"&B36&\" *)\"","v":"(* IOM 0401A地址: 21 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH35&AA35&\"-\"&AK35","v":"F新风机组NJ-5AP(KT)1-水阀控制"},{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-5AP(KT)1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)1","05H01","水阀控制",{"$f":"AH35&\"-\"&AK35","v":"F新风机组-水阀控制"},{"$f":"VLOOKUP(AH35,[1]List!$D$3:$F$527,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05H01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%Q\"&B36*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LFAU05H01_WVC AT%Q336.0 :INT; (*F新风机组NJ-5AP(KT)1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35))),SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35)))))),\" \")","v":"LFAU05H01_WVC           AT%Q336.0      :INT; (*F新风机组NJ-5AP(KT)1-水阀控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM35","v":"L01\\L01FAU05H01_WVC"},{"$f":"J35","v":"F新风机组NJ-5AP(KT)1-水阀控制"},{"$f":"40000+($B36*8+F35-1)","v":40168}]
[null,21,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":0},2,null,3,4,"F新风机组NJ-5AP(KT)1-变频器频率控制",{"$nulls":16},"NJ-5AP(KT)1",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)1","05H01","变频器频率控制","F新风机组-变频器频率控制",{"$f":"VLOOKUP(AH36,[1]List!$D$3:$F$527,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05H01_VFC"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%Q\"&B36*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LFAU05H01_VFC AT%Q338.0 :INT; (*F新风机组NJ-5AP(KT)1-变频器频率控制*)"},"LFAU05H01_VFC           AT%Q338.0      :INT; (*F新风机组NJ-5AP(KT)1-变频器频率控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM36","v":"L01\\L01FAU05H01_VFC"},"F新风机组NJ-5AP(KT)1-变频器频率控制",{"$f":"AS35+1","v":40169}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":1},3,null,5,6,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH37,[1]List!$D$3:$F$527,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%Q\"&B36*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM37","v":{"$error":"#N/A"}},"-",40170]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":0},4,null,7,8,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH38,[1]List!$D$3:$F$527,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%Q\"&B36*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN38,SEARCH(\"AT%\",AN38),,REPT(\" \",30-SEARCH(\"AT%\",AN38))),SEARCH(\":\",REPLACE(AN38,SEARCH(\"AT%\",AN38),,REPT(\" \",30-SEARCH(\"AT%\",AN38)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN38,SEARCH(\"AT%\",AN38),,REPT(\" \",25-SEARCH(\"AT%\",AN38)))))),\" \")","v":" "},null,{"$f":"$B$2&\"\\\"&$B$2&AM38","v":{"$error":"#N/A"}},"-",40171]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
{"$rows_empty":77}
[null," "]

{"sheet":"L302","index":24,"n_rows":111,"n_cols":45,"rows_kept":111,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[6,1,6,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[92,5,92,6],[92,9,92,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[101,5,101,6],[101,9,101,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[109,5,109,6],[109,9,109,25],[110,5,110,6],[110,9,110,25],[4,1,5,1],[12,1,23,1],[29,1,40,1],[46,1,57,1],[63,1,74,1],[80,1,83,1],[89,1,92,1],[98,1,101,1],[107,1,110,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[16,2,23,4],[33,2,40,4],[50,2,57,4],[67,2,74,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L20",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"EXC-1000"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B13&\"地址: \"&B10&\" *)\"","v":"(* IOM 1601R地址: 0 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH9&AA9&\"-\"&AK9","v":"空调机组NJ-3AP(KT)2-1-运行状态"},{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-3AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-1","03B01","运行状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU03B01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B10*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU03B01_R AT%I0.0 :BOOL; (*空调机组NJ-3AP(KT)2-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9))),SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))))),\" \")","v":"LAHU03B01_R             AT%I0.0        :BOOL; (*空调机组NJ-3AP(KT)2-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM9","v":"L20\\L20AHU03B01_R"},{"$f":"J9","v":"空调机组NJ-3AP(KT)2-1-运行状态"},{"$f":"10000+($B10*16*8+F9-1)","v":10000}]
[null,0,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-3AP(KT)2-1-故障状态",{"$nulls":16},{"$f":"IF(AI10=\"\",\"\",AI10)","v":"NJ-3AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-1","03B01","故障状态",{"$f":"AH10&\"-\"&AK10","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU03B01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B10*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU03B01_F AT%I0.1 :BOOL; (*空调机组NJ-3AP(KT)2-1-故障状态*)"},"LAHU03B01_F             AT%I0.1        :BOOL; (*空调机组NJ-3AP(KT)2-1-故障状态*)",null,"L20\\L20AHU03B01_F",{"$f":"J10","v":"空调机组NJ-3AP(KT)2-1-故障状态"},{"$f":"AS9+1","v":10001}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)2-1-自动状态",{"$nulls":16},"NJ-3AP(KT)2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-1","03B01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU03B01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B10*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU03B01_A AT%I0.2 :BOOL; (*空调机组NJ-3AP(KT)2-1-自动状态*)"},"LAHU03B01_A             AT%I0.2        :BOOL; (*空调机组NJ-3AP(KT)2-1-自动状态*)",null,"L20\\L20AHU03B01_A","空调机组NJ-3AP(KT)2-1-自动状态",{"$f":"AS10+1","v":10002}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)2-1-风机压差",{"$nulls":16},"NJ-3AP(KT)2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-1","03B01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU03B01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B10*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU03B01_FPS AT%I0.3 :BOOL; (*空调机组NJ-3AP(KT)2-1-风机压差*)"},"LAHU03B01_FPS           AT%I0.3        :BOOL; (*空调机组NJ-3AP(KT)2-1-风机压差*)",null,"L20\\L20AHU03B01_FPS","空调机组NJ-3AP(KT)2-1-风机压差",10003]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)2-2-运行状态",{"$nulls":16},"NJ-3AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-2","03B02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU03B02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B10*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU03B02_R AT%I0.4 :BOOL; (*空调机组NJ-3AP(KT)2-2-运行状态*)"},"LAHU03B02_R             AT%I0.4        :BOOL; (*空调机组NJ-3AP(KT)2-2-运行状态*)",null,"L20\\L20AHU03B02_R","空调机组NJ-3AP(KT)2-2-运行状态",10004]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)2-2-故障状态",{"$nulls":16},"NJ-3AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-2","03B02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU03B02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B10*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU03B02_F AT%I0.5 :BOOL; (*空调机组NJ-3AP(KT)2-2-故障状态*)"},"LAHU03B02_F             AT%I0.5        :BOOL; (*空调机组NJ-3AP(KT)2-2-故障状态*)",null,"L20\\L20AHU03B02_F","空调机组NJ-3AP(KT)2-2-故障状态",10005]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)2-2-自动状态",{"$nulls":16},"NJ-3AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-2","03B02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU03B02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B10*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU03B02_A AT%I0.6 :BOOL; (*空调机组NJ-3AP(KT)2-2-自动状态*)"},"LAHU03B02_A             AT%I0.6        :BOOL; (*空调机组NJ-3AP(KT)2-2-自动状态*)",null,"L20\\L20AHU03B02_A","空调机组NJ-3AP(KT)2-2-自动状态",10006]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)2-2-风机压差",{"$nulls":16},"NJ-3AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-2","03B02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU03B02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B10*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU03B02_FPS AT%I0.7 :BOOL; (*空调机组NJ-3AP(KT)2-2-风机压差*)"},"LAHU03B02_FPS           AT%I0.7        :BOOL; (*空调机组NJ-3AP(KT)2-2-风机压差*)",null,"L20\\L20AHU03B02_FPS","空调机组NJ-3AP(KT)2-2-风机压差",10007]
[{"$nulls":5},9,null,17,18,"空调机组NJ-3AP(KT)2-3-运行状态",{"$nulls":16},"NJ-3AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-3","03B03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU03B03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B10*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU03B03_R AT%I1.0 :BOOL; (*空调机组NJ-3AP(KT)2-3-运行状态*)"},"LAHU03B03_R             AT%I1.0        :BOOL; (*空调机组NJ-3AP(KT)2-3-运行状态*)",null,"L20\\L20AHU03B03_R","空调机组NJ-3AP(KT)2-3-运行状态",10008]
[{"$nulls":5},10,null,19,20,"空调机组NJ-3AP(KT)2-3-故障状态",{"$nulls":16},{"$f":"IF(AI18=\"\",\"\",AI18)","v":"NJ-3AP(KT)2-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-3","03B03","故障状态",{"$f":"AH18&\"-\"&AK18","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU03B03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B10*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU03B03_F AT%I1.1 :BOOL; (*空调机组NJ-3AP(KT)2-3-故障状态*)"},"LAHU03B03_F             AT%I1.1        :BOOL; (*空调机组NJ-3AP(KT)2-3-故障状态*)",null,"L20\\L20AHU03B03_F","空调机组NJ-3AP(KT)2-3-故障状态",10009]
[{"$nulls":5},11,null,21,22,"空调机组NJ-3AP(KT)2-3-自动状态",{"$nulls":16},"NJ-3AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-3","03B03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU03B03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B10*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU03B03_A AT%I1.2 :BOOL; (*空调机组NJ-3AP(KT)2-3-自动状态*)"},"LAHU03B03_A             AT%I1.2        :BOOL; (*空调机组NJ-3AP(KT)2-3-自动状态*)",null,"L20\\L20AHU03B03_A","空调机组NJ-3AP(KT)2-3-自动状态",10010]
[{"$nulls":5},12,null,23,24,"空调机组NJ-3AP(KT)2-3-风机压差",{"$nulls":16},"NJ-3AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-3","03B03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU03B03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B10*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU03B03_FPS AT%I1.3 :BOOL; (*空调机组NJ-3AP(KT)2-3-风机压差*)"},"LAHU03B03_FPS           AT%I1.3        :BOOL; (*空调机组NJ-3AP(KT)2-3-风机压差*)",null,"L20\\L20AHU03B03_FPS","空调机组NJ-3AP(KT)2-3-风机压差",10011]
[{"$nulls":5},13,null,25,26,"空调机组NJ-3AP(KT)2-4-运行状态",{"$nulls":16},"NJ-3AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-4","03B04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU03B04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B10*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU03B04_R AT%I1.4 :BOOL; (*空调机组NJ-3AP(KT)2-4-运行状态*)"},"LAHU03B04_R             AT%I1.4        :BOOL; (*空调机组NJ-3AP(KT)2-4-运行状态*)",null,"L20\\L20AHU03B04_R","空调机组NJ-3AP(KT)2-4-运行状态",10012]
[{"$nulls":5},14,null,27,28,"空调机组NJ-3AP(KT)2-4-故障状态",{"$nulls":16},"NJ-3AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-4","03B04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU03B04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B10*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU03B04_F AT%I1.5 :BOOL; (*空调机组NJ-3AP(KT)2-4-故障状态*)"},"LAHU03B04_F             AT%I1.5        :BOOL; (*空调机组NJ-3AP(KT)2-4-故障状态*)",null,"L20\\L20AHU03B04_F","空调机组NJ-3AP(KT)2-4-故障状态",10013]
[{"$nulls":5},15,null,29,30,"空调机组NJ-3AP(KT)2-4-自动状态",{"$nulls":16},"NJ-3AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-4","03B04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU03B04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B10*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU03B04_A AT%I1.6 :BOOL; (*空调机组NJ-3AP(KT)2-4-自动状态*)"},"LAHU03B04_A             AT%I1.6        :BOOL; (*空调机组NJ-3AP(KT)2-4-自动状态*)",null,"L20\\L20AHU03B04_A","空调机组NJ-3AP(KT)2-4-自动状态",10014]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-3AP(KT)2-4-风机压差",{"$nulls":16},"NJ-3AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-4","03B04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH24,List!$B$3:$D$445,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,List!$K$2:$M$447,2,FALSE)","v":"AHU03B04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%I\"&B10*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":"LAHU03B04_FPS AT%I1.7 :BOOL; (*空调机组NJ-3AP(KT)2-4-风机压差*)"},"LAHU03B04_FPS           AT%I1.7        :BOOL; (*空调机组NJ-3AP(KT)2-4-风机压差*)",null,"L20\\L20AHU03B04_FPS","空调机组NJ-3AP(KT)2-4-风机压差",10015]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 1601R地址: 1 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH26&AA26&\"-\"&AK26","v":"空调机组NJ-3AP(KT)2-5-运行状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-3AP(KT)2-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-5","03B05","运行状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU03B05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU03B05_R AT%I16.0 :BOOL; (*空调机组NJ-3AP(KT)2-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LAHU03B05_R             AT%I16.0       :BOOL; (*空调机组NJ-3AP(KT)2-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L20\\L20AHU03B05_R"},{"$f":"J26","v":"空调机组NJ-3AP(KT)2-5-运行状态"},{"$f":"10000+($B27*16*8+F26-1)","v":10128}]
[null,1,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-3AP(KT)2-5-故障状态",{"$nulls":16},{"$f":"IF(AI27=\"\",\"\",AI27)","v":"NJ-3AP(KT)2-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-5","03B05","故障状态",{"$f":"AH27&\"-\"&AK27","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU03B05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU03B05_F AT%I16.1 :BOOL; (*空调机组NJ-3AP(KT)2-5-故障状态*)"},"LAHU03B05_F             AT%I16.1       :BOOL; (*空调机组NJ-3AP(KT)2-5-故障状态*)",null,"L20\\L20AHU03B05_F",{"$f":"J27","v":"空调机组NJ-3AP(KT)2-5-故障状态"},{"$f":"AS26+1","v":10129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)2-5-自动状态",{"$nulls":16},"NJ-3AP(KT)2-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-5","03B05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU03B05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU03B05_A AT%I16.2 :BOOL; (*空调机组NJ-3AP(KT)2-5-自动状态*)"},"LAHU03B05_A             AT%I16.2       :BOOL; (*空调机组NJ-3AP(KT)2-5-自动状态*)",null,"L20\\L20AHU03B05_A","空调机组NJ-3AP(KT)2-5-自动状态",{"$f":"AS27+1","v":10130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)2-5-风机压差",{"$nulls":16},"NJ-3AP(KT)2-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-5","03B05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU03B05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU03B05_FPS AT%I16.3 :BOOL; (*空调机组NJ-3AP(KT)2-5-风机压差*)"},"LAHU03B05_FPS           AT%I16.3       :BOOL; (*空调机组NJ-3AP(KT)2-5-风机压差*)",null,"L20\\L20AHU03B05_FPS","空调机组NJ-3AP(KT)2-5-风机压差",10131]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)2-6-运行状态",{"$nulls":16},"NJ-3AP(KT)2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-6","03B06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU03B06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B27*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU03B06_R AT%I16.4 :BOOL; (*空调机组NJ-3AP(KT)2-6-运行状态*)"},"LAHU03B06_R             AT%I16.4       :BOOL; (*空调机组NJ-3AP(KT)2-6-运行状态*)",null,"L20\\L20AHU03B06_R","空调机组NJ-3AP(KT)2-6-运行状态",10132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)2-6-故障状态",{"$nulls":16},"NJ-3AP(KT)2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-6","03B06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU03B06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B27*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU03B06_F AT%I16.5 :BOOL; (*空调机组NJ-3AP(KT)2-6-故障状态*)"},"LAHU03B06_F             AT%I16.5       :BOOL; (*空调机组NJ-3AP(KT)2-6-故障状态*)",null,"L20\\L20AHU03B06_F","空调机组NJ-3AP(KT)2-6-故障状态",10133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)2-6-自动状态",{"$nulls":16},"NJ-3AP(KT)2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-6","03B06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU03B06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B27*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU03B06_A AT%I16.6 :BOOL; (*空调机组NJ-3AP(KT)2-6-自动状态*)"},"LAHU03B06_A             AT%I16.6       :BOOL; (*空调机组NJ-3AP(KT)2-6-自动状态*)",null,"L20\\L20AHU03B06_A","空调机组NJ-3AP(KT)2-6-自动状态",10134]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)2-6-风机压差",{"$nulls":16},"NJ-3AP(KT)2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-6","03B06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU03B06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B27*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU03B06_FPS AT%I16.7 :BOOL; (*空调机组NJ-3AP(KT)2-6-风机压差*)"},"LAHU03B06_FPS           AT%I16.7       :BOOL; (*空调机组NJ-3AP(KT)2-6-风机压差*)",null,"L20\\L20AHU03B06_FPS","空调机组NJ-3AP(KT)2-6-风机压差",10135]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-3AL2-1-运行状态",{"$nulls":16},"NJ-3AL2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-3AL2-1","03B01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"LCB03B01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B27*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LLCB03B01_R AT%I17.0 :BOOL; (*照明控制箱NJ-3AL2-1-运行状态*)"},"LLCB03B01_R             AT%I17.0       :BOOL; (*照明控制箱NJ-3AL2-1-运行状态*)",null,"L20\\L20LCB03B01_R","照明控制箱NJ-3AL2-1-运行状态",10136]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-3AL2-1-自动状态",{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-3AL2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-3AL2-1","03B01","自动状态",{"$f":"AH35&\"-\"&AK35","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"LCB03B01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B27*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LLCB03B01_A AT%I17.1 :BOOL; (*照明控制箱NJ-3AL2-1-自动状态*)"},"LLCB03B01_A             AT%I17.1       :BOOL; (*照明控制箱NJ-3AL2-1-自动状态*)",null,"L20\\L20LCB03B01_A",{"$f":"J35","v":"照明控制箱NJ-3AL2-1-自动状态"},10137]
[{"$nulls":5},11,null,21,22,"照明控制箱NJ-3AL2-2-运行状态",{"$nulls":16},"NJ-3AL2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-3AL2-2","03B02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"LCB03B02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B27*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LLCB03B02_R AT%I17.2 :BOOL; (*照明控制箱NJ-3AL2-2-运行状态*)"},"LLCB03B02_R             AT%I17.2       :BOOL; (*照明控制箱NJ-3AL2-2-运行状态*)",null,"L20\\L20LCB03B02_R","照明控制箱NJ-3AL2-2-运行状态",10138]
[{"$nulls":5},12,null,23,24,"照明控制箱NJ-3AL2-2-自动状态",{"$nulls":16},"NJ-3AL2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-3AL2-2","03B02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"LCB03B02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B27*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LLCB03B02_A AT%I17.3 :BOOL; (*照明控制箱NJ-3AL2-2-自动状态*)"},"LLCB03B02_A             AT%I17.3       :BOOL; (*照明控制箱NJ-3AL2-2-自动状态*)",null,"L20\\L20LCB03B02_A","照明控制箱NJ-3AL2-2-自动状态",10139]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-3AL2-3-运行状态",{"$nulls":16},"NJ-3AL2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-3AL2-3","03B03","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB03B03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B27*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB03B03_R AT%I17.4 :BOOL; (*照明控制箱NJ-3AL2-3-运行状态*)"},"LLCB03B03_R             AT%I17.4       :BOOL; (*照明控制箱NJ-3AL2-3-运行状态*)",null,"L20\\L20LCB03B03_R","照明控制箱NJ-3AL2-3-运行状态",10140]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-3AL2-3-自动状态",{"$nulls":16},"NJ-3AL2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-3AL2-3","03B03","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB03B03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B27*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB03B03_A AT%I17.5 :BOOL; (*照明控制箱NJ-3AL2-3-自动状态*)"},"LLCB03B03_A             AT%I17.5       :BOOL; (*照明控制箱NJ-3AL2-3-自动状态*)",null,"L20\\L20LCB03B03_A","照明控制箱NJ-3AL2-3-自动状态",10141]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-3AL2-4-运行状态",{"$nulls":16},"NJ-3AL2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-3AL2-4","03B04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"LCB03B04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B27*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LLCB03B04_R AT%I17.6 :BOOL; (*照明控制箱NJ-3AL2-4-运行状态*)"},"LLCB03B04_R             AT%I17.6       :BOOL; (*照明控制箱NJ-3AL2-4-运行状态*)",null,"L20\\L20LCB03B04_R","照明控制箱NJ-3AL2-4-运行状态",10142]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-3AL2-4-自动状态",{"$nulls":16},"NJ-3AL2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-3AL2-4","03B04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":"LCB03B04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%I\"&B27*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":"LLCB03B04_A AT%I17.7 :BOOL; (*照明控制箱NJ-3AL2-4-自动状态*)"},"LLCB03B04_A             AT%I17.7       :BOOL; (*照明控制箱NJ-3AL2-4-自动状态*)",null,"L20\\L20LCB03B04_A","照明控制箱NJ-3AL2-4-自动状态",10143]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 1601R地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH43&AA43&\"-\"&AK43","v":"照明控制箱NJ-3AL(GG)2-1-运行状态"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-3AL(GG)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)2-1","03B05","运行状态",{"$f":"AH43&\"-\"&AK43","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"LCB03B05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B44*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LLCB03B05_R AT%I32.0 :BOOL; (*照明控制箱NJ-3AL(GG)2-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LLCB03B05_R             AT%I32.0       :BOOL; (*照明控制箱NJ-3AL(GG)2-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM43","v":"L20\\L20LCB03B05_R"},{"$f":"J43","v":"照明控制箱NJ-3AL(GG)2-1-运行状态"},{"$f":"10000+($B44*16*8+F43-1)","v":10256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},2,null,3,4,"照明控制箱NJ-3AL(GG)2-1-自动状态",{"$nulls":16},{"$f":"IF(AI44=\"\",\"\",AI44)","v":"NJ-3AL(GG)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)2-1","03B05","自动状态",{"$f":"AH44&\"-\"&AK44","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"LCB03B05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B44*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LLCB03B05_A AT%I32.1 :BOOL; (*照明控制箱NJ-3AL(GG)2-1-自动状态*)"},"LLCB03B05_A             AT%I32.1       :BOOL; (*照明控制箱NJ-3AL(GG)2-1-自动状态*)",null,"L20\\L20LCB03B05_A",{"$f":"J44","v":"照明控制箱NJ-3AL(GG)2-1-自动状态"},{"$f":"AS43+1","v":10257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,5,6,"照明控制箱NJ-3AL(GG)2-2-运行状态",{"$nulls":16},"NJ-3AL(GG)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)2-2","03B06","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"LCB03B06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B44*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LLCB03B06_R AT%I32.2 :BOOL; (*照明控制箱NJ-3AL(GG)2-2-运行状态*)"},"LLCB03B06_R             AT%I32.2       :BOOL; (*照明控制箱NJ-3AL(GG)2-2-运行状态*)",null,"L20\\L20LCB03B06_R","照明控制箱NJ-3AL(GG)2-2-运行状态",{"$f":"AS44+1","v":10258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},4,null,7,8,"照明控制箱NJ-3AL(GG)2-2-自动状态",{"$nulls":16},"NJ-3AL(GG)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)2-2","03B06","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"LCB03B06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B44*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LLCB03B06_A AT%I32.3 :BOOL; (*照明控制箱NJ-3AL(GG)2-2-自动状态*)"},"LLCB03B06_A             AT%I32.3       :BOOL; (*照明控制箱NJ-3AL(GG)2-2-自动状态*)",null,"L20\\L20LCB03B06_A","照明控制箱NJ-3AL(GG)2-2-自动状态",10259]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-3AL(GG)2-3-运行状态",{"$nulls":16},"NJ-3AL(GG)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)2-3","03B07","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"LCB03B07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B44*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LLCB03B07_R AT%I32.4 :BOOL; (*照明控制箱NJ-3AL(GG)2-3-运行状态*)"},"LLCB03B07_R             AT%I32.4       :BOOL; (*照明控制箱NJ-3AL(GG)2-3-运行状态*)",null,"L20\\L20LCB03B07_R","照明控制箱NJ-3AL(GG)2-3-运行状态",10260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-3AL(GG)2-3-自动状态",{"$nulls":16},"NJ-3AL(GG)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)2-3","03B07","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"LCB03B07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B44*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LLCB03B07_A AT%I32.5 :BOOL; (*照明控制箱NJ-3AL(GG)2-3-自动状态*)"},"LLCB03B07_A             AT%I32.5       :BOOL; (*照明控制箱NJ-3AL(GG)2-3-自动状态*)",null,"L20\\L20LCB03B07_A","照明控制箱NJ-3AL(GG)2-3-自动状态",10261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"照明控制箱NJ-3AL(GG)2-4-运行状态",{"$nulls":16},"NJ-3AL(GG)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)2-4","03B08","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"LCB03B08_R"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B44*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LLCB03B08_R AT%I32.6 :BOOL; (*照明控制箱NJ-3AL(GG)2-4-运行状态*)"},"LLCB03B08_R             AT%I32.6       :BOOL; (*照明控制箱NJ-3AL(GG)2-4-运行状态*)",null,"L20\\L20LCB03B08_R","照明控制箱NJ-3AL(GG)2-4-运行状态",10262]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"照明控制箱NJ-3AL(GG)2-4-自动状态",{"$nulls":16},"NJ-3AL(GG)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)2-4","03B08","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"LCB03B08_A"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B44*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LLCB03B08_A AT%I32.7 :BOOL; (*照明控制箱NJ-3AL(GG)2-4-自动状态*)"},"LLCB03B08_A             AT%I32.7       :BOOL; (*照明控制箱NJ-3AL(GG)2-4-自动状态*)",null,"L20\\L20LCB03B08_A","照明控制箱NJ-3AL(GG)2-4-自动状态",10263]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-3AL(GG)2-5-运行状态",{"$nulls":16},"NJ-3AL(GG)2-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)2-5","03B09","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"LCB03B09_R"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B44*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LLCB03B09_R AT%I33.0 :BOOL; (*照明控制箱NJ-3AL(GG)2-5-运行状态*)"},"LLCB03B09_R             AT%I33.0       :BOOL; (*照明控制箱NJ-3AL(GG)2-5-运行状态*)",null,"L20\\L20LCB03B09_R","照明控制箱NJ-3AL(GG)2-5-运行状态",10264]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-3AL(GG)2-5-自动状态",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-3AL(GG)2-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)2-5","03B09","自动状态",{"$f":"AH52&\"-\"&AK52","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"LCB03B09_A"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%I\"&B44*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LLCB03B09_A AT%I33.1 :BOOL; (*照明控制箱NJ-3AL(GG)2-5-自动状态*)"},"LLCB03B09_A             AT%I33.1       :BOOL; (*照明控制箱NJ-3AL(GG)2-5-自动状态*)",null,"L20\\L20LCB03B09_A",{"$f":"J52","v":"照明控制箱NJ-3AL(GG)2-5-自动状态"},10265]
[{"$nulls":5},11,null,21,22,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%I\"&B44*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10266]
[{"$nulls":5},12,null,23,24,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%I\"&B44*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN54,SEARCH(\"AT%\",AN54),,REPT(\" \",30-SEARCH(\"AT%\",AN54))),SEARCH(\":\",REPLACE(AN54,SEARCH(\"AT%\",AN54),,REPT(\" \",30-SEARCH(\"AT%\",AN54)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN54,SEARCH(\"AT%\",AN54),,REPT(\" \",25-SEARCH(\"AT%\",AN54)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",10267]
[{"$nulls":5},13,null,25,26,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%I\"&B44*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10268]
[{"$nulls":5},14,null,27,28,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%I\"&B44*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10269]
[{"$nulls":5},15,null,29,30,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%I\"&B44*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10270]
[".",{"$nulls":4},16,null,31,32,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%I\"&B44*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10271]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B64&\"地址: \"&B61&\" *)\"","v":"(* IOM 1601D地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH60&AA60&\"-\"&AK60","v":"空调机组NJ-3AP(KT)2-1-启停控制"},{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-3AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-1","03B01","启停控制",{"$f":"AH60&\"-\"&AK60","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"AHU03B01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%Q\"&B61*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LAHU03B01_C AT%Q48.0 :BOOL; (*空调机组NJ-3AP(KT)2-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60))),SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))))),\" \")","v":"LAHU03B01_C             AT%Q48.0       :BOOL; (*空调机组NJ-3AP(KT)2-1-启停控制*)"},null,{"$f":"AM60","v":"AHU03B01_C"},{"$f":"J60","v":"空调机组NJ-3AP(KT)2-1-启停控制"},{"$f":"($B61*16*8+F60-1)","v":384}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-3AP(KT)2-2-启停控制",{"$nulls":16},{"$f":"IF(AI61=\"\",\"\",AI61)","v":"NJ-3AP(KT)2-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-2","03B02","启停控制",{"$f":"AH61&\"-\"&AK61","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"AHU03B02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%Q\"&B61*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LAHU03B02_C AT%Q48.1 :BOOL; (*空调机组NJ-3AP(KT)2-2-启停控制*)"},"LAHU03B02_C             AT%Q48.1       :BOOL; (*空调机组NJ-3AP(KT)2-2-启停控制*)",null,"AHU03B02_C",{"$f":"J61","v":"空调机组NJ-3AP(KT)2-2-启停控制"},{"$f":"AS60+1","v":385}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","空调机组NJ-3AP(KT)2-3-启停控制",{"$nulls":16},"NJ-3AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-3","03B03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"AHU03B03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%Q\"&B61*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LAHU03B03_C AT%Q48.2 :BOOL; (*空调机组NJ-3AP(KT)2-3-启停控制*)"},"LAHU03B03_C             AT%Q48.2       :BOOL; (*空调机组NJ-3AP(KT)2-3-启停控制*)",null,"AHU03B03_C","空调机组NJ-3AP(KT)2-3-启停控制",{"$f":"AS61+1","v":386}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","空调机组NJ-3AP(KT)2-4-启停控制",{"$nulls":16},"NJ-3AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-4","03B04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"AHU03B04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%Q\"&B61*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LAHU03B04_C AT%Q48.3 :BOOL; (*空调机组NJ-3AP(KT)2-4-启停控制*)"},"LAHU03B04_C             AT%Q48.3       :BOOL; (*空调机组NJ-3AP(KT)2-4-启停控制*)",null,"AHU03B04_C","空调机组NJ-3AP(KT)2-4-启停控制",387]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-3AP(KT)2-5-启停控制",{"$nulls":16},"NJ-3AP(KT)2-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-5","03B05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"AHU03B05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%Q\"&B61*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LAHU03B05_C AT%Q48.4 :BOOL; (*空调机组NJ-3AP(KT)2-5-启停控制*)"},"LAHU03B05_C             AT%Q48.4       :BOOL; (*空调机组NJ-3AP(KT)2-5-启停控制*)",null,"AHU03B05_C","空调机组NJ-3AP(KT)2-5-启停控制",388]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-3AP(KT)2-6-启停控制",{"$nulls":16},"NJ-3AP(KT)2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-6","03B06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":"AHU03B06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%Q\"&B61*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":"LAHU03B06_C AT%Q48.5 :BOOL; (*空调机组NJ-3AP(KT)2-6-启停控制*)"},"LAHU03B06_C             AT%Q48.5       :BOOL; (*空调机组NJ-3AP(KT)2-6-启停控制*)",null,"AHU03B06_C","空调机组NJ-3AP(KT)2-6-启停控制",389]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","照明控制箱NJ-3AL2-1-启停控制",{"$nulls":16},"NJ-3AL2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-3AL2-1","03B01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":"LCB03B01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%Q\"&B61*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":"LLCB03B01_C AT%Q48.6 :BOOL; (*照明控制箱NJ-3AL2-1-启停控制*)"},"LLCB03B01_C             AT%Q48.6       :BOOL; (*照明控制箱NJ-3AL2-1-启停控制*)",null,"LCB03B01_C","照明控制箱NJ-3AL2-1-启停控制",390]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-3AL2-2-启停控制",{"$nulls":16},"NJ-3AL2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-3AL2-2","03B02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":"LCB03B02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%Q\"&B61*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":"LLCB03B02_C AT%Q48.7 :BOOL; (*照明控制箱NJ-3AL2-2-启停控制*)"},"LLCB03B02_C             AT%Q48.7       :BOOL; (*照明控制箱NJ-3AL2-2-启停控制*)",null,"LCB03B02_C","照明控制箱NJ-3AL2-2-启停控制",391]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-3AL2-3-启停控制",{"$nulls":16},"NJ-3AL2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-3AL2-3","03B03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"LCB03B03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%Q\"&B61*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LLCB03B03_C AT%Q49.0 :BOOL; (*照明控制箱NJ-3AL2-3-启停控制*)"},"LLCB03B03_C             AT%Q49.0       :BOOL; (*照明控制箱NJ-3AL2-3-启停控制*)",null,"LCB03B03_C","照明控制箱NJ-3AL2-3-启停控制",392]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-3AL2-4-启停控制",{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-3AL2-4"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-3AL2-4","03B04","启停控制",{"$f":"AH69&\"-\"&AK69","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"LCB03B04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%Q\"&B61*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LLCB03B04_C AT%Q49.1 :BOOL; (*照明控制箱NJ-3AL2-4-启停控制*)"},"LLCB03B04_C             AT%Q49.1       :BOOL; (*照明控制箱NJ-3AL2-4-启停控制*)",null,"LCB03B04_C",{"$f":"J69","v":"照明控制箱NJ-3AL2-4-启停控制"},393]
[{"$nulls":5},11,null,"11+","11-","照明控制箱NJ-3AL(GG)2-1-启停控制",{"$nulls":16},"NJ-3AL(GG)2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)2-1","03B05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"LCB03B05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%Q\"&B61*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LLCB03B05_C AT%Q49.2 :BOOL; (*照明控制箱NJ-3AL(GG)2-1-启停控制*)"},"LLCB03B05_C             AT%Q49.2       :BOOL; (*照明控制箱NJ-3AL(GG)2-1-启停控制*)",null,"LCB03B05_C","照明控制箱NJ-3AL(GG)2-1-启停控制",394]
[{"$nulls":5},12,null,"12+","12-","照明控制箱NJ-3AL(GG)2-2-启停控制",{"$nulls":16},"NJ-3AL(GG)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)2-2","03B06","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"LCB03B06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%Q\"&B61*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LLCB03B06_C AT%Q49.3 :BOOL; (*照明控制箱NJ-3AL(GG)2-2-启停控制*)"},"LLCB03B06_C             AT%Q49.3       :BOOL; (*照明控制箱NJ-3AL(GG)2-2-启停控制*)",null,"LCB03B06_C","照明控制箱NJ-3AL(GG)2-2-启停控制",395]
[{"$nulls":5},13,null,"13+","13-","照明控制箱NJ-3AL(GG)2-3-启停控制",{"$nulls":16},"NJ-3AL(GG)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)2-3","03B07","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"LCB03B07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%Q\"&B61*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LLCB03B07_C AT%Q49.4 :BOOL; (*照明控制箱NJ-3AL(GG)2-3-启停控制*)"},"LLCB03B07_C             AT%Q49.4       :BOOL; (*照明控制箱NJ-3AL(GG)2-3-启停控制*)",null,"LCB03B07_C","照明控制箱NJ-3AL(GG)2-3-启停控制",396]
[{"$nulls":5},14,null,"14+","14-","照明控制箱NJ-3AL(GG)2-4-启停控制",{"$nulls":16},"NJ-3AL(GG)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)2-4","03B08","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"LCB03B08_C"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%Q\"&B61*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LLCB03B08_C AT%Q49.5 :BOOL; (*照明控制箱NJ-3AL(GG)2-4-启停控制*)"},"LLCB03B08_C             AT%Q49.5       :BOOL; (*照明控制箱NJ-3AL(GG)2-4-启停控制*)",null,"LCB03B08_C","照明控制箱NJ-3AL(GG)2-4-启停控制",397]
[{"$nulls":5},15,null,"15+","15-","照明控制箱NJ-3AL(GG)2-5-启停控制",{"$nulls":16},"NJ-3AL(GG)2-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)2-5","03B09","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":"LCB03B09_C"},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%Q\"&B61*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":"LLCB03B09_C AT%Q49.6 :BOOL; (*照明控制箱NJ-3AL(GG)2-5-启停控制*)"},"LLCB03B09_C             AT%Q49.6       :BOOL; (*照明控制箱NJ-3AL(GG)2-5-启停控制*)",null,"LCB03B09_C","照明控制箱NJ-3AL(GG)2-5-启停控制",398]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%Q\"&B61*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",399]
[null,{"$f":"B81","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B81&\"地址: \"&B78&\" *)\"","v":"(* IOM 0801U地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH77&AA77&\"-\"&AK77","v":"空调机组NJ-3AP(KT)2-1-回风温度"},{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-3AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-1","03B01","回风温度",{"$f":"AH77&\"-\"&AK77","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"AHU03B01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%I\"&B78*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LAHU03B01_RT AT%I64.0 :INT ; (*空调机组NJ-3AP(KT)2-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77))),SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))))),\" \")","v":"LAHU03B01_RT            AT%I64.0       :INT ; (*空调机组NJ-3AP(KT)2-1-回风温度*)"},null,{"$f":"AM77","v":"AHU03B01_RT"},{"$f":"J77","v":"空调机组NJ-3AP(KT)2-1-回风温度"},{"$f":"30000+($B78*8+F77-1)","v":30032}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-3AP(KT)2-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-3AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-1","03B01","水阀反馈",{"$f":"AH78&\"-\"&AK78","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU03B01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%I\"&B78*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU03B01_WVB AT%I66.0 :INT ; (*空调机组NJ-3AP(KT)2-1-水阀反馈*)"},"LAHU03B01_WVB           AT%I66.0       :INT ; (*空调机组NJ-3AP(KT)2-1-水阀反馈*)",null,"AHU03B01_WVB",{"$f":"J78","v":"空调机组NJ-3AP(KT)2-1-水阀反馈"},{"$f":"AS77+1","v":30033}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)2-2-回风温度",{"$nulls":16},"NJ-3AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-2","03B02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU03B02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%I\"&B78*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU03B02_RT AT%I68.0 :INT ; (*空调机组NJ-3AP(KT)2-2-回风温度*)"},"LAHU03B02_RT            AT%I68.0       :INT ; (*空调机组NJ-3AP(KT)2-2-回风温度*)",null,"AHU03B02_RT","空调机组NJ-3AP(KT)2-2-回风温度",{"$f":"AS78+1","v":30034}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-3AP(KT)2-2-水阀反馈",{"$nulls":16},"NJ-3AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-2","03B02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU03B02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%I\"&B78*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU03B02_WVB AT%I70.0 :INT ; (*空调机组NJ-3AP(KT)2-2-水阀反馈*)"},"LAHU03B02_WVB           AT%I70.0       :INT ; (*空调机组NJ-3AP(KT)2-2-水阀反馈*)",null,"AHU03B02_WVB","空调机组NJ-3AP(KT)2-2-水阀反馈",30035]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-3AP(KT)2-3-回风温度",{"$nulls":16},"NJ-3AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-3","03B03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"AHU03B03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%I\"&B78*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LAHU03B03_RT AT%I72.0 :INT ; (*空调机组NJ-3AP(KT)2-3-回风温度*)"},"LAHU03B03_RT            AT%I72.0       :INT ; (*空调机组NJ-3AP(KT)2-3-回风温度*)",null,"AHU03B03_RT","空调机组NJ-3AP(KT)2-3-回风温度",30036]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-3AP(KT)2-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI82=\"\",\"\",AI82)","v":"NJ-3AP(KT)2-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-3","03B03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":"AHU03B03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%I\"&B78*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":"LAHU03B03_WVB AT%I74.0 :INT ; (*空调机组NJ-3AP(KT)2-3-水阀反馈*)"},"LAHU03B03_WVB           AT%I74.0       :INT ; (*空调机组NJ-3AP(KT)2-3-水阀反馈*)",null,"AHU03B03_WVB",{"$f":"J82","v":"空调机组NJ-3AP(KT)2-3-水阀反馈"},30037]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-3AP(KT)2-4-回风温度",{"$nulls":16},"NJ-3AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-4","03B04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":"AHU03B04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%I\"&B78*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":"LAHU03B04_RT AT%I76.0 :INT ; (*空调机组NJ-3AP(KT)2-4-回风温度*)"},"LAHU03B04_RT            AT%I76.0       :INT ; (*空调机组NJ-3AP(KT)2-4-回风温度*)",null,"AHU03B04_RT","空调机组NJ-3AP(KT)2-4-回风温度",30038]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-3AP(KT)2-4-水阀反馈",{"$nulls":16},"NJ-3AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-4","03B04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH84,List!$B$3:$D$445,2,FALSE)&AJ84&\"_\"&VLOOKUP(AK84,List!$K$2:$M$447,2,FALSE)","v":"AHU03B04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM84&\" \"&\"AT%I\"&B78*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J84&\"*)\",\" \")","v":"LAHU03B04_WVB AT%I78.0 :INT ; (*空调机组NJ-3AP(KT)2-4-水阀反馈*)"},"LAHU03B04_WVB           AT%I78.0       :INT ; (*空调机组NJ-3AP(KT)2-4-水阀反馈*)",null,"AHU03B04_WVB","空调机组NJ-3AP(KT)2-4-水阀反馈",30039]
[null,{"$f":"B90","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B90&\"地址: \"&B87&\" *)\"","v":"(* IOM 0401U地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH86&AA86&\"-\"&AK86","v":"空调机组NJ-3AP(KT)2-5-回风温度"},{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-3AP(KT)2-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-5","03B05","回风温度",{"$f":"AH86&\"-\"&AK86","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"AHU03B05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%I\"&B87*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LAHU03B05_RT AT%I80.0 :INT ; (*空调机组NJ-3AP(KT)2-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86))),SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))))),\" \")","v":"LAHU03B05_RT            AT%I80.0       :INT ; (*空调机组NJ-3AP(KT)2-5-回风温度*)"},null,{"$f":"AM86","v":"AHU03B05_RT"},{"$f":"J86","v":"空调机组NJ-3AP(KT)2-5-回风温度"},{"$f":"30000+($B87*8+F86-1)","v":30040}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-3AP(KT)2-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI87=\"\",\"\",AI87)","v":"NJ-3AP(KT)2-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-5","03B05","水阀反馈",{"$f":"AH87&\"-\"&AK87","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"AHU03B05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%I\"&B87*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LAHU03B05_WVB AT%I82.0 :INT ; (*空调机组NJ-3AP(KT)2-5-水阀反馈*)"},"LAHU03B05_WVB           AT%I82.0       :INT ; (*空调机组NJ-3AP(KT)2-5-水阀反馈*)",null,"AHU03B05_WVB",{"$f":"J87","v":"空调机组NJ-3AP(KT)2-5-水阀反馈"},{"$f":"AS86+1","v":30041}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)2-6-回风温度",{"$nulls":16},"NJ-3AP(KT)2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-6","03B06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"AHU03B06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%I\"&B87*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LAHU03B06_RT AT%I84.0 :INT ; (*空调机组NJ-3AP(KT)2-6-回风温度*)"},"LAHU03B06_RT            AT%I84.0       :INT ; (*空调机组NJ-3AP(KT)2-6-回风温度*)",null,"AHU03B06_RT","空调机组NJ-3AP(KT)2-6-回风温度",{"$f":"AS87+1","v":30042}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-3AP(KT)2-6-水阀反馈",{"$nulls":16},"NJ-3AP(KT)2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-6","03B06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"AHU03B06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%I\"&B87*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LAHU03B06_WVB AT%I86.0 :INT ; (*空调机组NJ-3AP(KT)2-6-水阀反馈*)"},"LAHU03B06_WVB           AT%I86.0       :INT ; (*空调机组NJ-3AP(KT)2-6-水阀反馈*)",null,"AHU03B06_WVB","空调机组NJ-3AP(KT)2-6-水阀反馈",30043]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B99","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B99&\"地址: \"&B96&\" *)\"","v":"(* IOM 0401A地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH95&AA95&\"-\"&AK95","v":"空调机组NJ-3AP(KT)2-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-3AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-1","03B01","水阀控制",{"$f":"AH95&\"-\"&AK95","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"AHU03B01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%Q\"&B96*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LAHU03B01_WVC AT%Q96.0 :INT ; (*空调机组NJ-3AP(KT)2-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95))),SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))))),\" \")","v":"LAHU03B01_WVC           AT%Q96.0       :INT ; (*空调机组NJ-3AP(KT)2-1-水阀控制*)"},null,{"$f":"AM95","v":"AHU03B01_WVC"},{"$f":"J95","v":"空调机组NJ-3AP(KT)2-1-水阀控制"},{"$f":"40000+($B96*8+F95-1)","v":40048}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH96&AA96&\"-\"&AK96","v":"空调机组NJ-3AP(KT)2-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI96=\"\",\"\",AI96)","v":"NJ-3AP(KT)2-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-2","03B02","水阀控制",{"$f":"AH96&\"-\"&AK96","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"AHU03B02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%Q\"&B96*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LAHU03B02_WVC AT%Q98.0 :INT ; (*空调机组NJ-3AP(KT)2-2-水阀控制*)"},"LAHU03B02_WVC           AT%Q98.0       :INT ; (*空调机组NJ-3AP(KT)2-2-水阀控制*)",null,"AHU03B02_WVC",{"$f":"J96","v":"空调机组NJ-3AP(KT)2-2-水阀控制"},{"$f":"AS95+1","v":40049}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH97&AA97&\"-\"&AK97","v":"空调机组NJ-3AP(KT)2-3-水阀控制"},{"$nulls":16},"NJ-3AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-3","03B03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":"AHU03B03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%Q\"&B96*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":"LAHU03B03_WVC AT%Q100.0 :INT ; (*空调机组NJ-3AP(KT)2-3-水阀控制*)"},"LAHU03B03_WVC           AT%Q100.0      :INT ; (*空调机组NJ-3AP(KT)2-3-水阀控制*)",null,"AHU03B03_WVC","空调机组NJ-3AP(KT)2-3-水阀控制",{"$f":"AS96+1","v":40050}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH98&AA98&\"-\"&AK98","v":"空调机组NJ-3AP(KT)2-4-水阀控制"},{"$nulls":16},"NJ-3AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-4","03B04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":"AHU03B04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%Q\"&B96*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":"LAHU03B04_WVC AT%Q102.0 :INT ; (*空调机组NJ-3AP(KT)2-4-水阀控制*)"},"LAHU03B04_WVC           AT%Q102.0      :INT ; (*空调机组NJ-3AP(KT)2-4-水阀控制*)",null,"AHU03B04_WVC","空调机组NJ-3AP(KT)2-4-水阀控制",40051]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B108","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B108&\"地址: \"&B105&\" *)\"","v":"(* IOM 0401A地址: 7 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH104&AA104&\"-\"&AK104","v":"空调机组NJ-3AP(KT)2-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI104=\"\",\"\",AI104)","v":"NJ-3AP(KT)2-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-5","03B05","水阀控制",{"$f":"AH104&\"-\"&AK104","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"AHU03B05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%Q\"&B105*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LAHU03B05_WVC AT%Q112.0 :INT ; (*空调机组NJ-3AP(KT)2-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104))),SEARCH(\":\",REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104)))))),\" \")","v":"LAHU03B05_WVC           AT%Q112.0      :INT ; (*空调机组NJ-3AP(KT)2-5-水阀控制*)"},null,{"$f":"AM104","v":"AHU03B05_WVC"},{"$f":"J104","v":"空调机组NJ-3AP(KT)2-5-水阀控制"},{"$f":"40000+($B105*8+F104-1)","v":40056}]
[null,7,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH105&AA105&\"-\"&AK105","v":"空调机组NJ-3AP(KT)2-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI105=\"\",\"\",AI105)","v":"NJ-3AP(KT)2-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)2-6","03B06","水阀控制",{"$f":"AH105&\"-\"&AK105","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"AHU03B06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%Q\"&B105*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LAHU03B06_WVC AT%Q114.0 :INT ; (*空调机组NJ-3AP(KT)2-6-水阀控制*)"},"LAHU03B06_WVC           AT%Q114.0      :INT ; (*空调机组NJ-3AP(KT)2-6-水阀控制*)",null,"AHU03B06_WVC",{"$f":"J105","v":"空调机组NJ-3AP(KT)2-6-水阀控制"},{"$f":"AS104+1","v":40057}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH106&AA106&\"-\"&AK106","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%Q\"&B105*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS105+1","v":40058}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH107&AA107&\"-\"&AK107","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH107,List!$B$3:$D$445,2,FALSE)&AJ107&\"_\"&VLOOKUP(AK107,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM107&\" \"&\"AT%Q\"&B105*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J107&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40059]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L402","index":25,"n_rows":128,"n_cols":45,"rows_kept":128,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[41,5,41,6],[41,9,41,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[75,5,75,6],[75,9,75,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[84,5,84,6],[84,9,84,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[93,5,93,6],[93,9,93,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[102,5,102,6],[102,9,102,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[109,5,109,6],[109,9,109,25],[111,5,111,6],[111,9,111,25],[112,5,112,6],[112,9,112,25],[113,5,113,6],[113,9,113,25],[114,5,114,6],[114,9,114,25],[115,5,115,6],[115,9,115,25],[116,5,116,6],[116,9,116,25],[117,5,117,6],[117,9,117,25],[118,5,118,6],[118,9,118,25],[120,5,120,6],[120,9,120,25],[121,5,121,6],[121,9,121,25],[122,5,122,6],[122,9,122,25],[123,5,123,6],[123,9,123,25],[124,5,124,6],[124,9,124,25],[125,5,125,6],[125,9,125,25],[126,5,126,6],[126,9,126,25],[127,5,127,6],[127,9,127,25],[4,1,5,1],[11,1,22,1],[28,1,39,1],[45,1,56,1],[62,1,73,1],[79,1,82,1],[88,1,91,1],[97,1,100,1],[106,1,109,1],[115,1,118,1],[124,1,127,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4],[32,2,39,4],[49,2,56,4],[66,2,73,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L20",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 8 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH8&AA8&\"-\"&AK8","v":"空调机组NJ-4AP(KT)2-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-4AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-1","04B01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH8,List!$B$3:$D$445,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,List!$K$2:$M$447,2,FALSE)","v":"AHU04B01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LAHU04B01_R AT%I128.0 :BOOL; (*空调机组NJ-4AP(KT)2-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LAHU04B01_R             AT%I128.0      :BOOL; (*空调机组NJ-4AP(KT)2-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L20\\L20AHU04B01_R"},{"$f":"J8","v":"空调机组NJ-4AP(KT)2-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":11024}]
[null,8,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-4AP(KT)2-1-故障状态",{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-4AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-1","04B01","故障状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU04B01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU04B01_F AT%I128.1 :BOOL; (*空调机组NJ-4AP(KT)2-1-故障状态*)"},"LAHU04B01_F             AT%I128.1      :BOOL; (*空调机组NJ-4AP(KT)2-1-故障状态*)",null,"L20\\L20AHU04B01_F",{"$f":"J9","v":"空调机组NJ-4AP(KT)2-1-故障状态"},{"$f":"AS8+1","v":11025}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-4AP(KT)2-1-自动状态",{"$nulls":16},"NJ-4AP(KT)2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-1","04B01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU04B01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU04B01_A AT%I128.2 :BOOL; (*空调机组NJ-4AP(KT)2-1-自动状态*)"},"LAHU04B01_A             AT%I128.2      :BOOL; (*空调机组NJ-4AP(KT)2-1-自动状态*)",null,"L20\\L20AHU04B01_A","空调机组NJ-4AP(KT)2-1-自动状态",{"$f":"AS9+1","v":11026}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-4AP(KT)2-1-风机压差",{"$nulls":16},"NJ-4AP(KT)2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-1","04B01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU04B01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU04B01_FPS AT%I128.3 :BOOL; (*空调机组NJ-4AP(KT)2-1-风机压差*)"},"LAHU04B01_FPS           AT%I128.3      :BOOL; (*空调机组NJ-4AP(KT)2-1-风机压差*)",null,"L20\\L20AHU04B01_FPS","空调机组NJ-4AP(KT)2-1-风机压差",11027]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-4AP(KT)2-2-运行状态",{"$nulls":16},"NJ-4AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-2","04B02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU04B02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU04B02_R AT%I128.4 :BOOL; (*空调机组NJ-4AP(KT)2-2-运行状态*)"},"LAHU04B02_R             AT%I128.4      :BOOL; (*空调机组NJ-4AP(KT)2-2-运行状态*)",null,"L20\\L20AHU04B02_R","空调机组NJ-4AP(KT)2-2-运行状态",11028]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-4AP(KT)2-2-故障状态",{"$nulls":16},"NJ-4AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-2","04B02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU04B02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU04B02_F AT%I128.5 :BOOL; (*空调机组NJ-4AP(KT)2-2-故障状态*)"},"LAHU04B02_F             AT%I128.5      :BOOL; (*空调机组NJ-4AP(KT)2-2-故障状态*)",null,"L20\\L20AHU04B02_F","空调机组NJ-4AP(KT)2-2-故障状态",11029]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-4AP(KT)2-2-自动状态",{"$nulls":16},"NJ-4AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-2","04B02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU04B02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU04B02_A AT%I128.6 :BOOL; (*空调机组NJ-4AP(KT)2-2-自动状态*)"},"LAHU04B02_A             AT%I128.6      :BOOL; (*空调机组NJ-4AP(KT)2-2-自动状态*)",null,"L20\\L20AHU04B02_A","空调机组NJ-4AP(KT)2-2-自动状态",11030]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-4AP(KT)2-2-风机压差",{"$nulls":16},"NJ-4AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-2","04B02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU04B02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU04B02_FPS AT%I128.7 :BOOL; (*空调机组NJ-4AP(KT)2-2-风机压差*)"},"LAHU04B02_FPS           AT%I128.7      :BOOL; (*空调机组NJ-4AP(KT)2-2-风机压差*)",null,"L20\\L20AHU04B02_FPS","空调机组NJ-4AP(KT)2-2-风机压差",11031]
[{"$nulls":5},9,null,17,18,"空调机组NJ-4AP(KT)2-3-运行状态",{"$nulls":16},"NJ-4AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-3","04B03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU04B03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU04B03_R AT%I129.0 :BOOL; (*空调机组NJ-4AP(KT)2-3-运行状态*)"},"LAHU04B03_R             AT%I129.0      :BOOL; (*空调机组NJ-4AP(KT)2-3-运行状态*)",null,"L20\\L20AHU04B03_R","空调机组NJ-4AP(KT)2-3-运行状态",11032]
[{"$nulls":5},10,null,19,20,"空调机组NJ-4AP(KT)2-3-故障状态",{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-4AP(KT)2-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-3","04B03","故障状态",{"$f":"AH17&\"-\"&AK17","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU04B03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU04B03_F AT%I129.1 :BOOL; (*空调机组NJ-4AP(KT)2-3-故障状态*)"},"LAHU04B03_F             AT%I129.1      :BOOL; (*空调机组NJ-4AP(KT)2-3-故障状态*)",null,"L20\\L20AHU04B03_F","空调机组NJ-4AP(KT)2-3-故障状态",11033]
[{"$nulls":5},11,null,21,22,"空调机组NJ-4AP(KT)2-3-自动状态",{"$nulls":16},"NJ-4AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-3","04B03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU04B03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU04B03_A AT%I129.2 :BOOL; (*空调机组NJ-4AP(KT)2-3-自动状态*)"},"LAHU04B03_A             AT%I129.2      :BOOL; (*空调机组NJ-4AP(KT)2-3-自动状态*)",null,"L20\\L20AHU04B03_A","空调机组NJ-4AP(KT)2-3-自动状态",11034]
[{"$nulls":5},12,null,23,24,"空调机组NJ-4AP(KT)2-3-风机压差",{"$nulls":16},"NJ-4AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-3","04B03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU04B03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU04B03_FPS AT%I129.3 :BOOL; (*空调机组NJ-4AP(KT)2-3-风机压差*)"},"LAHU04B03_FPS           AT%I129.3      :BOOL; (*空调机组NJ-4AP(KT)2-3-风机压差*)",null,"L20\\L20AHU04B03_FPS","空调机组NJ-4AP(KT)2-3-风机压差",11035]
[{"$nulls":5},13,null,25,26,"空调机组NJ-4AP(KT)2-4-运行状态",{"$nulls":16},"NJ-4AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-4","04B04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU04B04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU04B04_R AT%I129.4 :BOOL; (*空调机组NJ-4AP(KT)2-4-运行状态*)"},"LAHU04B04_R             AT%I129.4      :BOOL; (*空调机组NJ-4AP(KT)2-4-运行状态*)",null,"L20\\L20AHU04B04_R","空调机组NJ-4AP(KT)2-4-运行状态",11036]
[{"$nulls":5},14,null,27,28,"空调机组NJ-4AP(KT)2-4-故障状态",{"$nulls":16},"NJ-4AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-4","04B04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU04B04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU04B04_F AT%I129.5 :BOOL; (*空调机组NJ-4AP(KT)2-4-故障状态*)"},"LAHU04B04_F             AT%I129.5      :BOOL; (*空调机组NJ-4AP(KT)2-4-故障状态*)",null,"L20\\L20AHU04B04_F","空调机组NJ-4AP(KT)2-4-故障状态",11037]
[{"$nulls":5},15,null,29,30,"空调机组NJ-4AP(KT)2-4-自动状态",{"$nulls":16},"NJ-4AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-4","04B04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU04B04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU04B04_A AT%I129.6 :BOOL; (*空调机组NJ-4AP(KT)2-4-自动状态*)"},"LAHU04B04_A             AT%I129.6      :BOOL; (*空调机组NJ-4AP(KT)2-4-自动状态*)",null,"L20\\L20AHU04B04_A","空调机组NJ-4AP(KT)2-4-自动状态",11038]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-4AP(KT)2-4-风机压差",{"$nulls":16},"NJ-4AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-4","04B04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU04B04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU04B04_FPS AT%I129.7 :BOOL; (*空调机组NJ-4AP(KT)2-4-风机压差*)"},"LAHU04B04_FPS           AT%I129.7      :BOOL; (*空调机组NJ-4AP(KT)2-4-风机压差*)",null,"L20\\L20AHU04B04_FPS","空调机组NJ-4AP(KT)2-4-风机压差",11039]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 1601R地址: 9 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH25&AA25&\"-\"&AK25","v":"空调机组NJ-4AP(KT)2-5-运行状态"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-4AP(KT)2-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-5","04B05","运行状态",{"$f":"AH25&\"-\"&AK25","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"AHU04B05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LAHU04B05_R AT%I144.0 :BOOL; (*空调机组NJ-4AP(KT)2-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LAHU04B05_R             AT%I144.0      :BOOL; (*空调机组NJ-4AP(KT)2-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L20\\L20AHU04B05_R"},{"$f":"J25","v":"空调机组NJ-4AP(KT)2-5-运行状态"},{"$f":"10000+($B26*16*8+F25-1)","v":11152}]
[null,9,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-4AP(KT)2-5-故障状态",{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-4AP(KT)2-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-5","04B05","故障状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU04B05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU04B05_F AT%I144.1 :BOOL; (*空调机组NJ-4AP(KT)2-5-故障状态*)"},"LAHU04B05_F             AT%I144.1      :BOOL; (*空调机组NJ-4AP(KT)2-5-故障状态*)",null,"L20\\L20AHU04B05_F",{"$f":"J26","v":"空调机组NJ-4AP(KT)2-5-故障状态"},{"$f":"AS25+1","v":11153}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-4AP(KT)2-5-自动状态",{"$nulls":16},"NJ-4AP(KT)2-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-5","04B05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU04B05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU04B05_A AT%I144.2 :BOOL; (*空调机组NJ-4AP(KT)2-5-自动状态*)"},"LAHU04B05_A             AT%I144.2      :BOOL; (*空调机组NJ-4AP(KT)2-5-自动状态*)",null,"L20\\L20AHU04B05_A","空调机组NJ-4AP(KT)2-5-自动状态",{"$f":"AS26+1","v":11154}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-4AP(KT)2-5-风机压差",{"$nulls":16},"NJ-4AP(KT)2-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-5","04B05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU04B05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU04B05_FPS AT%I144.3 :BOOL; (*空调机组NJ-4AP(KT)2-5-风机压差*)"},"LAHU04B05_FPS           AT%I144.3      :BOOL; (*空调机组NJ-4AP(KT)2-5-风机压差*)",null,"L20\\L20AHU04B05_FPS","空调机组NJ-4AP(KT)2-5-风机压差",11155]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-4AP(KT)2-6-运行状态",{"$nulls":16},"NJ-4AP(KT)2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-6","04B06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU04B06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU04B06_R AT%I144.4 :BOOL; (*空调机组NJ-4AP(KT)2-6-运行状态*)"},"LAHU04B06_R             AT%I144.4      :BOOL; (*空调机组NJ-4AP(KT)2-6-运行状态*)",null,"L20\\L20AHU04B06_R","空调机组NJ-4AP(KT)2-6-运行状态",11156]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-4AP(KT)2-6-故障状态",{"$nulls":16},"NJ-4AP(KT)2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-6","04B06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU04B06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU04B06_F AT%I144.5 :BOOL; (*空调机组NJ-4AP(KT)2-6-故障状态*)"},"LAHU04B06_F             AT%I144.5      :BOOL; (*空调机组NJ-4AP(KT)2-6-故障状态*)",null,"L20\\L20AHU04B06_F","空调机组NJ-4AP(KT)2-6-故障状态",11157]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-4AP(KT)2-6-自动状态",{"$nulls":16},"NJ-4AP(KT)2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-6","04B06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU04B06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU04B06_A AT%I144.6 :BOOL; (*空调机组NJ-4AP(KT)2-6-自动状态*)"},"LAHU04B06_A             AT%I144.6      :BOOL; (*空调机组NJ-4AP(KT)2-6-自动状态*)",null,"L20\\L20AHU04B06_A","空调机组NJ-4AP(KT)2-6-自动状态",11158]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-4AP(KT)2-6-风机压差",{"$nulls":16},"NJ-4AP(KT)2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-6","04B06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU04B06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU04B06_FPS AT%I144.7 :BOOL; (*空调机组NJ-4AP(KT)2-6-风机压差*)"},"LAHU04B06_FPS           AT%I144.7      :BOOL; (*空调机组NJ-4AP(KT)2-6-风机压差*)",null,"L20\\L20AHU04B06_FPS","空调机组NJ-4AP(KT)2-6-风机压差",11159]
[{"$nulls":5},9,null,17,18,"空调机组NJ-4AP(KT)2-7-运行状态",{"$nulls":16},"NJ-4AP(KT)2-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-7","04B07","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU04B07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B26*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU04B07_R AT%I145.0 :BOOL; (*空调机组NJ-4AP(KT)2-7-运行状态*)"},"LAHU04B07_R             AT%I145.0      :BOOL; (*空调机组NJ-4AP(KT)2-7-运行状态*)",null,"L20\\L20AHU04B07_R","空调机组NJ-4AP(KT)2-7-运行状态",11160]
[{"$nulls":5},10,null,19,20,"空调机组NJ-4AP(KT)2-7-故障状态",{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-4AP(KT)2-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-7","04B07","故障状态",{"$f":"AH34&\"-\"&AK34","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU04B07_F"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B26*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU04B07_F AT%I145.1 :BOOL; (*空调机组NJ-4AP(KT)2-7-故障状态*)"},"LAHU04B07_F             AT%I145.1      :BOOL; (*空调机组NJ-4AP(KT)2-7-故障状态*)",null,"L20\\L20AHU04B07_F",{"$f":"J34","v":"空调机组NJ-4AP(KT)2-7-故障状态"},11161]
[{"$nulls":5},11,null,21,22,"空调机组NJ-4AP(KT)2-7-自动状态",{"$nulls":16},"NJ-4AP(KT)2-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-7","04B07","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU04B07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B26*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU04B07_A AT%I145.2 :BOOL; (*空调机组NJ-4AP(KT)2-7-自动状态*)"},"LAHU04B07_A             AT%I145.2      :BOOL; (*空调机组NJ-4AP(KT)2-7-自动状态*)",null,"L20\\L20AHU04B07_A","空调机组NJ-4AP(KT)2-7-自动状态",11162]
[{"$nulls":5},12,null,23,24,"空调机组NJ-4AP(KT)2-7-风机压差",{"$nulls":16},"NJ-4AP(KT)2-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-7","04B07","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU04B07_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B26*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU04B07_FPS AT%I145.3 :BOOL; (*空调机组NJ-4AP(KT)2-7-风机压差*)"},"LAHU04B07_FPS           AT%I145.3      :BOOL; (*空调机组NJ-4AP(KT)2-7-风机压差*)",null,"L20\\L20AHU04B07_FPS","空调机组NJ-4AP(KT)2-7-风机压差",11163]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-4AL2-1-运行状态",{"$nulls":16},"NJ-4AL2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-1","04B01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"LCB04B01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B26*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LLCB04B01_R AT%I145.4 :BOOL; (*照明控制箱NJ-4AL2-1-运行状态*)"},"LLCB04B01_R             AT%I145.4      :BOOL; (*照明控制箱NJ-4AL2-1-运行状态*)",null,"L20\\L20LCB04B01_R","照明控制箱NJ-4AL2-1-运行状态",11164]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-4AL2-1-自动状态",{"$nulls":16},"NJ-4AL2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-1","04B01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB04B01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B26*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB04B01_A AT%I145.5 :BOOL; (*照明控制箱NJ-4AL2-1-自动状态*)"},"LLCB04B01_A             AT%I145.5      :BOOL; (*照明控制箱NJ-4AL2-1-自动状态*)",null,"L20\\L20LCB04B01_A","照明控制箱NJ-4AL2-1-自动状态",11165]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-4AL2-2-运行状态",{"$nulls":16},"NJ-4AL2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-2","04B02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB04B02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B26*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB04B02_R AT%I145.6 :BOOL; (*照明控制箱NJ-4AL2-2-运行状态*)"},"LLCB04B02_R             AT%I145.6      :BOOL; (*照明控制箱NJ-4AL2-2-运行状态*)",null,"L20\\L20LCB04B02_R","照明控制箱NJ-4AL2-2-运行状态",11166]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-4AL2-2-自动状态",{"$nulls":16},"NJ-4AL2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-2","04B02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"LCB04B02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B26*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LLCB04B02_A AT%I145.7 :BOOL; (*照明控制箱NJ-4AL2-2-自动状态*)"},"LLCB04B02_A             AT%I145.7      :BOOL; (*照明控制箱NJ-4AL2-2-自动状态*)",null,"L20\\L20LCB04B02_A","照明控制箱NJ-4AL2-2-自动状态",11167]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B46&\"地址: \"&B43&\" *)\"","v":"(* IOM 1601R地址: 10 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH42&AA42&\"-\"&AK42","v":"照明控制箱NJ-4AL2-3-运行状态"},{"$nulls":16},{"$f":"IF(AI42=\"\",\"\",AI42)","v":"NJ-4AL2-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-3","04B03","运行状态",{"$f":"AH42&\"-\"&AK42","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":"LCB04B03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%I\"&B43*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":"LLCB04B03_R AT%I160.0 :BOOL; (*照明控制箱NJ-4AL2-3-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42))),SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))))),\" \")","v":"LLCB04B03_R             AT%I160.0      :BOOL; (*照明控制箱NJ-4AL2-3-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM42","v":"L20\\L20LCB04B03_R"},{"$f":"J42","v":"照明控制箱NJ-4AL2-3-运行状态"},{"$f":"10000+($B43*16*8+F42-1)","v":11280}]
[null,10,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},2,null,3,4,"照明控制箱NJ-4AL2-3-自动状态",{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-4AL2-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-3","04B03","自动状态",{"$f":"AH43&\"-\"&AK43","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"LCB04B03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B43*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LLCB04B03_A AT%I160.1 :BOOL; (*照明控制箱NJ-4AL2-3-自动状态*)"},"LLCB04B03_A             AT%I160.1      :BOOL; (*照明控制箱NJ-4AL2-3-自动状态*)",null,"L20\\L20LCB04B03_A",{"$f":"J43","v":"照明控制箱NJ-4AL2-3-自动状态"},{"$f":"AS42+1","v":11281}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":0},3,null,5,6,"照明控制箱NJ-4AL2-4-运行状态",{"$nulls":16},"NJ-4AL2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-4","04B04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"LCB04B04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B43*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LLCB04B04_R AT%I160.2 :BOOL; (*照明控制箱NJ-4AL2-4-运行状态*)"},"LLCB04B04_R             AT%I160.2      :BOOL; (*照明控制箱NJ-4AL2-4-运行状态*)",null,"L20\\L20LCB04B04_R","照明控制箱NJ-4AL2-4-运行状态",{"$f":"AS43+1","v":11282}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},4,null,7,8,"照明控制箱NJ-4AL2-4-自动状态",{"$nulls":16},"NJ-4AL2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-4","04B04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"LCB04B04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B43*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LLCB04B04_A AT%I160.3 :BOOL; (*照明控制箱NJ-4AL2-4-自动状态*)"},"LLCB04B04_A             AT%I160.3      :BOOL; (*照明控制箱NJ-4AL2-4-自动状态*)",null,"L20\\L20LCB04B04_A","照明控制箱NJ-4AL2-4-自动状态",11283]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-4AL2-5-运行状态",{"$nulls":16},"NJ-4AL2-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-5","04B05","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"LCB04B05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B43*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LLCB04B05_R AT%I160.4 :BOOL; (*照明控制箱NJ-4AL2-5-运行状态*)"},"LLCB04B05_R             AT%I160.4      :BOOL; (*照明控制箱NJ-4AL2-5-运行状态*)",null,"L20\\L20LCB04B05_R","照明控制箱NJ-4AL2-5-运行状态",11284]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-4AL2-5-自动状态",{"$nulls":16},"NJ-4AL2-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-5","04B05","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"LCB04B05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B43*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LLCB04B05_A AT%I160.5 :BOOL; (*照明控制箱NJ-4AL2-5-自动状态*)"},"LLCB04B05_A             AT%I160.5      :BOOL; (*照明控制箱NJ-4AL2-5-自动状态*)",null,"L20\\L20LCB04B05_A","照明控制箱NJ-4AL2-5-自动状态",11285]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"照明控制箱NJ-4AL2-6-运行状态",{"$nulls":16},"NJ-4AL2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-6","04B06","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"LCB04B06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B43*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LLCB04B06_R AT%I160.6 :BOOL; (*照明控制箱NJ-4AL2-6-运行状态*)"},"LLCB04B06_R             AT%I160.6      :BOOL; (*照明控制箱NJ-4AL2-6-运行状态*)",null,"L20\\L20LCB04B06_R","照明控制箱NJ-4AL2-6-运行状态",11286]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"照明控制箱NJ-4AL2-6-自动状态",{"$nulls":16},"NJ-4AL2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-6","04B06","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"LCB04B06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B43*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LLCB04B06_A AT%I160.7 :BOOL; (*照明控制箱NJ-4AL2-6-自动状态*)"},"LLCB04B06_A             AT%I160.7      :BOOL; (*照明控制箱NJ-4AL2-6-自动状态*)",null,"L20\\L20LCB04B06_A","照明控制箱NJ-4AL2-6-自动状态",11287]
[{"$nulls":5},9,null,17,18,"遮阳帘-运行状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04B01","运行状态","遮阳帘-运行状态",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"SSC04B01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B43*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LSSC04B01_R AT%I161.0 :BOOL; (*遮阳帘-运行状态*)"},"LSSC04B01_R             AT%I161.0      :BOOL; (*遮阳帘-运行状态*)",null,"L20\\L20SSC04B01_R","遮阳帘-运行状态",11288]
[{"$nulls":5},10,null,19,20,"遮阳帘-自动状态",{"$nulls":16},{"$f":"IF(AI51=\"\",\"\",AI51)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04B01","自动状态",{"$f":"AH51&\"-\"&AK51","v":"遮阳帘-自动状态"},{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"SSC04B01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B43*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LSSC04B01_A AT%I161.1 :BOOL; (*遮阳帘-自动状态*)"},"LSSC04B01_A             AT%I161.1      :BOOL; (*遮阳帘-自动状态*)",null,"L20\\L20SSC04B01_A",{"$f":"J51","v":"遮阳帘-自动状态"},11289]
[{"$nulls":5},11,null,21,22,"遮阳帘-运行状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04B02","运行状态","遮阳帘-运行状态",{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"SSC04B02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%I\"&B43*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LSSC04B02_R AT%I161.2 :BOOL; (*遮阳帘-运行状态*)"},"LSSC04B02_R             AT%I161.2      :BOOL; (*遮阳帘-运行状态*)",null,"L20\\L20SSC04B02_R","遮阳帘-运行状态",11290]
[{"$nulls":5},12,null,23,24,"遮阳帘-自动状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04B02","自动状态","遮阳帘-自动状态",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"SSC04B02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%I\"&B43*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LSSC04B02_A AT%I161.3 :BOOL; (*遮阳帘-自动状态*)"},"LSSC04B02_A             AT%I161.3      :BOOL; (*遮阳帘-自动状态*)",null,"L20\\L20SSC04B02_A","遮阳帘-自动状态",11291]
[{"$nulls":5},13,null,25,26,"风机盘管NJ-4AP(KT)2-1-运行状态",{"$nulls":16},"NJ-4AP(KT)2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)2-1","04B01","运行状态","风机盘管-运行状态",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"FCU04B01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%I\"&B43*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LFCU04B01_R AT%I161.4 :BOOL; (*风机盘管NJ-4AP(KT)2-1-运行状态*)"},"LFCU04B01_R             AT%I161.4      :BOOL; (*风机盘管NJ-4AP(KT)2-1-运行状态*)",null,"L20\\L20FCU04B01_R","风机盘管NJ-4AP(KT)2-1-运行状态",11292]
[{"$nulls":5},14,null,27,28,"风机盘管NJ-4AP(KT)2-1-自动状态",{"$nulls":16},"NJ-4AP(KT)2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)2-1","04B01","自动状态","风机盘管-自动状态",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"FCU04B01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%I\"&B43*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LFCU04B01_A AT%I161.5 :BOOL; (*风机盘管NJ-4AP(KT)2-1-自动状态*)"},"LFCU04B01_A             AT%I161.5      :BOOL; (*风机盘管NJ-4AP(KT)2-1-自动状态*)",null,"L20\\L20FCU04B01_A","风机盘管NJ-4AP(KT)2-1-自动状态",11293]
[{"$nulls":5},15,null,29,30,"风机盘管NJ-4AP(KT)2-1-电磁阀开启状态",{"$nulls":16},"NJ-4AP(KT)2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)2-1","04B01","电磁阀开启状态","风机盘管-电磁阀开启状态",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"FCU04B01_EVR"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%I\"&B43*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LFCU04B01_EVR AT%I161.6 :BOOL; (*风机盘管NJ-4AP(KT)2-1-电磁阀开启状态*)"},"LFCU04B01_EVR           AT%I161.6      :BOOL; (*风机盘管NJ-4AP(KT)2-1-电磁阀开启状态*)",null,"L20\\L20FCU04B01_EVR","风机盘管NJ-4AP(KT)2-1-电磁阀开启状态",11294]
[".",{"$nulls":4},16,null,31,32,"风机盘管NJ-4AP(KT)2-1-电磁阀自动状态",{"$nulls":16},"NJ-4AP(KT)2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)2-1","04B01","电磁阀自动状态","风机盘管-电磁阀自动状态",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"FCU04B01_EVA"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%I\"&B43*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LFCU04B01_EVA AT%I161.7 :BOOL; (*风机盘管NJ-4AP(KT)2-1-电磁阀自动状态*)"},"LFCU04B01_EVA           AT%I161.7      :BOOL; (*风机盘管NJ-4AP(KT)2-1-电磁阀自动状态*)",null,"L20\\L20FCU04B01_EVA","风机盘管NJ-4AP(KT)2-1-电磁阀自动状态",11295]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B63&\"地址: \"&B60&\" *)\"","v":"(* IOM 1601D地址: 11 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH59&AA59&\"-\"&AK59","v":"空调机组NJ-4AP(KT)2-1-启停控制"},{"$nulls":16},{"$f":"IF(AI59=\"\",\"\",AI59)","v":"NJ-4AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-1","04B01","启停控制",{"$f":"AH59&\"-\"&AK59","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH59,List!$B$3:$D$445,2,FALSE)&AJ59&\"_\"&VLOOKUP(AK59,List!$K$2:$M$447,2,FALSE)","v":"AHU04B01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM59&\" \"&\"AT%Q\"&B60*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J59&\"*)\",\" \")","v":"LAHU04B01_C AT%Q176.0 :BOOL; (*空调机组NJ-4AP(KT)2-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59))),SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))))),\" \")","v":"LAHU04B01_C             AT%Q176.0      :BOOL; (*空调机组NJ-4AP(KT)2-1-启停控制*)"},null,{"$f":"AM59","v":"AHU04B01_C"},{"$f":"J59","v":"空调机组NJ-4AP(KT)2-1-启停控制"},{"$f":"($B60*16*8+F59-1)","v":1408}]
[null,11,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-4AP(KT)2-2-启停控制",{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-4AP(KT)2-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-2","04B02","启停控制",{"$f":"AH60&\"-\"&AK60","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"AHU04B02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%Q\"&B60*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LAHU04B02_C AT%Q176.1 :BOOL; (*空调机组NJ-4AP(KT)2-2-启停控制*)"},"LAHU04B02_C             AT%Q176.1      :BOOL; (*空调机组NJ-4AP(KT)2-2-启停控制*)",null,"AHU04B02_C",{"$f":"J60","v":"空调机组NJ-4AP(KT)2-2-启停控制"},{"$f":"AS59+1","v":1409}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","空调机组NJ-4AP(KT)2-3-启停控制",{"$nulls":16},"NJ-4AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-3","04B03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"AHU04B03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%Q\"&B60*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LAHU04B03_C AT%Q176.2 :BOOL; (*空调机组NJ-4AP(KT)2-3-启停控制*)"},"LAHU04B03_C             AT%Q176.2      :BOOL; (*空调机组NJ-4AP(KT)2-3-启停控制*)",null,"AHU04B03_C","空调机组NJ-4AP(KT)2-3-启停控制",{"$f":"AS60+1","v":1410}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","空调机组NJ-4AP(KT)2-4-启停控制",{"$nulls":16},"NJ-4AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-4","04B04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"AHU04B04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%Q\"&B60*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LAHU04B04_C AT%Q176.3 :BOOL; (*空调机组NJ-4AP(KT)2-4-启停控制*)"},"LAHU04B04_C             AT%Q176.3      :BOOL; (*空调机组NJ-4AP(KT)2-4-启停控制*)",null,"AHU04B04_C","空调机组NJ-4AP(KT)2-4-启停控制",1411]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-4AP(KT)2-5-启停控制",{"$nulls":16},"NJ-4AP(KT)2-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-5","04B05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"AHU04B05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%Q\"&B60*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LAHU04B05_C AT%Q176.4 :BOOL; (*空调机组NJ-4AP(KT)2-5-启停控制*)"},"LAHU04B05_C             AT%Q176.4      :BOOL; (*空调机组NJ-4AP(KT)2-5-启停控制*)",null,"AHU04B05_C","空调机组NJ-4AP(KT)2-5-启停控制",1412]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-4AP(KT)2-6-启停控制",{"$nulls":16},"NJ-4AP(KT)2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-6","04B06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"AHU04B06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%Q\"&B60*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LAHU04B06_C AT%Q176.5 :BOOL; (*空调机组NJ-4AP(KT)2-6-启停控制*)"},"LAHU04B06_C             AT%Q176.5      :BOOL; (*空调机组NJ-4AP(KT)2-6-启停控制*)",null,"AHU04B06_C","空调机组NJ-4AP(KT)2-6-启停控制",1413]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","空调机组NJ-4AP(KT)2-7-启停控制",{"$nulls":16},"NJ-4AP(KT)2-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-7","04B07","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":"AHU04B07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%Q\"&B60*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":"LAHU04B07_C AT%Q176.6 :BOOL; (*空调机组NJ-4AP(KT)2-7-启停控制*)"},"LAHU04B07_C             AT%Q176.6      :BOOL; (*空调机组NJ-4AP(KT)2-7-启停控制*)",null,"AHU04B07_C","空调机组NJ-4AP(KT)2-7-启停控制",1414]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-4AL2-1-启停控制",{"$nulls":16},"NJ-4AL2-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-1","04B01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":"LCB04B01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%Q\"&B60*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":"LLCB04B01_C AT%Q176.7 :BOOL; (*照明控制箱NJ-4AL2-1-启停控制*)"},"LLCB04B01_C             AT%Q176.7      :BOOL; (*照明控制箱NJ-4AL2-1-启停控制*)",null,"LCB04B01_C","照明控制箱NJ-4AL2-1-启停控制",1415]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-4AL2-2-启停控制",{"$nulls":16},"NJ-4AL2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-2","04B02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":"LCB04B02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%Q\"&B60*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":"LLCB04B02_C AT%Q177.0 :BOOL; (*照明控制箱NJ-4AL2-2-启停控制*)"},"LLCB04B02_C             AT%Q177.0      :BOOL; (*照明控制箱NJ-4AL2-2-启停控制*)",null,"LCB04B02_C","照明控制箱NJ-4AL2-2-启停控制",1416]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-4AL2-3-启停控制",{"$nulls":16},{"$f":"IF(AI68=\"\",\"\",AI68)","v":"NJ-4AL2-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-3","04B03","启停控制",{"$f":"AH68&\"-\"&AK68","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"LCB04B03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%Q\"&B60*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LLCB04B03_C AT%Q177.1 :BOOL; (*照明控制箱NJ-4AL2-3-启停控制*)"},"LLCB04B03_C             AT%Q177.1      :BOOL; (*照明控制箱NJ-4AL2-3-启停控制*)",null,"LCB04B03_C",{"$f":"J68","v":"照明控制箱NJ-4AL2-3-启停控制"},1417]
[{"$nulls":5},11,null,"11+","11-","照明控制箱NJ-4AL2-4-启停控制",{"$nulls":16},"NJ-4AL2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-4","04B04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"LCB04B04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%Q\"&B60*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LLCB04B04_C AT%Q177.2 :BOOL; (*照明控制箱NJ-4AL2-4-启停控制*)"},"LLCB04B04_C             AT%Q177.2      :BOOL; (*照明控制箱NJ-4AL2-4-启停控制*)",null,"LCB04B04_C","照明控制箱NJ-4AL2-4-启停控制",1418]
[{"$nulls":5},12,null,"12+","12-","照明控制箱NJ-4AL2-5-启停控制",{"$nulls":16},"NJ-4AL2-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-5","04B05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"LCB04B05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%Q\"&B60*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LLCB04B05_C AT%Q177.3 :BOOL; (*照明控制箱NJ-4AL2-5-启停控制*)"},"LLCB04B05_C             AT%Q177.3      :BOOL; (*照明控制箱NJ-4AL2-5-启停控制*)",null,"LCB04B05_C","照明控制箱NJ-4AL2-5-启停控制",1419]
[{"$nulls":5},13,null,"13+","13-","照明控制箱NJ-4AL2-6-启停控制",{"$nulls":16},"NJ-4AL2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL2-6","04B06","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"LCB04B06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%Q\"&B60*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LLCB04B06_C AT%Q177.4 :BOOL; (*照明控制箱NJ-4AL2-6-启停控制*)"},"LLCB04B06_C             AT%Q177.4      :BOOL; (*照明控制箱NJ-4AL2-6-启停控制*)",null,"LCB04B06_C","照明控制箱NJ-4AL2-6-启停控制",1420]
[{"$nulls":5},14,null,"14+","14-","遮阳帘-启停控制",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04B01","启停控制","遮阳帘-启停控制",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"SSC04B01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%Q\"&B60*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LSSC04B01_C AT%Q177.5 :BOOL; (*遮阳帘-启停控制*)"},"LSSC04B01_C             AT%Q177.5      :BOOL; (*遮阳帘-启停控制*)",null,"SSC04B01_C","遮阳帘-启停控制",1421]
[{"$nulls":5},15,null,"15+","15-","遮阳帘-启停控制",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04B02","启停控制","遮阳帘-启停控制",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"SSC04B02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%Q\"&B60*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LSSC04B02_C AT%Q177.6 :BOOL; (*遮阳帘-启停控制*)"},"LSSC04B02_C             AT%Q177.6      :BOOL; (*遮阳帘-启停控制*)",null,"SSC04B02_C","遮阳帘-启停控制",1422]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%Q\"&B60*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1423]
[null,"IOM 0801D",{"$nulls":38},{"$f":"\"(* \"&B80&\"地址: \"&B77&\" *)\"","v":"(* IOM 0801D地址: 12 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH76&AA76&\"-\"&AK76","v":"风机盘管NJ-4AP(KT)2-1-启停控制"},{"$nulls":16},{"$f":"IF(AI76=\"\",\"\",AI76)","v":"NJ-4AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)2-1","04B01","启停控制",{"$f":"AH76&\"-\"&AK76","v":"风机盘管-启停控制"},{"$f":"VLOOKUP(AH76,List!$B$3:$D$445,2,FALSE)&AJ76&\"_\"&VLOOKUP(AK76,List!$K$2:$M$447,2,FALSE)","v":"FCU04B01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM76&\" \"&\"AT%Q\"&B77*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J76&\"*)\",\" \")","v":"LFCU04B01_C AT%Q192.0 :BOOL; (*风机盘管NJ-4AP(KT)2-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN76,SEARCH(\"AT%\",AN76),,REPT(\" \",25-SEARCH(\"AT%\",AN76))),SEARCH(\":\",REPLACE(AN76,SEARCH(\"AT%\",AN76),,REPT(\" \",25-SEARCH(\"AT%\",AN76)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN76,SEARCH(\"AT%\",AN76),,REPT(\" \",25-SEARCH(\"AT%\",AN76)))))),\" \")","v":"LFCU04B01_C             AT%Q192.0      :BOOL; (*风机盘管NJ-4AP(KT)2-1-启停控制*)"},null,{"$f":"AM76","v":"FCU04B01_C"},{"$f":"J76","v":"风机盘管NJ-4AP(KT)2-1-启停控制"},{"$f":"($B77*16*8+F76-1)","v":1536}]
[null,12,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","风机盘管NJ-4AP(KT)2-1-电磁阀开关控制",{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-4AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)2-1","04B01","电磁阀开关控制",{"$f":"AH77&\"-\"&AK77","v":"风机盘管-电磁阀开关控制"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"FCU04B01_EVC"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%Q\"&B77*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LFCU04B01_EVC AT%Q192.1 :BOOL; (*风机盘管NJ-4AP(KT)2-1-电磁阀开关控制*)"},"LFCU04B01_EVC           AT%Q192.1      :BOOL; (*风机盘管NJ-4AP(KT)2-1-电磁阀开关控制*)",null,"FCU04B01_EVC",{"$f":"J77","v":"风机盘管NJ-4AP(KT)2-1-电磁阀开关控制"},{"$f":"AS76+1","v":1537}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B77*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS77+1","v":1538}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B77*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1539]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B77*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1540]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%Q\"&B77*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1541]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%Q\"&B77*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1542]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%Q\"&B77*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1543]
[null,{"$f":"B89","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B89&\"地址: \"&B86&\" *)\"","v":"(* IOM 0801U地址: 13 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH85&AA85&\"-\"&AK85","v":"空调机组NJ-4AP(KT)2-1-回风温度"},{"$nulls":16},{"$f":"IF(AI85=\"\",\"\",AI85)","v":"NJ-4AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-1","04B01","回风温度",{"$f":"AH85&\"-\"&AK85","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH85,List!$B$3:$D$445,2,FALSE)&AJ85&\"_\"&VLOOKUP(AK85,List!$K$2:$M$447,2,FALSE)","v":"AHU04B01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM85&\" \"&\"AT%I\"&B86*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J85&\"*)\",\" \")","v":"LAHU04B01_RT AT%I208.0 :INT ; (*空调机组NJ-4AP(KT)2-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN85,SEARCH(\"AT%\",AN85),,REPT(\" \",25-SEARCH(\"AT%\",AN85))),SEARCH(\":\",REPLACE(AN85,SEARCH(\"AT%\",AN85),,REPT(\" \",25-SEARCH(\"AT%\",AN85)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN85,SEARCH(\"AT%\",AN85),,REPT(\" \",25-SEARCH(\"AT%\",AN85)))))),\" \")","v":"LAHU04B01_RT            AT%I208.0      :INT ; (*空调机组NJ-4AP(KT)2-1-回风温度*)"},null,{"$f":"AM85","v":"AHU04B01_RT"},{"$f":"J85","v":"空调机组NJ-4AP(KT)2-1-回风温度"},{"$f":"30000+($B86*8+F85-1)","v":30104}]
[null,13,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-4AP(KT)2-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-4AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-1","04B01","水阀反馈",{"$f":"AH86&\"-\"&AK86","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"AHU04B01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%I\"&B86*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LAHU04B01_WVB AT%I210.0 :INT ; (*空调机组NJ-4AP(KT)2-1-水阀反馈*)"},"LAHU04B01_WVB           AT%I210.0      :INT ; (*空调机组NJ-4AP(KT)2-1-水阀反馈*)",null,"AHU04B01_WVB",{"$f":"J86","v":"空调机组NJ-4AP(KT)2-1-水阀反馈"},{"$f":"AS85+1","v":30105}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-4AP(KT)2-2-回风温度",{"$nulls":16},"NJ-4AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-2","04B02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"AHU04B02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%I\"&B86*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LAHU04B02_RT AT%I212.0 :INT ; (*空调机组NJ-4AP(KT)2-2-回风温度*)"},"LAHU04B02_RT            AT%I212.0      :INT ; (*空调机组NJ-4AP(KT)2-2-回风温度*)",null,"AHU04B02_RT","空调机组NJ-4AP(KT)2-2-回风温度",{"$f":"AS86+1","v":30106}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-4AP(KT)2-2-水阀反馈",{"$nulls":16},"NJ-4AP(KT)2-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-2","04B02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"AHU04B02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%I\"&B86*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LAHU04B02_WVB AT%I214.0 :INT ; (*空调机组NJ-4AP(KT)2-2-水阀反馈*)"},"LAHU04B02_WVB           AT%I214.0      :INT ; (*空调机组NJ-4AP(KT)2-2-水阀反馈*)",null,"AHU04B02_WVB","空调机组NJ-4AP(KT)2-2-水阀反馈",30107]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-4AP(KT)2-3-回风温度",{"$nulls":16},"NJ-4AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-3","04B03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"AHU04B03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%I\"&B86*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LAHU04B03_RT AT%I216.0 :INT ; (*空调机组NJ-4AP(KT)2-3-回风温度*)"},"LAHU04B03_RT            AT%I216.0      :INT ; (*空调机组NJ-4AP(KT)2-3-回风温度*)",null,"AHU04B03_RT","空调机组NJ-4AP(KT)2-3-回风温度",30108]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-4AP(KT)2-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI90=\"\",\"\",AI90)","v":"NJ-4AP(KT)2-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-3","04B03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":"AHU04B03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%I\"&B86*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":"LAHU04B03_WVB AT%I218.0 :INT ; (*空调机组NJ-4AP(KT)2-3-水阀反馈*)"},"LAHU04B03_WVB           AT%I218.0      :INT ; (*空调机组NJ-4AP(KT)2-3-水阀反馈*)",null,"AHU04B03_WVB",{"$f":"J90","v":"空调机组NJ-4AP(KT)2-3-水阀反馈"},30109]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-4AP(KT)2-4-回风温度",{"$nulls":16},"NJ-4AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-4","04B04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH91,List!$B$3:$D$445,2,FALSE)&AJ91&\"_\"&VLOOKUP(AK91,List!$K$2:$M$447,2,FALSE)","v":"AHU04B04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM91&\" \"&\"AT%I\"&B86*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J91&\"*)\",\" \")","v":"LAHU04B04_RT AT%I220.0 :INT ; (*空调机组NJ-4AP(KT)2-4-回风温度*)"},"LAHU04B04_RT            AT%I220.0      :INT ; (*空调机组NJ-4AP(KT)2-4-回风温度*)",null,"AHU04B04_RT","空调机组NJ-4AP(KT)2-4-回风温度",30110]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-4AP(KT)2-4-水阀反馈",{"$nulls":16},"NJ-4AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-4","04B04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH92,List!$B$3:$D$445,2,FALSE)&AJ92&\"_\"&VLOOKUP(AK92,List!$K$2:$M$447,2,FALSE)","v":"AHU04B04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM92&\" \"&\"AT%I\"&B86*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J92&\"*)\",\" \")","v":"LAHU04B04_WVB AT%I222.0 :INT ; (*空调机组NJ-4AP(KT)2-4-水阀反馈*)"},"LAHU04B04_WVB           AT%I222.0      :INT ; (*空调机组NJ-4AP(KT)2-4-水阀反馈*)",null,"AHU04B04_WVB","空调机组NJ-4AP(KT)2-4-水阀反馈",30111]
[null,{"$f":"B98","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B98&\"地址: \"&B95&\" *)\"","v":"(* IOM 0801U地址: 14 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH94&AA94&\"-\"&AK94","v":"空调机组NJ-4AP(KT)2-5-回风温度"},{"$nulls":16},{"$f":"IF(AI94=\"\",\"\",AI94)","v":"NJ-4AP(KT)2-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-5","04B05","回风温度",{"$f":"AH94&\"-\"&AK94","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH94,List!$B$3:$D$445,2,FALSE)&AJ94&\"_\"&VLOOKUP(AK94,List!$K$2:$M$447,2,FALSE)","v":"AHU04B05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM94&\" \"&\"AT%I\"&B95*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J94&\"*)\",\" \")","v":"LAHU04B05_RT AT%I224.0 :INT ; (*空调机组NJ-4AP(KT)2-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94))),SEARCH(\":\",REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94)))))),\" \")","v":"LAHU04B05_RT            AT%I224.0      :INT ; (*空调机组NJ-4AP(KT)2-5-回风温度*)"},null,{"$f":"AM94","v":"AHU04B05_RT"},{"$f":"J94","v":"空调机组NJ-4AP(KT)2-5-回风温度"},{"$f":"30000+($B95*8+F94-1)","v":30112}]
[null,14,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-4AP(KT)2-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-4AP(KT)2-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-5","04B05","水阀反馈",{"$f":"AH95&\"-\"&AK95","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"AHU04B05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%I\"&B95*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LAHU04B05_WVB AT%I226.0 :INT ; (*空调机组NJ-4AP(KT)2-5-水阀反馈*)"},"LAHU04B05_WVB           AT%I226.0      :INT ; (*空调机组NJ-4AP(KT)2-5-水阀反馈*)",null,"AHU04B05_WVB",{"$f":"J95","v":"空调机组NJ-4AP(KT)2-5-水阀反馈"},{"$f":"AS94+1","v":30113}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-4AP(KT)2-6-回风温度",{"$nulls":16},"NJ-4AP(KT)2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-6","04B06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"AHU04B06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%I\"&B95*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LAHU04B06_RT AT%I228.0 :INT ; (*空调机组NJ-4AP(KT)2-6-回风温度*)"},"LAHU04B06_RT            AT%I228.0      :INT ; (*空调机组NJ-4AP(KT)2-6-回风温度*)",null,"AHU04B06_RT","空调机组NJ-4AP(KT)2-6-回风温度",{"$f":"AS95+1","v":30114}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-4AP(KT)2-6-水阀反馈",{"$nulls":16},"NJ-4AP(KT)2-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-6","04B06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":"AHU04B06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%I\"&B95*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":"LAHU04B06_WVB AT%I230.0 :INT ; (*空调机组NJ-4AP(KT)2-6-水阀反馈*)"},"LAHU04B06_WVB           AT%I230.0      :INT ; (*空调机组NJ-4AP(KT)2-6-水阀反馈*)",null,"AHU04B06_WVB","空调机组NJ-4AP(KT)2-6-水阀反馈",30115]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-4AP(KT)2-7-回风温度",{"$nulls":16},"NJ-4AP(KT)2-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-7","04B07","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":"AHU04B07_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%I\"&B95*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":"LAHU04B07_RT AT%I232.0 :INT ; (*空调机组NJ-4AP(KT)2-7-回风温度*)"},"LAHU04B07_RT            AT%I232.0      :INT ; (*空调机组NJ-4AP(KT)2-7-回风温度*)",null,"AHU04B07_RT","空调机组NJ-4AP(KT)2-7-回风温度",30116]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-4AP(KT)2-7-水阀反馈",{"$nulls":16},"NJ-4AP(KT)2-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-7","04B07","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH99,List!$B$3:$D$445,2,FALSE)&AJ99&\"_\"&VLOOKUP(AK99,List!$K$2:$M$447,2,FALSE)","v":"AHU04B07_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM99&\" \"&\"AT%I\"&B95*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J99&\"*)\",\" \")","v":"LAHU04B07_WVB AT%I234.0 :INT ; (*空调机组NJ-4AP(KT)2-7-水阀反馈*)"},"LAHU04B07_WVB           AT%I234.0      :INT ; (*空调机组NJ-4AP(KT)2-7-水阀反馈*)",null,"AHU04B07_WVB",{"$f":"J99","v":"空调机组NJ-4AP(KT)2-7-水阀反馈"},30117]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH100,List!$B$3:$D$445,2,FALSE)&AJ100&\"_\"&VLOOKUP(AK100,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM100&\" \"&\"AT%I\"&B95*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J100&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30118]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},{"$f":"IF(AI101=\"\",\"\",AI101)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH101,List!$B$3:$D$445,2,FALSE)&AJ101&\"_\"&VLOOKUP(AK101,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM101&\" \"&\"AT%I\"&B95*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J101&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30119]
[null,{"$f":"B107","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B107&\"地址: \"&B104&\" *)\"","v":"(* IOM 0401U地址: 15 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH103&AA103&\"-\"&AK103","v":"室内环境状态T-03-温度状态"},{"$nulls":16},{"$f":"IF(AI103=\"\",\"\",AI103)","v":"T-03"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","T-03","04B01","温度状态",{"$f":"AH103&\"-\"&AK103","v":"室内环境状态-温度状态"},{"$f":"VLOOKUP(AH103,List!$B$3:$D$445,2,FALSE)&AJ103&\"_\"&VLOOKUP(AK103,List!$K$2:$M$447,2,FALSE)","v":"IES04B01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM103&\" \"&\"AT%I\"&B104*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J103&\"*)\",\" \")","v":"LIES04B01_T AT%I240.0 :INT ; (*室内环境状态T-03-温度状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103))),SEARCH(\":\",REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103)))))),\" \")","v":"LIES04B01_T             AT%I240.0      :INT ; (*室内环境状态T-03-温度状态*)"},null,{"$f":"AM103","v":"IES04B01_T"},{"$f":"J103","v":"室内环境状态T-03-温度状态"},{"$f":"30000+($B104*8+F103-1)","v":30120}]
[null,15,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),4,1))","v":1},2,null,2,"0V","风机盘管-温度状态",{"$nulls":16},{"$f":"IF(AI104=\"\",\"\",AI104)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管",null,"04B01","温度状态",{"$f":"AH104&\"-\"&AK104","v":"风机盘管-温度状态"},{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"FCU04B01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%I\"&B104*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LFCU04B01_T AT%I242.0 :INT ; (*风机盘管-温度状态*)"},"LFCU04B01_T             AT%I242.0      :INT ; (*风机盘管-温度状态*)",null,"FCU04B01_T",{"$f":"J104","v":"风机盘管-温度状态"},{"$f":"AS103+1","v":30121}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),3,1))","v":1},3,null,3,"0V","室内环境状态CO2-02-二氧化碳浓度状态",{"$nulls":16},"CO2-02",{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","CO2-02","04B01","二氧化碳浓度状态","室内环境状态-二氧化碳浓度状态",{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"IES04B01_CO2"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%I\"&B104*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LIES04B01_CO2 AT%I244.0 :INT ; (*室内环境状态CO2-02-二氧化碳浓度状态*)"},"LIES04B01_CO2           AT%I244.0      :INT ; (*室内环境状态CO2-02-二氧化碳浓度状态*)",null,"IES04B01_CO2","室内环境状态CO2-02-二氧化碳浓度状态",{"$f":"AS104+1","v":30122}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),2,1))","v":1},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%I\"&B104*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30123]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),1,1))","v":0}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B116","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B116&\"地址: \"&B113&\" *)\"","v":"(* IOM 0401A地址: 16 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH112&AA112&\"-\"&AK112","v":"空调机组NJ-4AP(KT)2-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI112=\"\",\"\",AI112)","v":"NJ-4AP(KT)2-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-1","04B01","水阀控制",{"$f":"AH112&\"-\"&AK112","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH112,List!$B$3:$D$445,2,FALSE)&AJ112&\"_\"&VLOOKUP(AK112,List!$K$2:$M$447,2,FALSE)","v":"AHU04B01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM112&\" \"&\"AT%Q\"&B113*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J112&\"*)\",\" \")","v":"LAHU04B01_WVC AT%Q256.0 :INT ; (*空调机组NJ-4AP(KT)2-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112))),SEARCH(\":\",REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112)))))),\" \")","v":"LAHU04B01_WVC           AT%Q256.0      :INT ; (*空调机组NJ-4AP(KT)2-1-水阀控制*)"},null,{"$f":"AM112","v":"AHU04B01_WVC"},{"$f":"J112","v":"空调机组NJ-4AP(KT)2-1-水阀控制"},{"$f":"40000+($B113*8+F112-1)","v":40128}]
[null,16,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH113&AA113&\"-\"&AK113","v":"空调机组NJ-4AP(KT)2-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI113=\"\",\"\",AI113)","v":"NJ-4AP(KT)2-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-2","04B02","水阀控制",{"$f":"AH113&\"-\"&AK113","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH113,List!$B$3:$D$445,2,FALSE)&AJ113&\"_\"&VLOOKUP(AK113,List!$K$2:$M$447,2,FALSE)","v":"AHU04B02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM113&\" \"&\"AT%Q\"&B113*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J113&\"*)\",\" \")","v":"LAHU04B02_WVC AT%Q258.0 :INT ; (*空调机组NJ-4AP(KT)2-2-水阀控制*)"},"LAHU04B02_WVC           AT%Q258.0      :INT ; (*空调机组NJ-4AP(KT)2-2-水阀控制*)",null,"AHU04B02_WVC",{"$f":"J113","v":"空调机组NJ-4AP(KT)2-2-水阀控制"},{"$f":"AS112+1","v":40129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH114&AA114&\"-\"&AK114","v":"空调机组NJ-4AP(KT)2-3-水阀控制"},{"$nulls":16},"NJ-4AP(KT)2-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-3","04B03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH114,List!$B$3:$D$445,2,FALSE)&AJ114&\"_\"&VLOOKUP(AK114,List!$K$2:$M$447,2,FALSE)","v":"AHU04B03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM114&\" \"&\"AT%Q\"&B113*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J114&\"*)\",\" \")","v":"LAHU04B03_WVC AT%Q260.0 :INT ; (*空调机组NJ-4AP(KT)2-3-水阀控制*)"},"LAHU04B03_WVC           AT%Q260.0      :INT ; (*空调机组NJ-4AP(KT)2-3-水阀控制*)",null,"AHU04B03_WVC","空调机组NJ-4AP(KT)2-3-水阀控制",{"$f":"AS113+1","v":40130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH115&AA115&\"-\"&AK115","v":"空调机组NJ-4AP(KT)2-4-水阀控制"},{"$nulls":16},"NJ-4AP(KT)2-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-4","04B04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH115,List!$B$3:$D$445,2,FALSE)&AJ115&\"_\"&VLOOKUP(AK115,List!$K$2:$M$447,2,FALSE)","v":"AHU04B04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM115&\" \"&\"AT%Q\"&B113*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J115&\"*)\",\" \")","v":"LAHU04B04_WVC AT%Q262.0 :INT ; (*空调机组NJ-4AP(KT)2-4-水阀控制*)"},"LAHU04B04_WVC           AT%Q262.0      :INT ; (*空调机组NJ-4AP(KT)2-4-水阀控制*)",null,"AHU04B04_WVC","空调机组NJ-4AP(KT)2-4-水阀控制",40131]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B50","v":0},{"$nulls":38},{"$f":"\"(* \"&B125&\"地址: \"&B122&\" *)\"","v":"(* IOM 0401A地址: 17 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH121&AA121&\"-\"&AK121","v":"空调机组NJ-4AP(KT)2-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI121=\"\",\"\",AI121)","v":"NJ-4AP(KT)2-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-5","04B05","水阀控制",{"$f":"AH121&\"-\"&AK121","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH121,List!$B$3:$D$445,2,FALSE)&AJ121&\"_\"&VLOOKUP(AK121,List!$K$2:$M$447,2,FALSE)","v":"AHU04B05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM121&\" \"&\"AT%Q\"&B122*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J121&\"*)\",\" \")","v":"LAHU04B05_WVC AT%Q272.0 :INT ; (*空调机组NJ-4AP(KT)2-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121))),SEARCH(\":\",REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121)))))),\" \")","v":"LAHU04B05_WVC           AT%Q272.0      :INT ; (*空调机组NJ-4AP(KT)2-5-水阀控制*)"},null,{"$f":"AM121","v":"AHU04B05_WVC"},{"$f":"J121","v":"空调机组NJ-4AP(KT)2-5-水阀控制"},{"$f":"40000+($B122*8+F121-1)","v":40136}]
[null,17,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH122&AA122&\"-\"&AK122","v":"空调机组NJ-4AP(KT)2-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI122=\"\",\"\",AI122)","v":"NJ-4AP(KT)2-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-6","04B06","水阀控制",{"$f":"AH122&\"-\"&AK122","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH122,List!$B$3:$D$445,2,FALSE)&AJ122&\"_\"&VLOOKUP(AK122,List!$K$2:$M$447,2,FALSE)","v":"AHU04B06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM122&\" \"&\"AT%Q\"&B122*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J122&\"*)\",\" \")","v":"LAHU04B06_WVC AT%Q274.0 :INT ; (*空调机组NJ-4AP(KT)2-6-水阀控制*)"},"LAHU04B06_WVC           AT%Q274.0      :INT ; (*空调机组NJ-4AP(KT)2-6-水阀控制*)",null,"AHU04B06_WVC",{"$f":"J122","v":"空调机组NJ-4AP(KT)2-6-水阀控制"},{"$f":"AS121+1","v":40137}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH123&AA123&\"-\"&AK123","v":"空调机组NJ-4AP(KT)2-7-水阀控制"},{"$nulls":16},"NJ-4AP(KT)2-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)2-7","04B07","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH123,List!$B$3:$D$445,2,FALSE)&AJ123&\"_\"&VLOOKUP(AK123,List!$K$2:$M$447,2,FALSE)","v":"AHU04B07_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM123&\" \"&\"AT%Q\"&B122*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J123&\"*)\",\" \")","v":"LAHU04B07_WVC AT%Q276.0 :INT ; (*空调机组NJ-4AP(KT)2-7-水阀控制*)"},"LAHU04B07_WVC           AT%Q276.0      :INT ; (*空调机组NJ-4AP(KT)2-7-水阀控制*)",null,"AHU04B07_WVC","空调机组NJ-4AP(KT)2-7-水阀控制",{"$f":"AS122+1","v":40138}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH124&AA124&\"-\"&AK124","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH124,List!$B$3:$D$445,2,FALSE)&AJ124&\"_\"&VLOOKUP(AK124,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM124&\" \"&\"AT%Q\"&B122*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J124&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40139]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L509","index":26,"n_rows":42,"n_cols":45,"rows_kept":42,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[41,5,41,6],[41,9,41,25],[4,1,5,1],[11,1,14,1],[20,1,23,1],[29,1,32,1],[38,1,41,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L01",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.0801R D7",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 0801R地址: 18 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH8&AA8&\"-\"&AK8","v":"F新风机组NJ-5AP(KT)2-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-5AP(KT)2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)2","05I01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"F新风机组-运行状态"},{"$f":"VLOOKUP(AH8,[1]List!$D$3:$F$527,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05I01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LFAU05I01_R AT%I288.0 :BOOL; (*F新风机组NJ-5AP(KT)2-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LFAU05I01_R             AT%I288.0      :BOOL; (*F新风机组NJ-5AP(KT)2-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L01\\L01FAU05I01_R"},{"$f":"J8","v":"F新风机组NJ-5AP(KT)2-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":12304}]
[null,18,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},2,null,2,"C","F新风机组NJ-5AP(KT)2-故障状态",{"$nulls":16},"NJ-5AP(KT)2",{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)2","05I01","故障状态","F新风机组-故障状态",{"$f":"VLOOKUP(AH9,[1]List!$D$3:$F$527,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05I01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LFAU05I01_F AT%I288.1 :BOOL; (*F新风机组NJ-5AP(KT)2-故障状态*)"},"LFAU05I01_F             AT%I288.1      :BOOL; (*F新风机组NJ-5AP(KT)2-故障状态*)",null,"L01\\L01FAU05I01_F","F新风机组NJ-5AP(KT)2-故障状态",{"$f":"AS8+1","v":12305}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},3,null,3,"C","F新风机组NJ-5AP(KT)2-自动状态",{"$nulls":16},"NJ-5AP(KT)2",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)2","05I01","自动状态","F新风机组-自动状态",{"$f":"VLOOKUP(AH10,[1]List!$D$3:$F$527,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05I01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LFAU05I01_A AT%I288.2 :BOOL; (*F新风机组NJ-5AP(KT)2-自动状态*)"},"LFAU05I01_A             AT%I288.2      :BOOL; (*F新风机组NJ-5AP(KT)2-自动状态*)",null,"L01\\L01FAU05I01_A","F新风机组NJ-5AP(KT)2-自动状态",12306]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},4,null,4,"C","F新风机组NJ-5AP(KT)2-风机压差",{"$nulls":16},"NJ-5AP(KT)2",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)2","05I01","风机压差","F新风机组-风机压差",{"$f":"VLOOKUP(AH11,[1]List!$D$3:$F$527,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05I01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LFAU05I01_FPS AT%I288.3 :BOOL; (*F新风机组NJ-5AP(KT)2-风机压差*)"},"LFAU05I01_FPS           AT%I288.3      :BOOL; (*F新风机组NJ-5AP(KT)2-风机压差*)",null,"L01\\L01FAU05I01_FPS","F新风机组NJ-5AP(KT)2-风机压差",12307]
[null,"IOM 0801R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},5,null,5,"C","F新风机组NJ-5AP(KT)2-初效滤网压差",{"$nulls":16},"NJ-5AP(KT)2",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)2","05I01","初效滤网压差","F新风机组-初效滤网压差",{"$f":"VLOOKUP(AH12,[1]List!$D$3:$F$527,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05I01_IPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LFAU05I01_IPS AT%I288.4 :BOOL; (*F新风机组NJ-5AP(KT)2-初效滤网压差*)"},"LFAU05I01_IPS           AT%I288.4      :BOOL; (*F新风机组NJ-5AP(KT)2-初效滤网压差*)",null,"L01\\L01FAU05I01_IPS","F新风机组NJ-5AP(KT)2-初效滤网压差",12308]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","F新风机组NJ-5AP(KT)2-低温断路开关",{"$nulls":16},"NJ-5AP(KT)2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)2","05I01","低温断路开关","F新风机组-低温断路开关",{"$f":"VLOOKUP(AH13,[1]List!$D$3:$F$527,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05I01_AFS"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LFAU05I01_AFS AT%I288.5 :BOOL; (*F新风机组NJ-5AP(KT)2-低温断路开关*)"},"LFAU05I01_AFS           AT%I288.5      :BOOL; (*F新风机组NJ-5AP(KT)2-低温断路开关*)",null,"L01\\L01FAU05I01_AFS","F新风机组NJ-5AP(KT)2-低温断路开关",12309]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","F新风机组NJ-5AP(KT)2-新风阀开状态",{"$nulls":16},"NJ-5AP(KT)2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)2","05I01","新风阀开状态","F新风机组-新风阀开状态",{"$f":"VLOOKUP(AH14,[1]List!$D$3:$F$527,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05I01_FDOB"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LFAU05I01_FDOB AT%I288.6 :BOOL; (*F新风机组NJ-5AP(KT)2-新风阀开状态*)"},"LFAU05I01_FDOB          AT%I288.6      :BOOL; (*F新风机组NJ-5AP(KT)2-新风阀开状态*)",null,"L01\\L01FAU05I01_FDOB","F新风机组NJ-5AP(KT)2-新风阀开状态",12310]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","F新风机组NJ-5AP(KT)2-新风阀关状态",{"$nulls":16},"NJ-5AP(KT)2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)2","05I01","新风阀关状态","F新风机组-新风阀关状态",{"$f":"VLOOKUP(AH15,[1]List!$D$3:$F$527,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05I01_FDSB"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LFAU05I01_FDSB AT%I288.7 :BOOL; (*F新风机组NJ-5AP(KT)2-新风阀关状态*)"},"LFAU05I01_FDSB          AT%I288.7      :BOOL; (*F新风机组NJ-5AP(KT)2-新风阀关状态*)",null,"L01\\L01FAU05I01_FDSB","F新风机组NJ-5AP(KT)2-新风阀关状态",12311]
[null,{"$f":"B21","v":"IOM 0801D"},{"$nulls":38},{"$f":"\"(* \"&B21&\"地址: \"&B18&\" *)\"","v":"(* IOM 0801D地址: 19 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH17&AA17&\"-\"&AK17","v":"F新风机组NJ-5AP(KT)2-启停控制"},{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-5AP(KT)2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)2","05I01","启停控制",{"$f":"AH17&\"-\"&AK17","v":"F新风机组-启停控制"},{"$f":"VLOOKUP(AH17,[1]List!$D$3:$F$527,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05I01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%Q\"&B18*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LFAU05I01_C AT%Q304.0 :BOOL; (*F新风机组NJ-5AP(KT)2-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",25-SEARCH(\"AT%\",AN17))),SEARCH(\":\",REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",25-SEARCH(\"AT%\",AN17)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",25-SEARCH(\"AT%\",AN17)))))),\" \")","v":"LFAU05I01_C             AT%Q304.0      :BOOL; (*F新风机组NJ-5AP(KT)2-启停控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM17","v":"L01\\L01FAU05I01_C"},{"$f":"J17","v":"F新风机组NJ-5AP(KT)2-启停控制"},{"$f":"($B18*16*8+F17-1)","v":2432}]
[null,19,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","F新风机组NJ-5AP(KT)2-新风阀开控制",{"$nulls":16},"NJ-5AP(KT)2",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)2","05I01","新风阀开控制","F新风机组-新风阀开控制",{"$f":"VLOOKUP(AH18,[1]List!$D$3:$F$527,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05I01_FDOC"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%Q\"&B18*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LFAU05I01_FDOC AT%Q304.1 :BOOL; (*F新风机组NJ-5AP(KT)2-新风阀开控制*)"},"LFAU05I01_FDOC          AT%Q304.1      :BOOL; (*F新风机组NJ-5AP(KT)2-新风阀开控制*)",null,"L01\\L01FAU05I01_FDOC","F新风机组NJ-5AP(KT)2-新风阀开控制",{"$f":"AS17+1","v":2433}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","F新风机组NJ-5AP(KT)2-新风阀关控制",{"$nulls":16},"NJ-5AP(KT)2",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)2","05I01","新风阀关控制","F新风机组-新风阀关控制",{"$f":"VLOOKUP(AH19,[1]List!$D$3:$F$527,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05I01_FDSC"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%Q\"&B18*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LFAU05I01_FDSC AT%Q304.2 :BOOL; (*F新风机组NJ-5AP(KT)2-新风阀关控制*)"},"LFAU05I01_FDSC          AT%Q304.2      :BOOL; (*F新风机组NJ-5AP(KT)2-新风阀关控制*)",null,"L01\\L01FAU05I01_FDSC","F新风机组NJ-5AP(KT)2-新风阀关控制",2434]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH20,[1]List!$D$3:$F$527,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%Q\"&B18*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN20,SEARCH(\"AT%\",AN20),,REPT(\" \",30-SEARCH(\"AT%\",AN20))),SEARCH(\":\",REPLACE(AN20,SEARCH(\"AT%\",AN20),,REPT(\" \",30-SEARCH(\"AT%\",AN20)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN20,SEARCH(\"AT%\",AN20),,REPT(\" \",25-SEARCH(\"AT%\",AN20)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",2435]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),1,1))","v":1},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH21,[1]List!$D$3:$F$527,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%Q\"&B18*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2436]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH22,[1]List!$D$3:$F$527,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%Q\"&B18*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2437]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH23,[1]List!$D$3:$F$527,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%Q\"&B18*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2438]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH24,[1]List!$D$3:$F$527,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%Q\"&B18*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2439]
[null,{"$f":"B30","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 0401U地址: 20 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH26&AA26&\"-\"&AK26","v":"F新风机组NJ-5AP(KT)2-送风温度"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-5AP(KT)2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)2","05I01","送风温度",{"$f":"AH26&\"-\"&AK26","v":"F新风机组-送风温度"},{"$f":"VLOOKUP(AH26,[1]List!$D$3:$F$527,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05I01_ST"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LFAU05I01_ST AT%I320.0 :INT; (*F新风机组NJ-5AP(KT)2-送风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LFAU05I01_ST            AT%I320.0      :INT; (*F新风机组NJ-5AP(KT)2-送风温度*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L01\\L01FAU05I01_ST"},{"$f":"J26","v":"F新风机组NJ-5AP(KT)2-送风温度"},{"$f":"30000+($B27*8+F26-1)","v":30160}]
[null,20,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,2,"0V","F新风机组NJ-5AP(KT)2-水阀反馈",{"$nulls":16},"NJ-5AP(KT)2",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)2","05I01","水阀反馈","F新风机组-水阀反馈",{"$f":"VLOOKUP(AH27,[1]List!$D$3:$F$527,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05I01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LFAU05I01_WVB AT%I322.0 :INT; (*F新风机组NJ-5AP(KT)2-水阀反馈*)"},"LFAU05I01_WVB           AT%I322.0      :INT; (*F新风机组NJ-5AP(KT)2-水阀反馈*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM27","v":"L01\\L01FAU05I01_WVB"},"F新风机组NJ-5AP(KT)2-水阀反馈",{"$f":"AS26+1","v":30161}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":1},3,null,3,"0V","F新风机组NJ-5AP(KT)2-变频器频率反馈",{"$nulls":16},"NJ-5AP(KT)2",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)2","05I01","变频器频率反馈","F新风机组-变频器频率反馈",{"$f":"VLOOKUP(AH28,[1]List!$D$3:$F$527,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05I01_VFB"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LFAU05I01_VFB AT%I324.0 :INT; (*F新风机组NJ-5AP(KT)2-变频器频率反馈*)"},"LFAU05I01_VFB           AT%I324.0      :INT; (*F新风机组NJ-5AP(KT)2-变频器频率反馈*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM28","v":"L01\\L01FAU05I01_VFB"},"F新风机组NJ-5AP(KT)2-变频器频率反馈",30162]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH29,[1]List!$D$3:$F$527,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN29,SEARCH(\"AT%\",AN29),,REPT(\" \",30-SEARCH(\"AT%\",AN29))),SEARCH(\":\",REPLACE(AN29,SEARCH(\"AT%\",AN29),,REPT(\" \",30-SEARCH(\"AT%\",AN29)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN29,SEARCH(\"AT%\",AN29),,REPT(\" \",25-SEARCH(\"AT%\",AN29)))))),\" \")","v":" "},null,{"$f":"$B$2&\"\\\"&$B$2&AM29","v":{"$error":"#N/A"}},"-",30163]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":1}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B39","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B39&\"地址: \"&B36&\" *)\"","v":"(* IOM 0401A地址: 21 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH35&AA35&\"-\"&AK35","v":"F新风机组NJ-5AP(KT)2-水阀控制"},{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-5AP(KT)2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)2","05I01","水阀控制",{"$f":"AH35&\"-\"&AK35","v":"F新风机组-水阀控制"},{"$f":"VLOOKUP(AH35,[1]List!$D$3:$F$527,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05I01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%Q\"&B36*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LFAU05I01_WVC AT%Q336.0 :INT; (*F新风机组NJ-5AP(KT)2-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35))),SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35)))))),\" \")","v":"LFAU05I01_WVC           AT%Q336.0      :INT; (*F新风机组NJ-5AP(KT)2-水阀控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM35","v":"L01\\L01FAU05I01_WVC"},{"$f":"J35","v":"F新风机组NJ-5AP(KT)2-水阀控制"},{"$f":"40000+($B36*8+F35-1)","v":40168}]
[null,21,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":0},2,null,3,4,"F新风机组NJ-5AP(KT)2-变频器频率控制",{"$nulls":16},"NJ-5AP(KT)2",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)2","05I01","变频器频率控制","F新风机组-变频器频率控制",{"$f":"VLOOKUP(AH36,[1]List!$D$3:$F$527,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05I01_VFC"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%Q\"&B36*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LFAU05I01_VFC AT%Q338.0 :INT; (*F新风机组NJ-5AP(KT)2-变频器频率控制*)"},"LFAU05I01_VFC           AT%Q338.0      :INT; (*F新风机组NJ-5AP(KT)2-变频器频率控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM36","v":"L01\\L01FAU05I01_VFC"},"F新风机组NJ-5AP(KT)2-变频器频率控制",{"$f":"AS35+1","v":40169}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":1},3,null,5,6,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH37,[1]List!$D$3:$F$527,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%Q\"&B36*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN37,SEARCH(\"AT%\",AN37),,REPT(\" \",30-SEARCH(\"AT%\",AN37))),SEARCH(\":\",REPLACE(AN37,SEARCH(\"AT%\",AN37),,REPT(\" \",30-SEARCH(\"AT%\",AN37)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN37,SEARCH(\"AT%\",AN37),,REPT(\" \",25-SEARCH(\"AT%\",AN37)))))),\" \")","v":" "},null,{"$f":"$B$2&\"\\\"&$B$2&AM37","v":{"$error":"#N/A"}},"-",40170]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":0},4,null,7,8,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH38,[1]List!$D$3:$F$527,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%Q\"&B36*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM38","v":{"$error":"#N/A"}},"-",40171]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L303","index":27,"n_rows":129,"n_cols":45,"rows_kept":129,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[6,1,6,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[75,5,75,6],[75,9,75,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[92,5,92,6],[92,9,92,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[101,5,101,6],[101,9,101,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[109,5,109,6],[109,9,109,25],[110,5,110,6],[110,9,110,25],[112,5,112,6],[112,9,112,25],[113,5,113,6],[113,9,113,25],[114,5,114,6],[114,9,114,25],[115,5,115,6],[115,9,115,25],[116,5,116,6],[116,9,116,25],[117,5,117,6],[117,9,117,25],[118,5,118,6],[118,9,118,25],[119,5,119,6],[119,9,119,25],[121,5,121,6],[121,9,121,25],[122,5,122,6],[122,9,122,25],[123,5,123,6],[123,9,123,25],[124,5,124,6],[124,9,124,25],[125,5,125,6],[125,9,125,25],[126,5,126,6],[126,9,126,25],[127,5,127,6],[127,9,127,25],[128,5,128,6],[128,9,128,25],[4,1,5,1],[12,1,23,1],[29,1,40,1],[46,1,57,1],[63,1,66,1],[72,1,83,1],[89,1,92,1],[98,1,101,1],[107,1,110,1],[116,1,119,1],[125,1,128,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[16,2,23,4],[33,2,40,4],[50,2,57,4],[76,2,83,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L21",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"EXC-1000"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B13&\"地址: \"&B10&\" *)\"","v":"(* IOM 1601R地址: 0 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH9&AA9&\"-\"&AK9","v":"空调机组NJ-3AP(KT)3-1-运行状态"},{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-3AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-1","03C01","运行状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU03C01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B10*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU03C01_R AT%I0.0 :BOOL; (*空调机组NJ-3AP(KT)3-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9))),SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))))),\" \")","v":"LAHU03C01_R             AT%I0.0        :BOOL; (*空调机组NJ-3AP(KT)3-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM9","v":"L21\\L21AHU03C01_R"},{"$f":"J9","v":"空调机组NJ-3AP(KT)3-1-运行状态"},{"$f":"10000+($B10*16*8+F9-1)","v":10000}]
[null,0,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-3AP(KT)3-1-故障状态",{"$nulls":16},{"$f":"IF(AI10=\"\",\"\",AI10)","v":"NJ-3AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-1","03C01","故障状态",{"$f":"AH10&\"-\"&AK10","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU03C01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B10*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU03C01_F AT%I0.1 :BOOL; (*空调机组NJ-3AP(KT)3-1-故障状态*)"},"LAHU03C01_F             AT%I0.1        :BOOL; (*空调机组NJ-3AP(KT)3-1-故障状态*)",null,"L21\\L21AHU03C01_F",{"$f":"J10","v":"空调机组NJ-3AP(KT)3-1-故障状态"},{"$f":"AS9+1","v":10001}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)3-1-自动状态",{"$nulls":16},"NJ-3AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-1","03C01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU03C01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B10*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU03C01_A AT%I0.2 :BOOL; (*空调机组NJ-3AP(KT)3-1-自动状态*)"},"LAHU03C01_A             AT%I0.2        :BOOL; (*空调机组NJ-3AP(KT)3-1-自动状态*)",null,"L21\\L21AHU03C01_A","空调机组NJ-3AP(KT)3-1-自动状态",{"$f":"AS10+1","v":10002}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)3-1-风机压差",{"$nulls":16},"NJ-3AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-1","03C01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU03C01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B10*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU03C01_FPS AT%I0.3 :BOOL; (*空调机组NJ-3AP(KT)3-1-风机压差*)"},"LAHU03C01_FPS           AT%I0.3        :BOOL; (*空调机组NJ-3AP(KT)3-1-风机压差*)",null,"L21\\L21AHU03C01_FPS","空调机组NJ-3AP(KT)3-1-风机压差",10003]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)3-2-运行状态",{"$nulls":16},"NJ-3AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-2","03C02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU03C02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B10*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU03C02_R AT%I0.4 :BOOL; (*空调机组NJ-3AP(KT)3-2-运行状态*)"},"LAHU03C02_R             AT%I0.4        :BOOL; (*空调机组NJ-3AP(KT)3-2-运行状态*)",null,"L21\\L21AHU03C02_R","空调机组NJ-3AP(KT)3-2-运行状态",10004]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)3-2-故障状态",{"$nulls":16},"NJ-3AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-2","03C02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU03C02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B10*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU03C02_F AT%I0.5 :BOOL; (*空调机组NJ-3AP(KT)3-2-故障状态*)"},"LAHU03C02_F             AT%I0.5        :BOOL; (*空调机组NJ-3AP(KT)3-2-故障状态*)",null,"L21\\L21AHU03C02_F","空调机组NJ-3AP(KT)3-2-故障状态",10005]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)3-2-自动状态",{"$nulls":16},"NJ-3AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-2","03C02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU03C02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B10*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU03C02_A AT%I0.6 :BOOL; (*空调机组NJ-3AP(KT)3-2-自动状态*)"},"LAHU03C02_A             AT%I0.6        :BOOL; (*空调机组NJ-3AP(KT)3-2-自动状态*)",null,"L21\\L21AHU03C02_A","空调机组NJ-3AP(KT)3-2-自动状态",10006]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)3-2-风机压差",{"$nulls":16},"NJ-3AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-2","03C02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU03C02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B10*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU03C02_FPS AT%I0.7 :BOOL; (*空调机组NJ-3AP(KT)3-2-风机压差*)"},"LAHU03C02_FPS           AT%I0.7        :BOOL; (*空调机组NJ-3AP(KT)3-2-风机压差*)",null,"L21\\L21AHU03C02_FPS","空调机组NJ-3AP(KT)3-2-风机压差",10007]
[{"$nulls":5},9,null,17,18,"空调机组NJ-3AP(KT)3-3-运行状态",{"$nulls":16},"NJ-3AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-3","03C03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU03C03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B10*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU03C03_R AT%I1.0 :BOOL; (*空调机组NJ-3AP(KT)3-3-运行状态*)"},"LAHU03C03_R             AT%I1.0        :BOOL; (*空调机组NJ-3AP(KT)3-3-运行状态*)",null,"L21\\L21AHU03C03_R","空调机组NJ-3AP(KT)3-3-运行状态",10008]
[{"$nulls":5},10,null,19,20,"空调机组NJ-3AP(KT)3-3-故障状态",{"$nulls":16},{"$f":"IF(AI18=\"\",\"\",AI18)","v":"NJ-3AP(KT)3-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-3","03C03","故障状态",{"$f":"AH18&\"-\"&AK18","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU03C03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B10*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU03C03_F AT%I1.1 :BOOL; (*空调机组NJ-3AP(KT)3-3-故障状态*)"},"LAHU03C03_F             AT%I1.1        :BOOL; (*空调机组NJ-3AP(KT)3-3-故障状态*)",null,"L21\\L21AHU03C03_F","空调机组NJ-3AP(KT)3-3-故障状态",10009]
[{"$nulls":5},11,null,21,22,"空调机组NJ-3AP(KT)3-3-自动状态",{"$nulls":16},"NJ-3AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-3","03C03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU03C03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B10*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU03C03_A AT%I1.2 :BOOL; (*空调机组NJ-3AP(KT)3-3-自动状态*)"},"LAHU03C03_A             AT%I1.2        :BOOL; (*空调机组NJ-3AP(KT)3-3-自动状态*)",null,"L21\\L21AHU03C03_A","空调机组NJ-3AP(KT)3-3-自动状态",10010]
[{"$nulls":5},12,null,23,24,"空调机组NJ-3AP(KT)3-3-风机压差",{"$nulls":16},"NJ-3AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-3","03C03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU03C03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B10*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU03C03_FPS AT%I1.3 :BOOL; (*空调机组NJ-3AP(KT)3-3-风机压差*)"},"LAHU03C03_FPS           AT%I1.3        :BOOL; (*空调机组NJ-3AP(KT)3-3-风机压差*)",null,"L21\\L21AHU03C03_FPS","空调机组NJ-3AP(KT)3-3-风机压差",10011]
[{"$nulls":5},13,null,25,26,"空调机组NJ-3AP(KT)3-4-运行状态",{"$nulls":16},"NJ-3AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-4","03C04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU03C04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B10*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU03C04_R AT%I1.4 :BOOL; (*空调机组NJ-3AP(KT)3-4-运行状态*)"},"LAHU03C04_R             AT%I1.4        :BOOL; (*空调机组NJ-3AP(KT)3-4-运行状态*)",null,"L21\\L21AHU03C04_R","空调机组NJ-3AP(KT)3-4-运行状态",10012]
[{"$nulls":5},14,null,27,28,"空调机组NJ-3AP(KT)3-4-故障状态",{"$nulls":16},"NJ-3AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-4","03C04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU03C04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B10*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU03C04_F AT%I1.5 :BOOL; (*空调机组NJ-3AP(KT)3-4-故障状态*)"},"LAHU03C04_F             AT%I1.5        :BOOL; (*空调机组NJ-3AP(KT)3-4-故障状态*)",null,"L21\\L21AHU03C04_F","空调机组NJ-3AP(KT)3-4-故障状态",10013]
[{"$nulls":5},15,null,29,30,"空调机组NJ-3AP(KT)3-4-自动状态",{"$nulls":16},"NJ-3AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-4","03C04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU03C04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B10*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU03C04_A AT%I1.6 :BOOL; (*空调机组NJ-3AP(KT)3-4-自动状态*)"},"LAHU03C04_A             AT%I1.6        :BOOL; (*空调机组NJ-3AP(KT)3-4-自动状态*)",null,"L21\\L21AHU03C04_A","空调机组NJ-3AP(KT)3-4-自动状态",10014]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-3AP(KT)3-4-风机压差",{"$nulls":16},"NJ-3AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-4","03C04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH24,List!$B$3:$D$445,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,List!$K$2:$M$447,2,FALSE)","v":"AHU03C04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%I\"&B10*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":"LAHU03C04_FPS AT%I1.7 :BOOL; (*空调机组NJ-3AP(KT)3-4-风机压差*)"},"LAHU03C04_FPS           AT%I1.7        :BOOL; (*空调机组NJ-3AP(KT)3-4-风机压差*)",null,"L21\\L21AHU03C04_FPS","空调机组NJ-3AP(KT)3-4-风机压差",10015]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 1601R地址: 1 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH26&AA26&\"-\"&AK26","v":"空调机组NJ-3AP(KT)3-5-运行状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-3AP(KT)3-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-5","03C05","运行状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU03C05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU03C05_R AT%I16.0 :BOOL; (*空调机组NJ-3AP(KT)3-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LAHU03C05_R             AT%I16.0       :BOOL; (*空调机组NJ-3AP(KT)3-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L21\\L21AHU03C05_R"},{"$f":"J26","v":"空调机组NJ-3AP(KT)3-5-运行状态"},{"$f":"10000+($B27*16*8+F26-1)","v":10128}]
[null,1,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-3AP(KT)3-5-故障状态",{"$nulls":16},{"$f":"IF(AI27=\"\",\"\",AI27)","v":"NJ-3AP(KT)3-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-5","03C05","故障状态",{"$f":"AH27&\"-\"&AK27","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU03C05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU03C05_F AT%I16.1 :BOOL; (*空调机组NJ-3AP(KT)3-5-故障状态*)"},"LAHU03C05_F             AT%I16.1       :BOOL; (*空调机组NJ-3AP(KT)3-5-故障状态*)",null,"L21\\L21AHU03C05_F",{"$f":"J27","v":"空调机组NJ-3AP(KT)3-5-故障状态"},{"$f":"AS26+1","v":10129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)3-5-自动状态",{"$nulls":16},"NJ-3AP(KT)3-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-5","03C05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU03C05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU03C05_A AT%I16.2 :BOOL; (*空调机组NJ-3AP(KT)3-5-自动状态*)"},"LAHU03C05_A             AT%I16.2       :BOOL; (*空调机组NJ-3AP(KT)3-5-自动状态*)",null,"L21\\L21AHU03C05_A","空调机组NJ-3AP(KT)3-5-自动状态",{"$f":"AS27+1","v":10130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)3-5-风机压差",{"$nulls":16},"NJ-3AP(KT)3-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-5","03C05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU03C05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU03C05_FPS AT%I16.3 :BOOL; (*空调机组NJ-3AP(KT)3-5-风机压差*)"},"LAHU03C05_FPS           AT%I16.3       :BOOL; (*空调机组NJ-3AP(KT)3-5-风机压差*)",null,"L21\\L21AHU03C05_FPS","空调机组NJ-3AP(KT)3-5-风机压差",10131]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)3-6-运行状态",{"$nulls":16},"NJ-3AP(KT)3-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-6","03C06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU03C06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B27*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU03C06_R AT%I16.4 :BOOL; (*空调机组NJ-3AP(KT)3-6-运行状态*)"},"LAHU03C06_R             AT%I16.4       :BOOL; (*空调机组NJ-3AP(KT)3-6-运行状态*)",null,"L21\\L21AHU03C06_R","空调机组NJ-3AP(KT)3-6-运行状态",10132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)3-6-故障状态",{"$nulls":16},"NJ-3AP(KT)3-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-6","03C06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU03C06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B27*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU03C06_F AT%I16.5 :BOOL; (*空调机组NJ-3AP(KT)3-6-故障状态*)"},"LAHU03C06_F             AT%I16.5       :BOOL; (*空调机组NJ-3AP(KT)3-6-故障状态*)",null,"L21\\L21AHU03C06_F","空调机组NJ-3AP(KT)3-6-故障状态",10133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)3-6-自动状态",{"$nulls":16},"NJ-3AP(KT)3-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-6","03C06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU03C06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B27*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU03C06_A AT%I16.6 :BOOL; (*空调机组NJ-3AP(KT)3-6-自动状态*)"},"LAHU03C06_A             AT%I16.6       :BOOL; (*空调机组NJ-3AP(KT)3-6-自动状态*)",null,"L21\\L21AHU03C06_A","空调机组NJ-3AP(KT)3-6-自动状态",10134]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)3-6-风机压差",{"$nulls":16},"NJ-3AP(KT)3-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-6","03C06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU03C06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B27*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU03C06_FPS AT%I16.7 :BOOL; (*空调机组NJ-3AP(KT)3-6-风机压差*)"},"LAHU03C06_FPS           AT%I16.7       :BOOL; (*空调机组NJ-3AP(KT)3-6-风机压差*)",null,"L21\\L21AHU03C06_FPS","空调机组NJ-3AP(KT)3-6-风机压差",10135]
[{"$nulls":5},9,null,17,18,"空调机组NJ-3AP(KT)3-7-运行状态",{"$nulls":16},"NJ-3AP(KT)3-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-7","03C07","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU03C07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B27*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU03C07_R AT%I17.0 :BOOL; (*空调机组NJ-3AP(KT)3-7-运行状态*)"},"LAHU03C07_R             AT%I17.0       :BOOL; (*空调机组NJ-3AP(KT)3-7-运行状态*)",null,"L21\\L21AHU03C07_R","空调机组NJ-3AP(KT)3-7-运行状态",10136]
[{"$nulls":5},10,null,19,20,"空调机组NJ-3AP(KT)3-7-故障状态",{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-3AP(KT)3-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-7","03C07","故障状态",{"$f":"AH35&\"-\"&AK35","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU03C07_F"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B27*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU03C07_F AT%I17.1 :BOOL; (*空调机组NJ-3AP(KT)3-7-故障状态*)"},"LAHU03C07_F             AT%I17.1       :BOOL; (*空调机组NJ-3AP(KT)3-7-故障状态*)",null,"L21\\L21AHU03C07_F",{"$f":"J35","v":"空调机组NJ-3AP(KT)3-7-故障状态"},10137]
[{"$nulls":5},11,null,21,22,"空调机组NJ-3AP(KT)3-7-自动状态",{"$nulls":16},"NJ-3AP(KT)3-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-7","03C07","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU03C07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B27*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU03C07_A AT%I17.2 :BOOL; (*空调机组NJ-3AP(KT)3-7-自动状态*)"},"LAHU03C07_A             AT%I17.2       :BOOL; (*空调机组NJ-3AP(KT)3-7-自动状态*)",null,"L21\\L21AHU03C07_A","空调机组NJ-3AP(KT)3-7-自动状态",10138]
[{"$nulls":5},12,null,23,24,"空调机组NJ-3AP(KT)3-7-风机压差",{"$nulls":16},"NJ-3AP(KT)3-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-7","03C07","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"AHU03C07_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B27*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LAHU03C07_FPS AT%I17.3 :BOOL; (*空调机组NJ-3AP(KT)3-7-风机压差*)"},"LAHU03C07_FPS           AT%I17.3       :BOOL; (*空调机组NJ-3AP(KT)3-7-风机压差*)",null,"L21\\L21AHU03C07_FPS","空调机组NJ-3AP(KT)3-7-风机压差",10139]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-3AL3-1-运行状态",{"$nulls":16},"NJ-3AL3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL3-1","03C01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB03C01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B27*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB03C01_R AT%I17.4 :BOOL; (*照明控制箱NJ-3AL3-1-运行状态*)"},"LLCB03C01_R             AT%I17.4       :BOOL; (*照明控制箱NJ-3AL3-1-运行状态*)",null,"L21\\L21LCB03C01_R","照明控制箱NJ-3AL3-1-运行状态",10140]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-3AL3-1-自动状态",{"$nulls":16},"NJ-3AL3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL3-1","03C01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB03C01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B27*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB03C01_A AT%I17.5 :BOOL; (*照明控制箱NJ-3AL3-1-自动状态*)"},"LLCB03C01_A             AT%I17.5       :BOOL; (*照明控制箱NJ-3AL3-1-自动状态*)",null,"L21\\L21LCB03C01_A","照明控制箱NJ-3AL3-1-自动状态",10141]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-3AL3-2-运行状态",{"$nulls":16},"NJ-3AL3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL3-2","03C02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"LCB03C02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B27*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LLCB03C02_R AT%I17.6 :BOOL; (*照明控制箱NJ-3AL3-2-运行状态*)"},"LLCB03C02_R             AT%I17.6       :BOOL; (*照明控制箱NJ-3AL3-2-运行状态*)",null,"L21\\L21LCB03C02_R","照明控制箱NJ-3AL3-2-运行状态",10142]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-3AL3-2-自动状态",{"$nulls":16},"NJ-3AL3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL3-2","03C02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":"LCB03C02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%I\"&B27*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":"LLCB03C02_A AT%I17.7 :BOOL; (*照明控制箱NJ-3AL3-2-自动状态*)"},"LLCB03C02_A             AT%I17.7       :BOOL; (*照明控制箱NJ-3AL3-2-自动状态*)",null,"L21\\L21LCB03C02_A","照明控制箱NJ-3AL3-2-自动状态",10143]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 1601R地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH43&AA43&\"-\"&AK43","v":"照明控制箱NJ-3AL3-3-运行状态"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-3AL3-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL3-3","03C03","运行状态",{"$f":"AH43&\"-\"&AK43","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"LCB03C03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B44*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LLCB03C03_R AT%I32.0 :BOOL; (*照明控制箱NJ-3AL3-3-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LLCB03C03_R             AT%I32.0       :BOOL; (*照明控制箱NJ-3AL3-3-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM43","v":"L21\\L21LCB03C03_R"},{"$f":"J43","v":"照明控制箱NJ-3AL3-3-运行状态"},{"$f":"10000+($B44*16*8+F43-1)","v":10256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},2,null,3,4,"照明控制箱NJ-3AL3-3-自动状态",{"$nulls":16},{"$f":"IF(AI44=\"\",\"\",AI44)","v":"NJ-3AL3-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL3-3","03C03","自动状态",{"$f":"AH44&\"-\"&AK44","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"LCB03C03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B44*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LLCB03C03_A AT%I32.1 :BOOL; (*照明控制箱NJ-3AL3-3-自动状态*)"},"LLCB03C03_A             AT%I32.1       :BOOL; (*照明控制箱NJ-3AL3-3-自动状态*)",null,"L21\\L21LCB03C03_A",{"$f":"J44","v":"照明控制箱NJ-3AL3-3-自动状态"},{"$f":"AS43+1","v":10257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,5,6,"照明控制箱NJ-3AL3-4-运行状态",{"$nulls":16},"NJ-3AL3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL3-4","03C04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"LCB03C04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B44*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LLCB03C04_R AT%I32.2 :BOOL; (*照明控制箱NJ-3AL3-4-运行状态*)"},"LLCB03C04_R             AT%I32.2       :BOOL; (*照明控制箱NJ-3AL3-4-运行状态*)",null,"L21\\L21LCB03C04_R","照明控制箱NJ-3AL3-4-运行状态",{"$f":"AS44+1","v":10258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},4,null,7,8,"照明控制箱NJ-3AL3-4-自动状态",{"$nulls":16},"NJ-3AL3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL3-4","03C04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"LCB03C04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B44*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LLCB03C04_A AT%I32.3 :BOOL; (*照明控制箱NJ-3AL3-4-自动状态*)"},"LLCB03C04_A             AT%I32.3       :BOOL; (*照明控制箱NJ-3AL3-4-自动状态*)",null,"L21\\L21LCB03C04_A","照明控制箱NJ-3AL3-4-自动状态",10259]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-3AL3-5-运行状态",{"$nulls":16},"NJ-3AL3-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL3-5","03C05","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"LCB03C05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B44*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LLCB03C05_R AT%I32.4 :BOOL; (*照明控制箱NJ-3AL3-5-运行状态*)"},"LLCB03C05_R             AT%I32.4       :BOOL; (*照明控制箱NJ-3AL3-5-运行状态*)",null,"L21\\L21LCB03C05_R","照明控制箱NJ-3AL3-5-运行状态",10260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-3AL3-5-自动状态",{"$nulls":16},"NJ-3AL3-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL3-5","03C05","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"LCB03C05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B44*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LLCB03C05_A AT%I32.5 :BOOL; (*照明控制箱NJ-3AL3-5-自动状态*)"},"LLCB03C05_A             AT%I32.5       :BOOL; (*照明控制箱NJ-3AL3-5-自动状态*)",null,"L21\\L21LCB03C05_A","照明控制箱NJ-3AL3-5-自动状态",10261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"照明控制箱NJ-3AL(GG)3-1-运行状态",{"$nulls":16},"NJ-3AL(GG)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-1","03C06","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"LCB03C06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B44*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LLCB03C06_R AT%I32.6 :BOOL; (*照明控制箱NJ-3AL(GG)3-1-运行状态*)"},"LLCB03C06_R             AT%I32.6       :BOOL; (*照明控制箱NJ-3AL(GG)3-1-运行状态*)",null,"L21\\L21LCB03C06_R","照明控制箱NJ-3AL(GG)3-1-运行状态",10262]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"照明控制箱NJ-3AL(GG)3-1-自动状态",{"$nulls":16},"NJ-3AL(GG)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-1","03C06","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"LCB03C06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B44*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LLCB03C06_A AT%I32.7 :BOOL; (*照明控制箱NJ-3AL(GG)3-1-自动状态*)"},"LLCB03C06_A             AT%I32.7       :BOOL; (*照明控制箱NJ-3AL(GG)3-1-自动状态*)",null,"L21\\L21LCB03C06_A","照明控制箱NJ-3AL(GG)3-1-自动状态",10263]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-3AL(GG)3-2-运行状态",{"$nulls":16},"NJ-3AL(GG)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-2","03C07","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"LCB03C07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B44*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LLCB03C07_R AT%I33.0 :BOOL; (*照明控制箱NJ-3AL(GG)3-2-运行状态*)"},"LLCB03C07_R             AT%I33.0       :BOOL; (*照明控制箱NJ-3AL(GG)3-2-运行状态*)",null,"L21\\L21LCB03C07_R","照明控制箱NJ-3AL(GG)3-2-运行状态",10264]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-3AL(GG)3-2-自动状态",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-3AL(GG)3-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-2","03C07","自动状态",{"$f":"AH52&\"-\"&AK52","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"LCB03C07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%I\"&B44*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LLCB03C07_A AT%I33.1 :BOOL; (*照明控制箱NJ-3AL(GG)3-2-自动状态*)"},"LLCB03C07_A             AT%I33.1       :BOOL; (*照明控制箱NJ-3AL(GG)3-2-自动状态*)",null,"L21\\L21LCB03C07_A",{"$f":"J52","v":"照明控制箱NJ-3AL(GG)3-2-自动状态"},10265]
[{"$nulls":5},11,null,21,22,"照明控制箱NJ-3AL(GG)3-3-运行状态",{"$nulls":16},"NJ-3AL(GG)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-3","03C08","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"LCB03C08_R"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%I\"&B44*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LLCB03C08_R AT%I33.2 :BOOL; (*照明控制箱NJ-3AL(GG)3-3-运行状态*)"},"LLCB03C08_R             AT%I33.2       :BOOL; (*照明控制箱NJ-3AL(GG)3-3-运行状态*)",null,"L21\\L21LCB03C08_R","照明控制箱NJ-3AL(GG)3-3-运行状态",10266]
[{"$nulls":5},12,null,23,24,"照明控制箱NJ-3AL(GG)3-3-自动状态",{"$nulls":16},"NJ-3AL(GG)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-3","03C08","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"LCB03C08_A"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%I\"&B44*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LLCB03C08_A AT%I33.3 :BOOL; (*照明控制箱NJ-3AL(GG)3-3-自动状态*)"},"LLCB03C08_A             AT%I33.3       :BOOL; (*照明控制箱NJ-3AL(GG)3-3-自动状态*)",null,"L21\\L21LCB03C08_A","照明控制箱NJ-3AL(GG)3-3-自动状态",10267]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-3AL(GG)3-4-运行状态",{"$nulls":16},"NJ-3AL(GG)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-4","03C09","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"LCB03C09_R"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%I\"&B44*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LLCB03C09_R AT%I33.4 :BOOL; (*照明控制箱NJ-3AL(GG)3-4-运行状态*)"},"LLCB03C09_R             AT%I33.4       :BOOL; (*照明控制箱NJ-3AL(GG)3-4-运行状态*)",null,"L21\\L21LCB03C09_R","照明控制箱NJ-3AL(GG)3-4-运行状态",10268]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-3AL(GG)3-4-自动状态",{"$nulls":16},"NJ-3AL(GG)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-4","03C09","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"LCB03C09_A"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%I\"&B44*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LLCB03C09_A AT%I33.5 :BOOL; (*照明控制箱NJ-3AL(GG)3-4-自动状态*)"},"LLCB03C09_A             AT%I33.5       :BOOL; (*照明控制箱NJ-3AL(GG)3-4-自动状态*)",null,"L21\\L21LCB03C09_A","照明控制箱NJ-3AL(GG)3-4-自动状态",10269]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-3AL(GG)3-5-运行状态",{"$nulls":16},"NJ-3AL(GG)3-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-5","03C10","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"LCB03C10_R"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%I\"&B44*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LLCB03C10_R AT%I33.6 :BOOL; (*照明控制箱NJ-3AL(GG)3-5-运行状态*)"},"LLCB03C10_R             AT%I33.6       :BOOL; (*照明控制箱NJ-3AL(GG)3-5-运行状态*)",null,"L21\\L21LCB03C10_R","照明控制箱NJ-3AL(GG)3-5-运行状态",10270]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-3AL(GG)3-5-自动状态",{"$nulls":16},"NJ-3AL(GG)3-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-5","03C10","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":"LCB03C10_A"},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%I\"&B44*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":"LLCB03C10_A AT%I33.7 :BOOL; (*照明控制箱NJ-3AL(GG)3-5-自动状态*)"},"LLCB03C10_A             AT%I33.7       :BOOL; (*照明控制箱NJ-3AL(GG)3-5-自动状态*)",null,"L21\\L21LCB03C10_A","照明控制箱NJ-3AL(GG)3-5-自动状态",10271]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B64&\"地址: \"&B61&\" *)\"","v":"(* IOM 0801R 地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},1,null,1,"C",{"$f":"AH60&AA60&\"-\"&AK60","v":"照明控制箱NJ-3AL(GG)3-6-运行状态"},{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-3AL(GG)3-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-6","03C11","运行状态",{"$f":"AH60&\"-\"&AK60","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"LCB03C11_R"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%I\"&B61*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LLCB03C11_R AT%I48.0 :BOOL; (*照明控制箱NJ-3AL(GG)3-6-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60))),SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))))),\" \")","v":"LLCB03C11_R             AT%I48.0       :BOOL; (*照明控制箱NJ-3AL(GG)3-6-运行状态*)"},null,{"$f":"AM60","v":"LCB03C11_R"},{"$f":"J60","v":"照明控制箱NJ-3AL(GG)3-6-运行状态"},{"$f":"10000+($B61*16*8+F60-1)","v":10384}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},2,null,2,"C",{"$f":"AH61&AA61&\"-\"&AK61","v":"照明控制箱NJ-3AL(GG)3-6-自动状态"},{"$nulls":16},{"$f":"IF(AI61=\"\",\"\",AI61)","v":"NJ-3AL(GG)3-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-6","03C11","自动状态",{"$f":"AH61&\"-\"&AK61","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"LCB03C11_A"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%I\"&B61*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LLCB03C11_A AT%I48.1 :BOOL; (*照明控制箱NJ-3AL(GG)3-6-自动状态*)"},"LLCB03C11_A             AT%I48.1       :BOOL; (*照明控制箱NJ-3AL(GG)3-6-自动状态*)",null,{"$f":"AM61","v":"LCB03C11_A"},{"$f":"J61","v":"照明控制箱NJ-3AL(GG)3-6-自动状态"},{"$f":"AS60+1","v":10385}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},3,null,3,"C",{"$f":"AH62&AA62&\"-\"&AK62","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B61*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS61+1","v":10386}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},4,null,4,"C",{"$f":"AH63&AA63&\"-\"&AK63","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B61*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10387]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},5,null,5,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B61*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10388]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B61*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10389]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B61*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10390]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%I\"&B61*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10391]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B73&\"地址: \"&B70&\" *)\"","v":"(* IOM 1601D地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH69&AA69&\"-\"&AK69","v":"空调机组NJ-3AP(KT)3-1-启停控制"},{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-3AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-1","03C01","启停控制",{"$f":"AH69&\"-\"&AK69","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU03C01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%Q\"&B70*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU03C01_C AT%Q64.0 :BOOL; (*空调机组NJ-3AP(KT)3-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69))),SEARCH(\":\",REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69)))))),\" \")","v":"LAHU03C01_C             AT%Q64.0       :BOOL; (*空调机组NJ-3AP(KT)3-1-启停控制*)"},null,{"$f":"AM69","v":"AHU03C01_C"},{"$f":"J69","v":"空调机组NJ-3AP(KT)3-1-启停控制"},{"$f":"($B70*16*8+F69-1)","v":512}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","空调机组NJ-3AP(KT)3-2-启停控制",{"$nulls":16},{"$f":"IF(AI70=\"\",\"\",AI70)","v":"NJ-3AP(KT)3-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-2","03C02","启停控制",{"$f":"AH70&\"-\"&AK70","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"AHU03C02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%Q\"&B70*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LAHU03C02_C AT%Q64.1 :BOOL; (*空调机组NJ-3AP(KT)3-2-启停控制*)"},"LAHU03C02_C             AT%Q64.1       :BOOL; (*空调机组NJ-3AP(KT)3-2-启停控制*)",null,"AHU03C02_C",{"$f":"J70","v":"空调机组NJ-3AP(KT)3-2-启停控制"},{"$f":"AS69+1","v":513}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-3AP(KT)3-3-启停控制",{"$nulls":16},"NJ-3AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-3","03C03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"AHU03C03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%Q\"&B70*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LAHU03C03_C AT%Q64.2 :BOOL; (*空调机组NJ-3AP(KT)3-3-启停控制*)"},"LAHU03C03_C             AT%Q64.2       :BOOL; (*空调机组NJ-3AP(KT)3-3-启停控制*)",null,"AHU03C03_C","空调机组NJ-3AP(KT)3-3-启停控制",{"$f":"AS70+1","v":514}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","空调机组NJ-3AP(KT)3-4-启停控制",{"$nulls":16},"NJ-3AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-4","03C04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"AHU03C04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%Q\"&B70*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LAHU03C04_C AT%Q64.3 :BOOL; (*空调机组NJ-3AP(KT)3-4-启停控制*)"},"LAHU03C04_C             AT%Q64.3       :BOOL; (*空调机组NJ-3AP(KT)3-4-启停控制*)",null,"AHU03C04_C","空调机组NJ-3AP(KT)3-4-启停控制",515]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-3AP(KT)3-5-启停控制",{"$nulls":16},"NJ-3AP(KT)3-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-5","03C05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"AHU03C05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%Q\"&B70*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LAHU03C05_C AT%Q64.4 :BOOL; (*空调机组NJ-3AP(KT)3-5-启停控制*)"},"LAHU03C05_C             AT%Q64.4       :BOOL; (*空调机组NJ-3AP(KT)3-5-启停控制*)",null,"AHU03C05_C","空调机组NJ-3AP(KT)3-5-启停控制",516]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-3AP(KT)3-6-启停控制",{"$nulls":16},"NJ-3AP(KT)3-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-6","03C06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":"AHU03C06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%Q\"&B70*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":"LAHU03C06_C AT%Q64.5 :BOOL; (*空调机组NJ-3AP(KT)3-6-启停控制*)"},"LAHU03C06_C             AT%Q64.5       :BOOL; (*空调机组NJ-3AP(KT)3-6-启停控制*)",null,"AHU03C06_C","空调机组NJ-3AP(KT)3-6-启停控制",517]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","空调机组NJ-3AP(KT)3-7-启停控制",{"$nulls":16},"NJ-3AP(KT)3-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-7","03C07","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":"AHU03C07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%Q\"&B70*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":"LAHU03C07_C AT%Q64.6 :BOOL; (*空调机组NJ-3AP(KT)3-7-启停控制*)"},"LAHU03C07_C             AT%Q64.6       :BOOL; (*空调机组NJ-3AP(KT)3-7-启停控制*)",null,"AHU03C07_C","空调机组NJ-3AP(KT)3-7-启停控制",518]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-3AL3-1-启停控制",{"$nulls":16},"NJ-3AL3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL3-1","03C01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH76,List!$B$3:$D$445,2,FALSE)&AJ76&\"_\"&VLOOKUP(AK76,List!$K$2:$M$447,2,FALSE)","v":"LCB03C01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM76&\" \"&\"AT%Q\"&B70*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J76&\"*)\",\" \")","v":"LLCB03C01_C AT%Q64.7 :BOOL; (*照明控制箱NJ-3AL3-1-启停控制*)"},"LLCB03C01_C             AT%Q64.7       :BOOL; (*照明控制箱NJ-3AL3-1-启停控制*)",null,"LCB03C01_C","照明控制箱NJ-3AL3-1-启停控制",519]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-3AL3-2-启停控制",{"$nulls":16},"NJ-3AL3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL3-2","03C02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"LCB03C02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%Q\"&B70*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LLCB03C02_C AT%Q65.0 :BOOL; (*照明控制箱NJ-3AL3-2-启停控制*)"},"LLCB03C02_C             AT%Q65.0       :BOOL; (*照明控制箱NJ-3AL3-2-启停控制*)",null,"LCB03C02_C","照明控制箱NJ-3AL3-2-启停控制",520]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-3AL3-3-启停控制",{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-3AL3-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL3-3","03C03","启停控制",{"$f":"AH78&\"-\"&AK78","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"LCB03C03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B70*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LLCB03C03_C AT%Q65.1 :BOOL; (*照明控制箱NJ-3AL3-3-启停控制*)"},"LLCB03C03_C             AT%Q65.1       :BOOL; (*照明控制箱NJ-3AL3-3-启停控制*)",null,"LCB03C03_C",{"$f":"J78","v":"照明控制箱NJ-3AL3-3-启停控制"},521]
[{"$nulls":5},11,null,"11+","11-","照明控制箱NJ-3AL3-4-启停控制",{"$nulls":16},"NJ-3AL3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL3-4","03C04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"LCB03C04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B70*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LLCB03C04_C AT%Q65.2 :BOOL; (*照明控制箱NJ-3AL3-4-启停控制*)"},"LLCB03C04_C             AT%Q65.2       :BOOL; (*照明控制箱NJ-3AL3-4-启停控制*)",null,"LCB03C04_C","照明控制箱NJ-3AL3-4-启停控制",522]
[{"$nulls":5},12,null,"12+","12-","照明控制箱NJ-3AL3-5-启停控制",{"$nulls":16},"NJ-3AL3-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL3-5","03C05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"LCB03C05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B70*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LLCB03C05_C AT%Q65.3 :BOOL; (*照明控制箱NJ-3AL3-5-启停控制*)"},"LLCB03C05_C             AT%Q65.3       :BOOL; (*照明控制箱NJ-3AL3-5-启停控制*)",null,"LCB03C05_C","照明控制箱NJ-3AL3-5-启停控制",523]
[{"$nulls":5},13,null,"13+","13-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%Q\"&B70*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",524]
[{"$nulls":5},14,null,"14+","14-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%Q\"&B70*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",525]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%Q\"&B70*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",526]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH84,List!$B$3:$D$445,2,FALSE)&AJ84&\"_\"&VLOOKUP(AK84,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM84&\" \"&\"AT%Q\"&B70*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J84&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",527]
[null,"IOM 0801D",{"$nulls":38},{"$f":"\"(* \"&B90&\"地址: \"&B87&\" *)\"","v":"(* IOM 0801D地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH86&AA86&\"-\"&AK86","v":"照明控制箱NJ-3AL(GG)3-1-启停控制"},{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-3AL(GG)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-1","03C06","启停控制",{"$f":"AH86&\"-\"&AK86","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"LCB03C06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%Q\"&B87*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LLCB03C06_C AT%Q80.0 :BOOL; (*照明控制箱NJ-3AL(GG)3-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86))),SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))))),\" \")","v":"LLCB03C06_C             AT%Q80.0       :BOOL; (*照明控制箱NJ-3AL(GG)3-1-启停控制*)"},null,{"$f":"AM86","v":"LCB03C06_C"},{"$f":"J86","v":"照明控制箱NJ-3AL(GG)3-1-启停控制"},{"$f":"($B87*16*8+F86-1)","v":640}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","照明控制箱NJ-3AL(GG)3-2-启停控制",{"$nulls":16},{"$f":"IF(AI87=\"\",\"\",AI87)","v":"NJ-3AL(GG)3-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-2","03C07","启停控制",{"$f":"AH87&\"-\"&AK87","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"LCB03C07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%Q\"&B87*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LLCB03C07_C AT%Q80.1 :BOOL; (*照明控制箱NJ-3AL(GG)3-2-启停控制*)"},"LLCB03C07_C             AT%Q80.1       :BOOL; (*照明控制箱NJ-3AL(GG)3-2-启停控制*)",null,"LCB03C07_C",{"$f":"J87","v":"照明控制箱NJ-3AL(GG)3-2-启停控制"},{"$f":"AS86+1","v":641}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","照明控制箱NJ-3AL(GG)3-3-启停控制",{"$nulls":16},"NJ-3AL(GG)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-3","03C08","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"LCB03C08_C"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%Q\"&B87*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LLCB03C08_C AT%Q80.2 :BOOL; (*照明控制箱NJ-3AL(GG)3-3-启停控制*)"},"LLCB03C08_C             AT%Q80.2       :BOOL; (*照明控制箱NJ-3AL(GG)3-3-启停控制*)",null,"LCB03C08_C","照明控制箱NJ-3AL(GG)3-3-启停控制",{"$f":"AS87+1","v":642}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","照明控制箱NJ-3AL(GG)3-4-启停控制",{"$nulls":16},"NJ-3AL(GG)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-4","03C09","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"LCB03C09_C"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%Q\"&B87*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LLCB03C09_C AT%Q80.3 :BOOL; (*照明控制箱NJ-3AL(GG)3-4-启停控制*)"},"LLCB03C09_C             AT%Q80.3       :BOOL; (*照明控制箱NJ-3AL(GG)3-4-启停控制*)",null,"LCB03C09_C","照明控制箱NJ-3AL(GG)3-4-启停控制",643]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","照明控制箱NJ-3AL(GG)3-5-启停控制",{"$nulls":16},"NJ-3AL(GG)3-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-5","03C10","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":"LCB03C10_C"},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%Q\"&B87*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":"LLCB03C10_C AT%Q80.4 :BOOL; (*照明控制箱NJ-3AL(GG)3-5-启停控制*)"},"LLCB03C10_C             AT%Q80.4       :BOOL; (*照明控制箱NJ-3AL(GG)3-5-启停控制*)",null,"LCB03C10_C","照明控制箱NJ-3AL(GG)3-5-启停控制",644]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","照明控制箱NJ-3AL(GG)3-6-启停控制",{"$nulls":16},"NJ-3AL(GG)3-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)3-6","03C11","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH91,List!$B$3:$D$445,2,FALSE)&AJ91&\"_\"&VLOOKUP(AK91,List!$K$2:$M$447,2,FALSE)","v":"LCB03C11_C"},{"$f":"_xlfn.IFNA(\"L\"&AM91&\" \"&\"AT%Q\"&B87*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J91&\"*)\",\" \")","v":"LLCB03C11_C AT%Q80.5 :BOOL; (*照明控制箱NJ-3AL(GG)3-6-启停控制*)"},"LLCB03C11_C             AT%Q80.5       :BOOL; (*照明控制箱NJ-3AL(GG)3-6-启停控制*)",null,"LCB03C11_C","照明控制箱NJ-3AL(GG)3-6-启停控制",645]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH92,List!$B$3:$D$445,2,FALSE)&AJ92&\"_\"&VLOOKUP(AK92,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM92&\" \"&\"AT%Q\"&B87*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J92&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",646]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL93,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL93,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH93,List!$B$3:$D$445,2,FALSE)&AJ93&\"_\"&VLOOKUP(AK93,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM93&\" \"&\"AT%Q\"&B87*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J93&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",647]
[null,{"$f":"B99","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B99&\"地址: \"&B96&\" *)\"","v":"(* IOM 0801U地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH95&AA95&\"-\"&AK95","v":"空调机组NJ-3AP(KT)3-1-回风温度"},{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-3AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-1","03C01","回风温度",{"$f":"AH95&\"-\"&AK95","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"AHU03C01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%I\"&B96*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LAHU03C01_RT AT%I96.0 :INT ; (*空调机组NJ-3AP(KT)3-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95))),SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))))),\" \")","v":"LAHU03C01_RT            AT%I96.0       :INT ; (*空调机组NJ-3AP(KT)3-1-回风温度*)"},null,{"$f":"AM95","v":"AHU03C01_RT"},{"$f":"J95","v":"空调机组NJ-3AP(KT)3-1-回风温度"},{"$f":"30000+($B96*8+F95-1)","v":30048}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-3AP(KT)3-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI96=\"\",\"\",AI96)","v":"NJ-3AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-1","03C01","水阀反馈",{"$f":"AH96&\"-\"&AK96","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"AHU03C01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%I\"&B96*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LAHU03C01_WVB AT%I98.0 :INT ; (*空调机组NJ-3AP(KT)3-1-水阀反馈*)"},"LAHU03C01_WVB           AT%I98.0       :INT ; (*空调机组NJ-3AP(KT)3-1-水阀反馈*)",null,"AHU03C01_WVB",{"$f":"J96","v":"空调机组NJ-3AP(KT)3-1-水阀反馈"},{"$f":"AS95+1","v":30049}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)3-2-回风温度",{"$nulls":16},"NJ-3AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-2","03C02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":"AHU03C02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%I\"&B96*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":"LAHU03C02_RT AT%I100.0 :INT ; (*空调机组NJ-3AP(KT)3-2-回风温度*)"},"LAHU03C02_RT            AT%I100.0      :INT ; (*空调机组NJ-3AP(KT)3-2-回风温度*)",null,"AHU03C02_RT","空调机组NJ-3AP(KT)3-2-回风温度",{"$f":"AS96+1","v":30050}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-3AP(KT)3-2-水阀反馈",{"$nulls":16},"NJ-3AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-2","03C02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":"AHU03C02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%I\"&B96*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":"LAHU03C02_WVB AT%I102.0 :INT ; (*空调机组NJ-3AP(KT)3-2-水阀反馈*)"},"LAHU03C02_WVB           AT%I102.0      :INT ; (*空调机组NJ-3AP(KT)3-2-水阀反馈*)",null,"AHU03C02_WVB","空调机组NJ-3AP(KT)3-2-水阀反馈",30051]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-3AP(KT)3-3-回风温度",{"$nulls":16},"NJ-3AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-3","03C03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH99,List!$B$3:$D$445,2,FALSE)&AJ99&\"_\"&VLOOKUP(AK99,List!$K$2:$M$447,2,FALSE)","v":"AHU03C03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM99&\" \"&\"AT%I\"&B96*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J99&\"*)\",\" \")","v":"LAHU03C03_RT AT%I104.0 :INT ; (*空调机组NJ-3AP(KT)3-3-回风温度*)"},"LAHU03C03_RT            AT%I104.0      :INT ; (*空调机组NJ-3AP(KT)3-3-回风温度*)",null,"AHU03C03_RT","空调机组NJ-3AP(KT)3-3-回风温度",30052]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-3AP(KT)3-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI100=\"\",\"\",AI100)","v":"NJ-3AP(KT)3-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-3","03C03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH100,List!$B$3:$D$445,2,FALSE)&AJ100&\"_\"&VLOOKUP(AK100,List!$K$2:$M$447,2,FALSE)","v":"AHU03C03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM100&\" \"&\"AT%I\"&B96*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J100&\"*)\",\" \")","v":"LAHU03C03_WVB AT%I106.0 :INT ; (*空调机组NJ-3AP(KT)3-3-水阀反馈*)"},"LAHU03C03_WVB           AT%I106.0      :INT ; (*空调机组NJ-3AP(KT)3-3-水阀反馈*)",null,"AHU03C03_WVB",{"$f":"J100","v":"空调机组NJ-3AP(KT)3-3-水阀反馈"},30053]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-3AP(KT)3-4-回风温度",{"$nulls":16},"NJ-3AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-4","03C04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH101,List!$B$3:$D$445,2,FALSE)&AJ101&\"_\"&VLOOKUP(AK101,List!$K$2:$M$447,2,FALSE)","v":"AHU03C04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM101&\" \"&\"AT%I\"&B96*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J101&\"*)\",\" \")","v":"LAHU03C04_RT AT%I108.0 :INT ; (*空调机组NJ-3AP(KT)3-4-回风温度*)"},"LAHU03C04_RT            AT%I108.0      :INT ; (*空调机组NJ-3AP(KT)3-4-回风温度*)",null,"AHU03C04_RT","空调机组NJ-3AP(KT)3-4-回风温度",30054]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-3AP(KT)3-4-水阀反馈",{"$nulls":16},"NJ-3AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL102,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL102,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-4","03C04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH102,List!$B$3:$D$445,2,FALSE)&AJ102&\"_\"&VLOOKUP(AK102,List!$K$2:$M$447,2,FALSE)","v":"AHU03C04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM102&\" \"&\"AT%I\"&B96*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J102&\"*)\",\" \")","v":"LAHU03C04_WVB AT%I110.0 :INT ; (*空调机组NJ-3AP(KT)3-4-水阀反馈*)"},"LAHU03C04_WVB           AT%I110.0      :INT ; (*空调机组NJ-3AP(KT)3-4-水阀反馈*)",null,"AHU03C04_WVB","空调机组NJ-3AP(KT)3-4-水阀反馈",30055]
[null,{"$f":"B108","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B108&\"地址: \"&B105&\" *)\"","v":"(* IOM 0801U地址: 7 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH104&AA104&\"-\"&AK104","v":"空调机组NJ-3AP(KT)3-5-回风温度"},{"$nulls":16},{"$f":"IF(AI104=\"\",\"\",AI104)","v":"NJ-3AP(KT)3-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-5","03C05","回风温度",{"$f":"AH104&\"-\"&AK104","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"AHU03C05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%I\"&B105*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LAHU03C05_RT AT%I112.0 :INT ; (*空调机组NJ-3AP(KT)3-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104))),SEARCH(\":\",REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104)))))),\" \")","v":"LAHU03C05_RT            AT%I112.0      :INT ; (*空调机组NJ-3AP(KT)3-5-回风温度*)"},null,{"$f":"AM104","v":"AHU03C05_RT"},{"$f":"J104","v":"空调机组NJ-3AP(KT)3-5-回风温度"},{"$f":"30000+($B105*8+F104-1)","v":30056}]
[null,7,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-3AP(KT)3-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI105=\"\",\"\",AI105)","v":"NJ-3AP(KT)3-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-5","03C05","水阀反馈",{"$f":"AH105&\"-\"&AK105","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"AHU03C05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%I\"&B105*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LAHU03C05_WVB AT%I114.0 :INT ; (*空调机组NJ-3AP(KT)3-5-水阀反馈*)"},"LAHU03C05_WVB           AT%I114.0      :INT ; (*空调机组NJ-3AP(KT)3-5-水阀反馈*)",null,"AHU03C05_WVB",{"$f":"J105","v":"空调机组NJ-3AP(KT)3-5-水阀反馈"},{"$f":"AS104+1","v":30057}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)3-6-回风温度",{"$nulls":16},"NJ-3AP(KT)3-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-6","03C06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":"AHU03C06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%I\"&B105*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":"LAHU03C06_RT AT%I116.0 :INT ; (*空调机组NJ-3AP(KT)3-6-回风温度*)"},"LAHU03C06_RT            AT%I116.0      :INT ; (*空调机组NJ-3AP(KT)3-6-回风温度*)",null,"AHU03C06_RT","空调机组NJ-3AP(KT)3-6-回风温度",{"$f":"AS105+1","v":30058}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-3AP(KT)3-6-水阀反馈",{"$nulls":16},"NJ-3AP(KT)3-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-6","03C06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH107,List!$B$3:$D$445,2,FALSE)&AJ107&\"_\"&VLOOKUP(AK107,List!$K$2:$M$447,2,FALSE)","v":"AHU03C06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM107&\" \"&\"AT%I\"&B105*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J107&\"*)\",\" \")","v":"LAHU03C06_WVB AT%I118.0 :INT ; (*空调机组NJ-3AP(KT)3-6-水阀反馈*)"},"LAHU03C06_WVB           AT%I118.0      :INT ; (*空调机组NJ-3AP(KT)3-6-水阀反馈*)",null,"AHU03C06_WVB","空调机组NJ-3AP(KT)3-6-水阀反馈",30059]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-3AP(KT)3-7-回风温度",{"$nulls":16},"NJ-3AP(KT)3-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-7","03C07","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH108,List!$B$3:$D$445,2,FALSE)&AJ108&\"_\"&VLOOKUP(AK108,List!$K$2:$M$447,2,FALSE)","v":"AHU03C07_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM108&\" \"&\"AT%I\"&B105*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J108&\"*)\",\" \")","v":"LAHU03C07_RT AT%I120.0 :INT ; (*空调机组NJ-3AP(KT)3-7-回风温度*)"},"LAHU03C07_RT            AT%I120.0      :INT ; (*空调机组NJ-3AP(KT)3-7-回风温度*)",null,"AHU03C07_RT","空调机组NJ-3AP(KT)3-7-回风温度",30060]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-3AP(KT)3-7-水阀反馈",{"$nulls":16},"NJ-3AP(KT)3-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-7","03C07","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH109,List!$B$3:$D$445,2,FALSE)&AJ109&\"_\"&VLOOKUP(AK109,List!$K$2:$M$447,2,FALSE)","v":"AHU03C07_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM109&\" \"&\"AT%I\"&B105*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J109&\"*)\",\" \")","v":"LAHU03C07_WVB AT%I122.0 :INT ; (*空调机组NJ-3AP(KT)3-7-水阀反馈*)"},"LAHU03C07_WVB           AT%I122.0      :INT ; (*空调机组NJ-3AP(KT)3-7-水阀反馈*)",null,"AHU03C07_WVB",{"$f":"J109","v":"空调机组NJ-3AP(KT)3-7-水阀反馈"},30061]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL110,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL110,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH110,List!$B$3:$D$445,2,FALSE)&AJ110&\"_\"&VLOOKUP(AK110,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM110&\" \"&\"AT%I\"&B105*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J110&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30062]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},{"$f":"IF(AI111=\"\",\"\",AI111)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL111,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL111,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH111,List!$B$3:$D$445,2,FALSE)&AJ111&\"_\"&VLOOKUP(AK111,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM111&\" \"&\"AT%I\"&B105*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J111&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30063]
[null,{"$f":"B117","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B117&\"地址: \"&B114&\" *)\"","v":"(* IOM 0401A地址: 8 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH113&AA113&\"-\"&AK113","v":"空调机组NJ-3AP(KT)3-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI113=\"\",\"\",AI113)","v":"NJ-3AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-1","03C01","水阀控制",{"$f":"AH113&\"-\"&AK113","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH113,List!$B$3:$D$445,2,FALSE)&AJ113&\"_\"&VLOOKUP(AK113,List!$K$2:$M$447,2,FALSE)","v":"AHU03C01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM113&\" \"&\"AT%Q\"&B114*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J113&\"*)\",\" \")","v":"LAHU03C01_WVC AT%Q128.0 :INT ; (*空调机组NJ-3AP(KT)3-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN113,SEARCH(\"AT%\",AN113),,REPT(\" \",25-SEARCH(\"AT%\",AN113))),SEARCH(\":\",REPLACE(AN113,SEARCH(\"AT%\",AN113),,REPT(\" \",25-SEARCH(\"AT%\",AN113)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN113,SEARCH(\"AT%\",AN113),,REPT(\" \",25-SEARCH(\"AT%\",AN113)))))),\" \")","v":"LAHU03C01_WVC           AT%Q128.0      :INT ; (*空调机组NJ-3AP(KT)3-1-水阀控制*)"},null,{"$f":"AM113","v":"AHU03C01_WVC"},{"$f":"J113","v":"空调机组NJ-3AP(KT)3-1-水阀控制"},{"$f":"40000+($B114*8+F113-1)","v":40064}]
[null,8,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH114&AA114&\"-\"&AK114","v":"空调机组NJ-3AP(KT)3-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI114=\"\",\"\",AI114)","v":"NJ-3AP(KT)3-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-2","03C02","水阀控制",{"$f":"AH114&\"-\"&AK114","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH114,List!$B$3:$D$445,2,FALSE)&AJ114&\"_\"&VLOOKUP(AK114,List!$K$2:$M$447,2,FALSE)","v":"AHU03C02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM114&\" \"&\"AT%Q\"&B114*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J114&\"*)\",\" \")","v":"LAHU03C02_WVC AT%Q130.0 :INT ; (*空调机组NJ-3AP(KT)3-2-水阀控制*)"},"LAHU03C02_WVC           AT%Q130.0      :INT ; (*空调机组NJ-3AP(KT)3-2-水阀控制*)",null,"AHU03C02_WVC",{"$f":"J114","v":"空调机组NJ-3AP(KT)3-2-水阀控制"},{"$f":"AS113+1","v":40065}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH115&AA115&\"-\"&AK115","v":"空调机组NJ-3AP(KT)3-3-水阀控制"},{"$nulls":16},"NJ-3AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-3","03C03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH115,List!$B$3:$D$445,2,FALSE)&AJ115&\"_\"&VLOOKUP(AK115,List!$K$2:$M$447,2,FALSE)","v":"AHU03C03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM115&\" \"&\"AT%Q\"&B114*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J115&\"*)\",\" \")","v":"LAHU03C03_WVC AT%Q132.0 :INT ; (*空调机组NJ-3AP(KT)3-3-水阀控制*)"},"LAHU03C03_WVC           AT%Q132.0      :INT ; (*空调机组NJ-3AP(KT)3-3-水阀控制*)",null,"AHU03C03_WVC","空调机组NJ-3AP(KT)3-3-水阀控制",{"$f":"AS114+1","v":40066}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH116&AA116&\"-\"&AK116","v":"空调机组NJ-3AP(KT)3-4-水阀控制"},{"$nulls":16},"NJ-3AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-4","03C04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH116,List!$B$3:$D$445,2,FALSE)&AJ116&\"_\"&VLOOKUP(AK116,List!$K$2:$M$447,2,FALSE)","v":"AHU03C04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM116&\" \"&\"AT%Q\"&B114*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J116&\"*)\",\" \")","v":"LAHU03C04_WVC AT%Q134.0 :INT ; (*空调机组NJ-3AP(KT)3-4-水阀控制*)"},"LAHU03C04_WVC           AT%Q134.0      :INT ; (*空调机组NJ-3AP(KT)3-4-水阀控制*)",null,"AHU03C04_WVC","空调机组NJ-3AP(KT)3-4-水阀控制",40067]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B126","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B126&\"地址: \"&B123&\" *)\"","v":"(* IOM 0401A地址: 9 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH122&AA122&\"-\"&AK122","v":"空调机组NJ-3AP(KT)3-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI122=\"\",\"\",AI122)","v":"NJ-3AP(KT)3-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-5","03C05","水阀控制",{"$f":"AH122&\"-\"&AK122","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH122,List!$B$3:$D$445,2,FALSE)&AJ122&\"_\"&VLOOKUP(AK122,List!$K$2:$M$447,2,FALSE)","v":"AHU03C05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM122&\" \"&\"AT%Q\"&B123*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J122&\"*)\",\" \")","v":"LAHU03C05_WVC AT%Q144.0 :INT ; (*空调机组NJ-3AP(KT)3-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN122,SEARCH(\"AT%\",AN122),,REPT(\" \",25-SEARCH(\"AT%\",AN122))),SEARCH(\":\",REPLACE(AN122,SEARCH(\"AT%\",AN122),,REPT(\" \",25-SEARCH(\"AT%\",AN122)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN122,SEARCH(\"AT%\",AN122),,REPT(\" \",25-SEARCH(\"AT%\",AN122)))))),\" \")","v":"LAHU03C05_WVC           AT%Q144.0      :INT ; (*空调机组NJ-3AP(KT)3-5-水阀控制*)"},null,{"$f":"AM122","v":"AHU03C05_WVC"},{"$f":"J122","v":"空调机组NJ-3AP(KT)3-5-水阀控制"},{"$f":"40000+($B123*8+F122-1)","v":40072}]
[null,9,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH123&AA123&\"-\"&AK123","v":"空调机组NJ-3AP(KT)3-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI123=\"\",\"\",AI123)","v":"NJ-3AP(KT)3-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-6","03C06","水阀控制",{"$f":"AH123&\"-\"&AK123","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH123,List!$B$3:$D$445,2,FALSE)&AJ123&\"_\"&VLOOKUP(AK123,List!$K$2:$M$447,2,FALSE)","v":"AHU03C06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM123&\" \"&\"AT%Q\"&B123*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J123&\"*)\",\" \")","v":"LAHU03C06_WVC AT%Q146.0 :INT ; (*空调机组NJ-3AP(KT)3-6-水阀控制*)"},"LAHU03C06_WVC           AT%Q146.0      :INT ; (*空调机组NJ-3AP(KT)3-6-水阀控制*)",null,"AHU03C06_WVC",{"$f":"J123","v":"空调机组NJ-3AP(KT)3-6-水阀控制"},{"$f":"AS122+1","v":40073}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH124&AA124&\"-\"&AK124","v":"空调机组NJ-3AP(KT)3-7-水阀控制"},{"$nulls":16},"NJ-3AP(KT)3-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)3-7","03C07","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH124,List!$B$3:$D$445,2,FALSE)&AJ124&\"_\"&VLOOKUP(AK124,List!$K$2:$M$447,2,FALSE)","v":"AHU03C07_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM124&\" \"&\"AT%Q\"&B123*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J124&\"*)\",\" \")","v":"LAHU03C07_WVC AT%Q148.0 :INT ; (*空调机组NJ-3AP(KT)3-7-水阀控制*)"},"LAHU03C07_WVC           AT%Q148.0      :INT ; (*空调机组NJ-3AP(KT)3-7-水阀控制*)",null,"AHU03C07_WVC","空调机组NJ-3AP(KT)3-7-水阀控制",{"$f":"AS123+1","v":40074}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH125&AA125&\"-\"&AK125","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH125,List!$B$3:$D$445,2,FALSE)&AJ125&\"_\"&VLOOKUP(AK125,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM125&\" \"&\"AT%Q\"&B123*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J125&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40075]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L403","index":28,"n_rows":102,"n_cols":45,"rows_kept":102,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[41,5,41,6],[41,9,41,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[92,5,92,6],[92,9,92,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[101,5,101,6],[101,9,101,25],[4,1,5,1],[11,1,22,1],[28,1,39,1],[45,1,48,1],[54,1,65,1],[71,1,74,1],[80,1,83,1],[89,1,92,1],[98,1,101,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4],[32,2,39,4],[58,2,65,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L21",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 10 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH8&AA8&\"-\"&AK8","v":"空调机组NJ-4AP(KT)3-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-4AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-1","04C01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH8,List!$B$3:$D$445,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,List!$K$2:$M$447,2,FALSE)","v":"AHU04C01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LAHU04C01_R AT%I160.0 :BOOL; (*空调机组NJ-4AP(KT)3-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LAHU04C01_R             AT%I160.0      :BOOL; (*空调机组NJ-4AP(KT)3-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L21\\L21AHU04C01_R"},{"$f":"J8","v":"空调机组NJ-4AP(KT)3-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":11280}]
[null,10,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},2,null,3,4,"空调机组NJ-4AP(KT)3-1-故障状态",{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-4AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-1","04C01","故障状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU04C01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU04C01_F AT%I160.1 :BOOL; (*空调机组NJ-4AP(KT)3-1-故障状态*)"},"LAHU04C01_F             AT%I160.1      :BOOL; (*空调机组NJ-4AP(KT)3-1-故障状态*)",null,"L21\\L21AHU04C01_F",{"$f":"J9","v":"空调机组NJ-4AP(KT)3-1-故障状态"},{"$f":"AS8+1","v":11281}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-4AP(KT)3-1-自动状态",{"$nulls":16},"NJ-4AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-1","04C01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU04C01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU04C01_A AT%I160.2 :BOOL; (*空调机组NJ-4AP(KT)3-1-自动状态*)"},"LAHU04C01_A             AT%I160.2      :BOOL; (*空调机组NJ-4AP(KT)3-1-自动状态*)",null,"L21\\L21AHU04C01_A","空调机组NJ-4AP(KT)3-1-自动状态",{"$f":"AS9+1","v":11282}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-4AP(KT)3-1-风机压差",{"$nulls":16},"NJ-4AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-1","04C01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU04C01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU04C01_FPS AT%I160.3 :BOOL; (*空调机组NJ-4AP(KT)3-1-风机压差*)"},"LAHU04C01_FPS           AT%I160.3      :BOOL; (*空调机组NJ-4AP(KT)3-1-风机压差*)",null,"L21\\L21AHU04C01_FPS","空调机组NJ-4AP(KT)3-1-风机压差",11283]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-4AP(KT)3-2-运行状态",{"$nulls":16},"NJ-4AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-2","04C02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU04C02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU04C02_R AT%I160.4 :BOOL; (*空调机组NJ-4AP(KT)3-2-运行状态*)"},"LAHU04C02_R             AT%I160.4      :BOOL; (*空调机组NJ-4AP(KT)3-2-运行状态*)",null,"L21\\L21AHU04C02_R","空调机组NJ-4AP(KT)3-2-运行状态",11284]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-4AP(KT)3-2-故障状态",{"$nulls":16},"NJ-4AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-2","04C02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU04C02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU04C02_F AT%I160.5 :BOOL; (*空调机组NJ-4AP(KT)3-2-故障状态*)"},"LAHU04C02_F             AT%I160.5      :BOOL; (*空调机组NJ-4AP(KT)3-2-故障状态*)",null,"L21\\L21AHU04C02_F","空调机组NJ-4AP(KT)3-2-故障状态",11285]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-4AP(KT)3-2-自动状态",{"$nulls":16},"NJ-4AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-2","04C02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU04C02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU04C02_A AT%I160.6 :BOOL; (*空调机组NJ-4AP(KT)3-2-自动状态*)"},"LAHU04C02_A             AT%I160.6      :BOOL; (*空调机组NJ-4AP(KT)3-2-自动状态*)",null,"L21\\L21AHU04C02_A","空调机组NJ-4AP(KT)3-2-自动状态",11286]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-4AP(KT)3-2-风机压差",{"$nulls":16},"NJ-4AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-2","04C02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU04C02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU04C02_FPS AT%I160.7 :BOOL; (*空调机组NJ-4AP(KT)3-2-风机压差*)"},"LAHU04C02_FPS           AT%I160.7      :BOOL; (*空调机组NJ-4AP(KT)3-2-风机压差*)",null,"L21\\L21AHU04C02_FPS","空调机组NJ-4AP(KT)3-2-风机压差",11287]
[{"$nulls":5},9,null,17,18,"空调机组NJ-4AP(KT)3-3-运行状态",{"$nulls":16},"NJ-4AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-3","04C03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU04C03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU04C03_R AT%I161.0 :BOOL; (*空调机组NJ-4AP(KT)3-3-运行状态*)"},"LAHU04C03_R             AT%I161.0      :BOOL; (*空调机组NJ-4AP(KT)3-3-运行状态*)",null,"L21\\L21AHU04C03_R","空调机组NJ-4AP(KT)3-3-运行状态",11288]
[{"$nulls":5},10,null,19,20,"空调机组NJ-4AP(KT)3-3-故障状态",{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-4AP(KT)3-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-3","04C03","故障状态",{"$f":"AH17&\"-\"&AK17","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU04C03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU04C03_F AT%I161.1 :BOOL; (*空调机组NJ-4AP(KT)3-3-故障状态*)"},"LAHU04C03_F             AT%I161.1      :BOOL; (*空调机组NJ-4AP(KT)3-3-故障状态*)",null,"L21\\L21AHU04C03_F","空调机组NJ-4AP(KT)3-3-故障状态",11289]
[{"$nulls":5},11,null,21,22,"空调机组NJ-4AP(KT)3-3-自动状态",{"$nulls":16},"NJ-4AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-3","04C03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU04C03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU04C03_A AT%I161.2 :BOOL; (*空调机组NJ-4AP(KT)3-3-自动状态*)"},"LAHU04C03_A             AT%I161.2      :BOOL; (*空调机组NJ-4AP(KT)3-3-自动状态*)",null,"L21\\L21AHU04C03_A","空调机组NJ-4AP(KT)3-3-自动状态",11290]
[{"$nulls":5},12,null,23,24,"空调机组NJ-4AP(KT)3-3-风机压差",{"$nulls":16},"NJ-4AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-3","04C03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU04C03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU04C03_FPS AT%I161.3 :BOOL; (*空调机组NJ-4AP(KT)3-3-风机压差*)"},"LAHU04C03_FPS           AT%I161.3      :BOOL; (*空调机组NJ-4AP(KT)3-3-风机压差*)",null,"L21\\L21AHU04C03_FPS","空调机组NJ-4AP(KT)3-3-风机压差",11291]
[{"$nulls":5},13,null,25,26,"空调机组NJ-4AP(KT)3-4-运行状态",{"$nulls":16},"NJ-4AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-4","04C04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU04C04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU04C04_R AT%I161.4 :BOOL; (*空调机组NJ-4AP(KT)3-4-运行状态*)"},"LAHU04C04_R             AT%I161.4      :BOOL; (*空调机组NJ-4AP(KT)3-4-运行状态*)",null,"L21\\L21AHU04C04_R","空调机组NJ-4AP(KT)3-4-运行状态",11292]
[{"$nulls":5},14,null,27,28,"空调机组NJ-4AP(KT)3-4-故障状态",{"$nulls":16},"NJ-4AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-4","04C04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU04C04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU04C04_F AT%I161.5 :BOOL; (*空调机组NJ-4AP(KT)3-4-故障状态*)"},"LAHU04C04_F             AT%I161.5      :BOOL; (*空调机组NJ-4AP(KT)3-4-故障状态*)",null,"L21\\L21AHU04C04_F","空调机组NJ-4AP(KT)3-4-故障状态",11293]
[{"$nulls":5},15,null,29,30,"空调机组NJ-4AP(KT)3-4-自动状态",{"$nulls":16},"NJ-4AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-4","04C04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU04C04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU04C04_A AT%I161.6 :BOOL; (*空调机组NJ-4AP(KT)3-4-自动状态*)"},"LAHU04C04_A             AT%I161.6      :BOOL; (*空调机组NJ-4AP(KT)3-4-自动状态*)",null,"L21\\L21AHU04C04_A","空调机组NJ-4AP(KT)3-4-自动状态",11294]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-4AP(KT)3-4-风机压差",{"$nulls":16},"NJ-4AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-4","04C04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU04C04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU04C04_FPS AT%I161.7 :BOOL; (*空调机组NJ-4AP(KT)3-4-风机压差*)"},"LAHU04C04_FPS           AT%I161.7      :BOOL; (*空调机组NJ-4AP(KT)3-4-风机压差*)",null,"L21\\L21AHU04C04_FPS","空调机组NJ-4AP(KT)3-4-风机压差",11295]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 1601R地址: 11 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH25&AA25&\"-\"&AK25","v":"空调机组NJ-4AP(KT)3-5-运行状态"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-4AP(KT)3-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-5","04C05","运行状态",{"$f":"AH25&\"-\"&AK25","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"AHU04C05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LAHU04C05_R AT%I176.0 :BOOL; (*空调机组NJ-4AP(KT)3-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LAHU04C05_R             AT%I176.0      :BOOL; (*空调机组NJ-4AP(KT)3-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L21\\L21AHU04C05_R"},{"$f":"J25","v":"空调机组NJ-4AP(KT)3-5-运行状态"},{"$f":"10000+($B26*16*8+F25-1)","v":11408}]
[null,11,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},2,null,3,4,"空调机组NJ-4AP(KT)3-5-故障状态",{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-4AP(KT)3-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-5","04C05","故障状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU04C05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU04C05_F AT%I176.1 :BOOL; (*空调机组NJ-4AP(KT)3-5-故障状态*)"},"LAHU04C05_F             AT%I176.1      :BOOL; (*空调机组NJ-4AP(KT)3-5-故障状态*)",null,"L21\\L21AHU04C05_F",{"$f":"J26","v":"空调机组NJ-4AP(KT)3-5-故障状态"},{"$f":"AS25+1","v":11409}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-4AP(KT)3-5-自动状态",{"$nulls":16},"NJ-4AP(KT)3-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-5","04C05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU04C05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU04C05_A AT%I176.2 :BOOL; (*空调机组NJ-4AP(KT)3-5-自动状态*)"},"LAHU04C05_A             AT%I176.2      :BOOL; (*空调机组NJ-4AP(KT)3-5-自动状态*)",null,"L21\\L21AHU04C05_A","空调机组NJ-4AP(KT)3-5-自动状态",{"$f":"AS26+1","v":11410}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-4AP(KT)3-5-风机压差",{"$nulls":16},"NJ-4AP(KT)3-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-5","04C05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU04C05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU04C05_FPS AT%I176.3 :BOOL; (*空调机组NJ-4AP(KT)3-5-风机压差*)"},"LAHU04C05_FPS           AT%I176.3      :BOOL; (*空调机组NJ-4AP(KT)3-5-风机压差*)",null,"L21\\L21AHU04C05_FPS","空调机组NJ-4AP(KT)3-5-风机压差",11411]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-4AP(KT)3-6-运行状态",{"$nulls":16},"NJ-4AP(KT)3-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-6","04C06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU04C06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU04C06_R AT%I176.4 :BOOL; (*空调机组NJ-4AP(KT)3-6-运行状态*)"},"LAHU04C06_R             AT%I176.4      :BOOL; (*空调机组NJ-4AP(KT)3-6-运行状态*)",null,"L21\\L21AHU04C06_R","空调机组NJ-4AP(KT)3-6-运行状态",11412]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-4AP(KT)3-6-故障状态",{"$nulls":16},"NJ-4AP(KT)3-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-6","04C06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU04C06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU04C06_F AT%I176.5 :BOOL; (*空调机组NJ-4AP(KT)3-6-故障状态*)"},"LAHU04C06_F             AT%I176.5      :BOOL; (*空调机组NJ-4AP(KT)3-6-故障状态*)",null,"L21\\L21AHU04C06_F","空调机组NJ-4AP(KT)3-6-故障状态",11413]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-4AP(KT)3-6-自动状态",{"$nulls":16},"NJ-4AP(KT)3-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-6","04C06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU04C06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU04C06_A AT%I176.6 :BOOL; (*空调机组NJ-4AP(KT)3-6-自动状态*)"},"LAHU04C06_A             AT%I176.6      :BOOL; (*空调机组NJ-4AP(KT)3-6-自动状态*)",null,"L21\\L21AHU04C06_A","空调机组NJ-4AP(KT)3-6-自动状态",11414]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-4AP(KT)3-6-风机压差",{"$nulls":16},"NJ-4AP(KT)3-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-6","04C06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU04C06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU04C06_FPS AT%I176.7 :BOOL; (*空调机组NJ-4AP(KT)3-6-风机压差*)"},"LAHU04C06_FPS           AT%I176.7      :BOOL; (*空调机组NJ-4AP(KT)3-6-风机压差*)",null,"L21\\L21AHU04C06_FPS","空调机组NJ-4AP(KT)3-6-风机压差",11415]
[{"$nulls":5},9,null,17,18,"空调机组NJ-4AP(KT)3-7-运行状态",{"$nulls":16},"NJ-4AP(KT)3-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-7","04C07","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU04C07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B26*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU04C07_R AT%I177.0 :BOOL; (*空调机组NJ-4AP(KT)3-7-运行状态*)"},"LAHU04C07_R             AT%I177.0      :BOOL; (*空调机组NJ-4AP(KT)3-7-运行状态*)",null,"L21\\L21AHU04C07_R","空调机组NJ-4AP(KT)3-7-运行状态",11416]
[{"$nulls":5},10,null,19,20,"空调机组NJ-4AP(KT)3-7-故障状态",{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-4AP(KT)3-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-7","04C07","故障状态",{"$f":"AH34&\"-\"&AK34","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU04C07_F"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B26*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU04C07_F AT%I177.1 :BOOL; (*空调机组NJ-4AP(KT)3-7-故障状态*)"},"LAHU04C07_F             AT%I177.1      :BOOL; (*空调机组NJ-4AP(KT)3-7-故障状态*)",null,"L21\\L21AHU04C07_F",{"$f":"J34","v":"空调机组NJ-4AP(KT)3-7-故障状态"},11417]
[{"$nulls":5},11,null,21,22,"空调机组NJ-4AP(KT)3-7-自动状态",{"$nulls":16},"NJ-4AP(KT)3-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-7","04C07","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU04C07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B26*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU04C07_A AT%I177.2 :BOOL; (*空调机组NJ-4AP(KT)3-7-自动状态*)"},"LAHU04C07_A             AT%I177.2      :BOOL; (*空调机组NJ-4AP(KT)3-7-自动状态*)",null,"L21\\L21AHU04C07_A","空调机组NJ-4AP(KT)3-7-自动状态",11418]
[{"$nulls":5},12,null,23,24,"空调机组NJ-4AP(KT)3-7-风机压差",{"$nulls":16},"NJ-4AP(KT)3-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-7","04C07","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU04C07_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B26*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU04C07_FPS AT%I177.3 :BOOL; (*空调机组NJ-4AP(KT)3-7-风机压差*)"},"LAHU04C07_FPS           AT%I177.3      :BOOL; (*空调机组NJ-4AP(KT)3-7-风机压差*)",null,"L21\\L21AHU04C07_FPS","空调机组NJ-4AP(KT)3-7-风机压差",11419]
[{"$nulls":5},13,null,25,26,"空调机组NJ-4AP(KT)3-8-运行状态",{"$nulls":16},"NJ-4AP(KT)3-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-8","04C08","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"AHU04C08_R"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B26*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LAHU04C08_R AT%I177.4 :BOOL; (*空调机组NJ-4AP(KT)3-8-运行状态*)"},"LAHU04C08_R             AT%I177.4      :BOOL; (*空调机组NJ-4AP(KT)3-8-运行状态*)",null,"L21\\L21AHU04C08_R","空调机组NJ-4AP(KT)3-8-运行状态",11420]
[{"$nulls":5},14,null,27,28,"空调机组NJ-4AP(KT)3-8-故障状态",{"$nulls":16},"NJ-4AP(KT)3-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-8","04C08","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"AHU04C08_F"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B26*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LAHU04C08_F AT%I177.5 :BOOL; (*空调机组NJ-4AP(KT)3-8-故障状态*)"},"LAHU04C08_F             AT%I177.5      :BOOL; (*空调机组NJ-4AP(KT)3-8-故障状态*)",null,"L21\\L21AHU04C08_F","空调机组NJ-4AP(KT)3-8-故障状态",11421]
[{"$nulls":5},15,null,29,30,"空调机组NJ-4AP(KT)3-8-自动状态",{"$nulls":16},"NJ-4AP(KT)3-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-8","04C08","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"AHU04C08_A"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B26*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LAHU04C08_A AT%I177.6 :BOOL; (*空调机组NJ-4AP(KT)3-8-自动状态*)"},"LAHU04C08_A             AT%I177.6      :BOOL; (*空调机组NJ-4AP(KT)3-8-自动状态*)",null,"L21\\L21AHU04C08_A","空调机组NJ-4AP(KT)3-8-自动状态",11422]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-4AP(KT)3-8-风机压差",{"$nulls":16},"NJ-4AP(KT)3-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-8","04C08","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"AHU04C08_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B26*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LAHU04C08_FPS AT%I177.7 :BOOL; (*空调机组NJ-4AP(KT)3-8-风机压差*)"},"LAHU04C08_FPS           AT%I177.7      :BOOL; (*空调机组NJ-4AP(KT)3-8-风机压差*)",null,"L21\\L21AHU04C08_FPS","空调机组NJ-4AP(KT)3-8-风机压差",11423]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B46&\"地址: \"&B43&\" *)\"","v":"(* IOM 0801R 地址: 12 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH42&AA42&\"-\"&AK42","v":"空调机组NJ-4AP(KT)3-9-运行状态"},{"$nulls":16},{"$f":"IF(AI42=\"\",\"\",AI42)","v":"NJ-4AP(KT)3-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-9","04C09","运行状态",{"$f":"AH42&\"-\"&AK42","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":"AHU04C09_R"},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%I\"&B43*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":"LAHU04C09_R AT%I192.0 :BOOL; (*空调机组NJ-4AP(KT)3-9-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42))),SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))))),\" \")","v":"LAHU04C09_R             AT%I192.0      :BOOL; (*空调机组NJ-4AP(KT)3-9-运行状态*)"},null,{"$f":"AM42","v":"AHU04C09_R"},{"$f":"J42","v":"空调机组NJ-4AP(KT)3-9-运行状态"},{"$f":"10000+($B43*16*8+F42-1)","v":11536}]
[null,12,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":0},2,null,2,"C",{"$f":"AH43&AA43&\"-\"&AK43","v":"空调机组NJ-4AP(KT)3-9-故障状态"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-4AP(KT)3-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-9","04C09","故障状态",{"$f":"AH43&\"-\"&AK43","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"AHU04C09_F"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B43*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LAHU04C09_F AT%I192.1 :BOOL; (*空调机组NJ-4AP(KT)3-9-故障状态*)"},"LAHU04C09_F             AT%I192.1      :BOOL; (*空调机组NJ-4AP(KT)3-9-故障状态*)",null,{"$f":"AM43","v":"AHU04C09_F"},{"$f":"J43","v":"空调机组NJ-4AP(KT)3-9-故障状态"},{"$f":"AS42+1","v":11537}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":1},3,null,3,"C",{"$f":"AH44&AA44&\"-\"&AK44","v":"空调机组NJ-4AP(KT)3-9-自动状态"},{"$nulls":16},"NJ-4AP(KT)3-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-9","04C09","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"AHU04C09_A"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B43*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LAHU04C09_A AT%I192.2 :BOOL; (*空调机组NJ-4AP(KT)3-9-自动状态*)"},"LAHU04C09_A             AT%I192.2      :BOOL; (*空调机组NJ-4AP(KT)3-9-自动状态*)",null,"AHU04C09_A","空调机组NJ-4AP(KT)3-9-自动状态",{"$f":"AS43+1","v":11538}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},4,null,4,"C",{"$f":"AH45&AA45&\"-\"&AK45","v":"空调机组NJ-4AP(KT)3-9-风机压差"},{"$nulls":16},"NJ-4AP(KT)3-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-9","04C09","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"AHU04C09_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B43*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LAHU04C09_FPS AT%I192.3 :BOOL; (*空调机组NJ-4AP(KT)3-9-风机压差*)"},"LAHU04C09_FPS           AT%I192.3      :BOOL; (*空调机组NJ-4AP(KT)3-9-风机压差*)",null,"AHU04C09_FPS","空调机组NJ-4AP(KT)3-9-风机压差",11539]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},5,null,5,"C","照明控制箱NJ-4AL3-1-运行状态",{"$nulls":16},"NJ-4AL3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL3-1","04C01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"LCB04C01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B43*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LLCB04C01_R AT%I192.4 :BOOL; (*照明控制箱NJ-4AL3-1-运行状态*)"},"LLCB04C01_R             AT%I192.4      :BOOL; (*照明控制箱NJ-4AL3-1-运行状态*)",null,"LCB04C01_R","照明控制箱NJ-4AL3-1-运行状态",11540]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","照明控制箱NJ-4AL3-1-自动状态",{"$nulls":16},"NJ-4AL3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL3-1","04C01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"LCB04C01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B43*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LLCB04C01_A AT%I192.5 :BOOL; (*照明控制箱NJ-4AL3-1-自动状态*)"},"LLCB04C01_A             AT%I192.5      :BOOL; (*照明控制箱NJ-4AL3-1-自动状态*)",null,"LCB04C01_A","照明控制箱NJ-4AL3-1-自动状态",11541]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B43*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11542]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B43*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11543]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B55&\"地址: \"&B52&\" *)\"","v":"(* IOM 1601D地址: 13 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH51&AA51&\"-\"&AK51","v":"空调机组NJ-4AP(KT)3-1-启停控制"},{"$nulls":16},{"$f":"IF(AI51=\"\",\"\",AI51)","v":"NJ-4AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-1","04C01","启停控制",{"$f":"AH51&\"-\"&AK51","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"AHU04C01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%Q\"&B52*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LAHU04C01_C AT%Q208.0 :BOOL; (*空调机组NJ-4AP(KT)3-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN51,SEARCH(\"AT%\",AN51),,REPT(\" \",25-SEARCH(\"AT%\",AN51))),SEARCH(\":\",REPLACE(AN51,SEARCH(\"AT%\",AN51),,REPT(\" \",25-SEARCH(\"AT%\",AN51)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN51,SEARCH(\"AT%\",AN51),,REPT(\" \",25-SEARCH(\"AT%\",AN51)))))),\" \")","v":"LAHU04C01_C             AT%Q208.0      :BOOL; (*空调机组NJ-4AP(KT)3-1-启停控制*)"},null,{"$f":"AM51","v":"AHU04C01_C"},{"$f":"J51","v":"空调机组NJ-4AP(KT)3-1-启停控制"},{"$f":"($B52*16*8+F51-1)","v":1664}]
[null,13,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","空调机组NJ-4AP(KT)3-2-启停控制",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-4AP(KT)3-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-2","04C02","启停控制",{"$f":"AH52&\"-\"&AK52","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"AHU04C02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%Q\"&B52*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LAHU04C02_C AT%Q208.1 :BOOL; (*空调机组NJ-4AP(KT)3-2-启停控制*)"},"LAHU04C02_C             AT%Q208.1      :BOOL; (*空调机组NJ-4AP(KT)3-2-启停控制*)",null,"AHU04C02_C",{"$f":"J52","v":"空调机组NJ-4AP(KT)3-2-启停控制"},{"$f":"AS51+1","v":1665}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-4AP(KT)3-3-启停控制",{"$nulls":16},"NJ-4AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-3","04C03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"AHU04C03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%Q\"&B52*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LAHU04C03_C AT%Q208.2 :BOOL; (*空调机组NJ-4AP(KT)3-3-启停控制*)"},"LAHU04C03_C             AT%Q208.2      :BOOL; (*空调机组NJ-4AP(KT)3-3-启停控制*)",null,"AHU04C03_C","空调机组NJ-4AP(KT)3-3-启停控制",{"$f":"AS52+1","v":1666}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","空调机组NJ-4AP(KT)3-4-启停控制",{"$nulls":16},"NJ-4AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-4","04C04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"AHU04C04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%Q\"&B52*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LAHU04C04_C AT%Q208.3 :BOOL; (*空调机组NJ-4AP(KT)3-4-启停控制*)"},"LAHU04C04_C             AT%Q208.3      :BOOL; (*空调机组NJ-4AP(KT)3-4-启停控制*)",null,"AHU04C04_C","空调机组NJ-4AP(KT)3-4-启停控制",1667]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-4AP(KT)3-5-启停控制",{"$nulls":16},"NJ-4AP(KT)3-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-5","04C05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"AHU04C05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%Q\"&B52*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LAHU04C05_C AT%Q208.4 :BOOL; (*空调机组NJ-4AP(KT)3-5-启停控制*)"},"LAHU04C05_C             AT%Q208.4      :BOOL; (*空调机组NJ-4AP(KT)3-5-启停控制*)",null,"AHU04C05_C","空调机组NJ-4AP(KT)3-5-启停控制",1668]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-4AP(KT)3-6-启停控制",{"$nulls":16},"NJ-4AP(KT)3-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-6","04C06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"AHU04C06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%Q\"&B52*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LAHU04C06_C AT%Q208.5 :BOOL; (*空调机组NJ-4AP(KT)3-6-启停控制*)"},"LAHU04C06_C             AT%Q208.5      :BOOL; (*空调机组NJ-4AP(KT)3-6-启停控制*)",null,"AHU04C06_C","空调机组NJ-4AP(KT)3-6-启停控制",1669]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","空调机组NJ-4AP(KT)3-7-启停控制",{"$nulls":16},"NJ-4AP(KT)3-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-7","04C07","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"AHU04C07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%Q\"&B52*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LAHU04C07_C AT%Q208.6 :BOOL; (*空调机组NJ-4AP(KT)3-7-启停控制*)"},"LAHU04C07_C             AT%Q208.6      :BOOL; (*空调机组NJ-4AP(KT)3-7-启停控制*)",null,"AHU04C07_C","空调机组NJ-4AP(KT)3-7-启停控制",1670]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","空调机组NJ-4AP(KT)3-8-启停控制",{"$nulls":16},"NJ-4AP(KT)3-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-8","04C08","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":"AHU04C08_C"},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%Q\"&B52*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":"LAHU04C08_C AT%Q208.7 :BOOL; (*空调机组NJ-4AP(KT)3-8-启停控制*)"},"LAHU04C08_C             AT%Q208.7      :BOOL; (*空调机组NJ-4AP(KT)3-8-启停控制*)",null,"AHU04C08_C","空调机组NJ-4AP(KT)3-8-启停控制",1671]
[{"$nulls":5},9,null,"9+","9-","空调机组NJ-4AP(KT)3-9-启停控制",{"$nulls":16},"NJ-4AP(KT)3-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-9","04C09","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH59,List!$B$3:$D$445,2,FALSE)&AJ59&\"_\"&VLOOKUP(AK59,List!$K$2:$M$447,2,FALSE)","v":"AHU04C09_C"},{"$f":"_xlfn.IFNA(\"L\"&AM59&\" \"&\"AT%Q\"&B52*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J59&\"*)\",\" \")","v":"LAHU04C09_C AT%Q209.0 :BOOL; (*空调机组NJ-4AP(KT)3-9-启停控制*)"},"LAHU04C09_C             AT%Q209.0      :BOOL; (*空调机组NJ-4AP(KT)3-9-启停控制*)",null,"AHU04C09_C","空调机组NJ-4AP(KT)3-9-启停控制",1672]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-4AL3-1-启停控制",{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-4AL3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL3-1","04C01","启停控制",{"$f":"AH60&\"-\"&AK60","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"LCB04C01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%Q\"&B52*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LLCB04C01_C AT%Q209.1 :BOOL; (*照明控制箱NJ-4AL3-1-启停控制*)"},"LLCB04C01_C             AT%Q209.1      :BOOL; (*照明控制箱NJ-4AL3-1-启停控制*)",null,"LCB04C01_C",{"$f":"J60","v":"照明控制箱NJ-4AL3-1-启停控制"},1673]
[{"$nulls":5},11,null,"11+","11-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%Q\"&B52*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1674]
[{"$nulls":5},12,null,"12+","12-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%Q\"&B52*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1675]
[{"$nulls":5},13,null,"13+","13-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%Q\"&B52*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1676]
[{"$nulls":5},14,null,"14+","14-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%Q\"&B52*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1677]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%Q\"&B52*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1678]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%Q\"&B52*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1679]
[null,{"$f":"B72","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B72&\"地址: \"&B69&\" *)\"","v":"(* IOM 0801U地址: 14 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH68&AA68&\"-\"&AK68","v":"空调机组NJ-4AP(KT)3-1-回风温度"},{"$nulls":16},{"$f":"IF(AI68=\"\",\"\",AI68)","v":"NJ-4AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-1","04C01","回风温度",{"$f":"AH68&\"-\"&AK68","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"AHU04C01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%I\"&B69*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LAHU04C01_RT AT%I224.0 :INT ; (*空调机组NJ-4AP(KT)3-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68))),SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))))),\" \")","v":"LAHU04C01_RT            AT%I224.0      :INT ; (*空调机组NJ-4AP(KT)3-1-回风温度*)"},null,{"$f":"AM68","v":"AHU04C01_RT"},{"$f":"J68","v":"空调机组NJ-4AP(KT)3-1-回风温度"},{"$f":"30000+($B69*8+F68-1)","v":30112}]
[null,14,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-4AP(KT)3-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-4AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-1","04C01","水阀反馈",{"$f":"AH69&\"-\"&AK69","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU04C01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%I\"&B69*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU04C01_WVB AT%I226.0 :INT ; (*空调机组NJ-4AP(KT)3-1-水阀反馈*)"},"LAHU04C01_WVB           AT%I226.0      :INT ; (*空调机组NJ-4AP(KT)3-1-水阀反馈*)",null,"AHU04C01_WVB",{"$f":"J69","v":"空调机组NJ-4AP(KT)3-1-水阀反馈"},{"$f":"AS68+1","v":30113}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-4AP(KT)3-2-回风温度",{"$nulls":16},"NJ-4AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-2","04C02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"AHU04C02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%I\"&B69*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LAHU04C02_RT AT%I228.0 :INT ; (*空调机组NJ-4AP(KT)3-2-回风温度*)"},"LAHU04C02_RT            AT%I228.0      :INT ; (*空调机组NJ-4AP(KT)3-2-回风温度*)",null,"AHU04C02_RT","空调机组NJ-4AP(KT)3-2-回风温度",{"$f":"AS69+1","v":30114}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-4AP(KT)3-2-水阀反馈",{"$nulls":16},"NJ-4AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-2","04C02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"AHU04C02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%I\"&B69*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LAHU04C02_WVB AT%I230.0 :INT ; (*空调机组NJ-4AP(KT)3-2-水阀反馈*)"},"LAHU04C02_WVB           AT%I230.0      :INT ; (*空调机组NJ-4AP(KT)3-2-水阀反馈*)",null,"AHU04C02_WVB","空调机组NJ-4AP(KT)3-2-水阀反馈",30115]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-4AP(KT)3-3-回风温度",{"$nulls":16},"NJ-4AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-3","04C03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"AHU04C03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%I\"&B69*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LAHU04C03_RT AT%I232.0 :INT ; (*空调机组NJ-4AP(KT)3-3-回风温度*)"},"LAHU04C03_RT            AT%I232.0      :INT ; (*空调机组NJ-4AP(KT)3-3-回风温度*)",null,"AHU04C03_RT","空调机组NJ-4AP(KT)3-3-回风温度",30116]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-4AP(KT)3-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI73=\"\",\"\",AI73)","v":"NJ-4AP(KT)3-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-3","04C03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"AHU04C03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%I\"&B69*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LAHU04C03_WVB AT%I234.0 :INT ; (*空调机组NJ-4AP(KT)3-3-水阀反馈*)"},"LAHU04C03_WVB           AT%I234.0      :INT ; (*空调机组NJ-4AP(KT)3-3-水阀反馈*)",null,"AHU04C03_WVB",{"$f":"J73","v":"空调机组NJ-4AP(KT)3-3-水阀反馈"},30117]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-4AP(KT)3-4-回风温度",{"$nulls":16},"NJ-4AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-4","04C04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":"AHU04C04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%I\"&B69*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":"LAHU04C04_RT AT%I236.0 :INT ; (*空调机组NJ-4AP(KT)3-4-回风温度*)"},"LAHU04C04_RT            AT%I236.0      :INT ; (*空调机组NJ-4AP(KT)3-4-回风温度*)",null,"AHU04C04_RT","空调机组NJ-4AP(KT)3-4-回风温度",30118]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-4AP(KT)3-4-水阀反馈",{"$nulls":16},"NJ-4AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-4","04C04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":"AHU04C04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%I\"&B69*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":"LAHU04C04_WVB AT%I238.0 :INT ; (*空调机组NJ-4AP(KT)3-4-水阀反馈*)"},"LAHU04C04_WVB           AT%I238.0      :INT ; (*空调机组NJ-4AP(KT)3-4-水阀反馈*)",null,"AHU04C04_WVB","空调机组NJ-4AP(KT)3-4-水阀反馈",30119]
[null,{"$f":"B81","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B81&\"地址: \"&B78&\" *)\"","v":"(* IOM 0801U地址: 15 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH77&AA77&\"-\"&AK77","v":"空调机组NJ-4AP(KT)3-5-回风温度"},{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-4AP(KT)3-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-5","04C05","回风温度",{"$f":"AH77&\"-\"&AK77","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"AHU04C05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%I\"&B78*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LAHU04C05_RT AT%I240.0 :INT ; (*空调机组NJ-4AP(KT)3-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77))),SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))))),\" \")","v":"LAHU04C05_RT            AT%I240.0      :INT ; (*空调机组NJ-4AP(KT)3-5-回风温度*)"},null,{"$f":"AM77","v":"AHU04C05_RT"},{"$f":"J77","v":"空调机组NJ-4AP(KT)3-5-回风温度"},{"$f":"30000+($B78*8+F77-1)","v":30120}]
[null,15,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-4AP(KT)3-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-4AP(KT)3-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-5","04C05","水阀反馈",{"$f":"AH78&\"-\"&AK78","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU04C05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%I\"&B78*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU04C05_WVB AT%I242.0 :INT ; (*空调机组NJ-4AP(KT)3-5-水阀反馈*)"},"LAHU04C05_WVB           AT%I242.0      :INT ; (*空调机组NJ-4AP(KT)3-5-水阀反馈*)",null,"AHU04C05_WVB",{"$f":"J78","v":"空调机组NJ-4AP(KT)3-5-水阀反馈"},{"$f":"AS77+1","v":30121}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-4AP(KT)3-6-回风温度",{"$nulls":16},"NJ-4AP(KT)3-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-6","04C06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU04C06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%I\"&B78*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU04C06_RT AT%I244.0 :INT ; (*空调机组NJ-4AP(KT)3-6-回风温度*)"},"LAHU04C06_RT            AT%I244.0      :INT ; (*空调机组NJ-4AP(KT)3-6-回风温度*)",null,"AHU04C06_RT","空调机组NJ-4AP(KT)3-6-回风温度",{"$f":"AS78+1","v":30122}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-4AP(KT)3-6-水阀反馈",{"$nulls":16},"NJ-4AP(KT)3-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-6","04C06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU04C06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%I\"&B78*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU04C06_WVB AT%I246.0 :INT ; (*空调机组NJ-4AP(KT)3-6-水阀反馈*)"},"LAHU04C06_WVB           AT%I246.0      :INT ; (*空调机组NJ-4AP(KT)3-6-水阀反馈*)",null,"AHU04C06_WVB","空调机组NJ-4AP(KT)3-6-水阀反馈",30123]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},5,null,5,"0V","室内环境状态T-04-温度状态",{"$nulls":16},"T-04",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","T-04","04C01","温度状态","室内环境状态-温度状态",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"IES04C01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%I\"&B78*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LIES04C01_T AT%I248.0 :INT ; (*室内环境状态T-04-温度状态*)"},"LIES04C01_T             AT%I248.0      :INT ; (*室内环境状态T-04-温度状态*)",null,"IES04C01_T","室内环境状态T-04-温度状态",30124]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","室内环境状态CO2-03-二氧化碳浓度状态",{"$nulls":16},"CO2-03",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","CO2-03","04C01","二氧化碳浓度状态","室内环境状态-二氧化碳浓度状态",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":"IES04C01_CO2"},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%I\"&B78*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":"LIES04C01_CO2 AT%I250.0 :INT ; (*室内环境状态CO2-03-二氧化碳浓度状态*)"},"LIES04C01_CO2           AT%I250.0      :INT ; (*室内环境状态CO2-03-二氧化碳浓度状态*)",null,"IES04C01_CO2",{"$f":"J82","v":"室内环境状态CO2-03-二氧化碳浓度状态"},30125]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%I\"&B78*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30126]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},{"$f":"IF(AI84=\"\",\"\",AI84)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH84,List!$B$3:$D$445,2,FALSE)&AJ84&\"_\"&VLOOKUP(AK84,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM84&\" \"&\"AT%I\"&B78*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J84&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30127]
[null,{"$f":"B90","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B90&\"地址: \"&B87&\" *)\"","v":"(* IOM 0401A地址: 17 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH86&AA86&\"-\"&AK86","v":"空调机组NJ-4AP(KT)3-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-4AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-1","04C01","水阀控制",{"$f":"AH86&\"-\"&AK86","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"AHU04C01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%Q\"&B87*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LAHU04C01_WVC AT%Q272.0 :INT ; (*空调机组NJ-4AP(KT)3-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86))),SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))))),\" \")","v":"LAHU04C01_WVC           AT%Q272.0      :INT ; (*空调机组NJ-4AP(KT)3-1-水阀控制*)"},null,{"$f":"AM86","v":"AHU04C01_WVC"},{"$f":"J86","v":"空调机组NJ-4AP(KT)3-1-水阀控制"},{"$f":"40000+($B87*8+F86-1)","v":40136}]
[null,17,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH87&AA87&\"-\"&AK87","v":"空调机组NJ-4AP(KT)3-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI87=\"\",\"\",AI87)","v":"NJ-4AP(KT)3-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-2","04C02","水阀控制",{"$f":"AH87&\"-\"&AK87","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"AHU04C02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%Q\"&B87*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LAHU04C02_WVC AT%Q274.0 :INT ; (*空调机组NJ-4AP(KT)3-2-水阀控制*)"},"LAHU04C02_WVC           AT%Q274.0      :INT ; (*空调机组NJ-4AP(KT)3-2-水阀控制*)",null,"AHU04C02_WVC",{"$f":"J87","v":"空调机组NJ-4AP(KT)3-2-水阀控制"},{"$f":"AS86+1","v":40137}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH88&AA88&\"-\"&AK88","v":"空调机组NJ-4AP(KT)3-3-水阀控制"},{"$nulls":16},"NJ-4AP(KT)3-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-3","04C03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"AHU04C03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%Q\"&B87*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LAHU04C03_WVC AT%Q276.0 :INT ; (*空调机组NJ-4AP(KT)3-3-水阀控制*)"},"LAHU04C03_WVC           AT%Q276.0      :INT ; (*空调机组NJ-4AP(KT)3-3-水阀控制*)",null,"AHU04C03_WVC","空调机组NJ-4AP(KT)3-3-水阀控制",{"$f":"AS87+1","v":40138}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH89&AA89&\"-\"&AK89","v":"空调机组NJ-4AP(KT)3-4-水阀控制"},{"$nulls":16},"NJ-4AP(KT)3-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-4","04C04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"AHU04C04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%Q\"&B87*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LAHU04C04_WVC AT%Q278.0 :INT ; (*空调机组NJ-4AP(KT)3-4-水阀控制*)"},"LAHU04C04_WVC           AT%Q278.0      :INT ; (*空调机组NJ-4AP(KT)3-4-水阀控制*)",null,"AHU04C04_WVC","空调机组NJ-4AP(KT)3-4-水阀控制",40139]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B99","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B99&\"地址: \"&B96&\" *)\"","v":"(* IOM 0401A地址: 18 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH95&AA95&\"-\"&AK95","v":"空调机组NJ-4AP(KT)3-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-4AP(KT)3-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-5","04C05","水阀控制",{"$f":"AH95&\"-\"&AK95","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"AHU04C05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%Q\"&B96*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LAHU04C05_WVC AT%Q288.0 :INT ; (*空调机组NJ-4AP(KT)3-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95))),SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))))),\" \")","v":"LAHU04C05_WVC           AT%Q288.0      :INT ; (*空调机组NJ-4AP(KT)3-5-水阀控制*)"},null,{"$f":"AM95","v":"AHU04C05_WVC"},{"$f":"J95","v":"空调机组NJ-4AP(KT)3-5-水阀控制"},{"$f":"40000+($B96*8+F95-1)","v":40144}]
[null,18,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH96&AA96&\"-\"&AK96","v":"空调机组NJ-4AP(KT)3-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI96=\"\",\"\",AI96)","v":"NJ-4AP(KT)3-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)3-6","04C06","水阀控制",{"$f":"AH96&\"-\"&AK96","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"AHU04C06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%Q\"&B96*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LAHU04C06_WVC AT%Q290.0 :INT ; (*空调机组NJ-4AP(KT)3-6-水阀控制*)"},"LAHU04C06_WVC           AT%Q290.0      :INT ; (*空调机组NJ-4AP(KT)3-6-水阀控制*)",null,"AHU04C06_WVC",{"$f":"J96","v":"空调机组NJ-4AP(KT)3-6-水阀控制"},{"$f":"AS95+1","v":40145}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH97&AA97&\"-\"&AK97","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%Q\"&B96*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS96+1","v":40146}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH98&AA98&\"-\"&AK98","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%Q\"&B96*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40147]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L507","index":29,"n_rows":50,"n_cols":45,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[4,1,5,1],[11,1,22,1],[28,1,31,1],[37,1,40,1],[46,1,49,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L01",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R D7",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 20 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH8&AA8&\"-\"&AK8","v":"F新风机组NJ-5AP(KT)3-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-5AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-1","05G01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"F新风机组-运行状态"},{"$f":"VLOOKUP(AH8,[1]List!$D$3:$F$527,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LFAU05G01_R AT%I320.0 :BOOL; (*F新风机组NJ-5AP(KT)3-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LFAU05G01_R             AT%I320.0      :BOOL; (*F新风机组NJ-5AP(KT)3-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L01\\L01FAU05G01_R"},{"$f":"J8","v":"F新风机组NJ-5AP(KT)3-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":12560}]
[null,20,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},2,null,2,"C","F新风机组NJ-5AP(KT)3-1-故障状态",{"$nulls":16},"NJ-5AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-1","05G01","故障状态","F新风机组-故障状态",{"$f":"VLOOKUP(AH9,[1]List!$D$3:$F$527,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LFAU05G01_F AT%I320.1 :BOOL; (*F新风机组NJ-5AP(KT)3-1-故障状态*)"},"LFAU05G01_F             AT%I320.1      :BOOL; (*F新风机组NJ-5AP(KT)3-1-故障状态*)",null,"L01\\L01FAU05G01_F","F新风机组NJ-5AP(KT)3-1-故障状态",{"$f":"AS8+1","v":12561}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},3,null,3,"C","F新风机组NJ-5AP(KT)3-1-自动状态",{"$nulls":16},"NJ-5AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-1","05G01","自动状态","F新风机组-自动状态",{"$f":"VLOOKUP(AH10,[1]List!$D$3:$F$527,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LFAU05G01_A AT%I320.2 :BOOL; (*F新风机组NJ-5AP(KT)3-1-自动状态*)"},"LFAU05G01_A             AT%I320.2      :BOOL; (*F新风机组NJ-5AP(KT)3-1-自动状态*)",null,"L01\\L01FAU05G01_A","F新风机组NJ-5AP(KT)3-1-自动状态",12562]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},4,null,4,"C","F新风机组NJ-5AP(KT)3-1-风机压差",{"$nulls":16},"NJ-5AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-1","05G01","风机压差","F新风机组-风机压差",{"$f":"VLOOKUP(AH11,[1]List!$D$3:$F$527,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LFAU05G01_FPS AT%I320.3 :BOOL; (*F新风机组NJ-5AP(KT)3-1-风机压差*)"},"LFAU05G01_FPS           AT%I320.3      :BOOL; (*F新风机组NJ-5AP(KT)3-1-风机压差*)",null,"L01\\L01FAU05G01_FPS","F新风机组NJ-5AP(KT)3-1-风机压差",12563]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},5,null,5,"C","F新风机组NJ-5AP(KT)3-1-初效滤网压差",{"$nulls":16},"NJ-5AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-1","05G01","初效滤网压差","F新风机组-初效滤网压差",{"$f":"VLOOKUP(AH12,[1]List!$D$3:$F$527,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G01_IPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LFAU05G01_IPS AT%I320.4 :BOOL; (*F新风机组NJ-5AP(KT)3-1-初效滤网压差*)"},"LFAU05G01_IPS           AT%I320.4      :BOOL; (*F新风机组NJ-5AP(KT)3-1-初效滤网压差*)",null,"L01\\L01FAU05G01_IPS","F新风机组NJ-5AP(KT)3-1-初效滤网压差",12564]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","F新风机组NJ-5AP(KT)3-1-低温断路开关",{"$nulls":16},"NJ-5AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-1","05G01","低温断路开关","F新风机组-低温断路开关",{"$f":"VLOOKUP(AH13,[1]List!$D$3:$F$527,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G01_AFS"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LFAU05G01_AFS AT%I320.5 :BOOL; (*F新风机组NJ-5AP(KT)3-1-低温断路开关*)"},"LFAU05G01_AFS           AT%I320.5      :BOOL; (*F新风机组NJ-5AP(KT)3-1-低温断路开关*)",null,"L01\\L01FAU05G01_AFS","F新风机组NJ-5AP(KT)3-1-低温断路开关",12565]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","F新风机组NJ-5AP(KT)3-1-新风阀开状态",{"$nulls":16},"NJ-5AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-1","05G01","新风阀开状态","F新风机组-新风阀开状态",{"$f":"VLOOKUP(AH14,[1]List!$D$3:$F$527,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G01_FDOB"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LFAU05G01_FDOB AT%I320.6 :BOOL; (*F新风机组NJ-5AP(KT)3-1-新风阀开状态*)"},"LFAU05G01_FDOB          AT%I320.6      :BOOL; (*F新风机组NJ-5AP(KT)3-1-新风阀开状态*)",null,"L01\\L01FAU05G01_FDOB","F新风机组NJ-5AP(KT)3-1-新风阀开状态",12566]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","F新风机组NJ-5AP(KT)3-1-新风阀关状态",{"$nulls":16},"NJ-5AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-1","05G01","新风阀关状态","F新风机组-新风阀关状态",{"$f":"VLOOKUP(AH15,[1]List!$D$3:$F$527,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G01_FDSB"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LFAU05G01_FDSB AT%I320.7 :BOOL; (*F新风机组NJ-5AP(KT)3-1-新风阀关状态*)"},"LFAU05G01_FDSB          AT%I320.7      :BOOL; (*F新风机组NJ-5AP(KT)3-1-新风阀关状态*)",null,"L01\\L01FAU05G01_FDSB","F新风机组NJ-5AP(KT)3-1-新风阀关状态",12567]
[{"$nulls":5},9,null,9,"C","F新风机组NJ-5AP(KT)3-2-运行状态",{"$nulls":16},"NJ-5AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-2","05G02","运行状态","F新风机组-运行状态",{"$f":"VLOOKUP(AH16,[1]List!$D$3:$F$527,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LFAU05G02_R AT%I321.0 :BOOL; (*F新风机组NJ-5AP(KT)3-2-运行状态*)"},"LFAU05G02_R             AT%I321.0      :BOOL; (*F新风机组NJ-5AP(KT)3-2-运行状态*)",null,"L01\\L01FAU05G02_R","F新风机组NJ-5AP(KT)3-2-运行状态",12568]
[{"$nulls":5},10,null,10,"C","F新风机组NJ-5AP(KT)3-2-故障状态",{"$nulls":16},"NJ-5AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-2","05G02","故障状态","F新风机组-故障状态",{"$f":"VLOOKUP(AH17,[1]List!$D$3:$F$527,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LFAU05G02_F AT%I321.1 :BOOL; (*F新风机组NJ-5AP(KT)3-2-故障状态*)"},"LFAU05G02_F             AT%I321.1      :BOOL; (*F新风机组NJ-5AP(KT)3-2-故障状态*)",null,"L01\\L01FAU05G02_F","F新风机组NJ-5AP(KT)3-2-故障状态",12569]
[{"$nulls":5},11,null,11,"C","F新风机组NJ-5AP(KT)3-2-自动状态",{"$nulls":16},"NJ-5AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-2","05G02","自动状态","F新风机组-自动状态",{"$f":"VLOOKUP(AH18,[1]List!$D$3:$F$527,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LFAU05G02_A AT%I321.2 :BOOL; (*F新风机组NJ-5AP(KT)3-2-自动状态*)"},"LFAU05G02_A             AT%I321.2      :BOOL; (*F新风机组NJ-5AP(KT)3-2-自动状态*)",null,"L01\\L01FAU05G02_A","F新风机组NJ-5AP(KT)3-2-自动状态",12570]
[{"$nulls":5},12,null,12,"C","F新风机组NJ-5AP(KT)3-2-风机压差",{"$nulls":16},"NJ-5AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-2","05G02","风机压差","F新风机组-风机压差",{"$f":"VLOOKUP(AH19,[1]List!$D$3:$F$527,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LFAU05G02_FPS AT%I321.3 :BOOL; (*F新风机组NJ-5AP(KT)3-2-风机压差*)"},"LFAU05G02_FPS           AT%I321.3      :BOOL; (*F新风机组NJ-5AP(KT)3-2-风机压差*)",null,"L01\\L01FAU05G02_FPS","F新风机组NJ-5AP(KT)3-2-风机压差",12571]
[{"$nulls":5},13,null,13,"C","F新风机组NJ-5AP(KT)3-2-初效滤网压差",{"$nulls":16},"NJ-5AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-2","05G02","初效滤网压差","F新风机组-初效滤网压差",{"$f":"VLOOKUP(AH20,[1]List!$D$3:$F$527,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G02_IPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LFAU05G02_IPS AT%I321.4 :BOOL; (*F新风机组NJ-5AP(KT)3-2-初效滤网压差*)"},"LFAU05G02_IPS           AT%I321.4      :BOOL; (*F新风机组NJ-5AP(KT)3-2-初效滤网压差*)",null,"L01\\L01FAU05G02_IPS","F新风机组NJ-5AP(KT)3-2-初效滤网压差",12572]
[{"$nulls":5},14,null,14,"C","F新风机组NJ-5AP(KT)3-2-低温断路开关",{"$nulls":16},"NJ-5AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-2","05G02","低温断路开关","F新风机组-低温断路开关",{"$f":"VLOOKUP(AH21,[1]List!$D$3:$F$527,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G02_AFS"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LFAU05G02_AFS AT%I321.5 :BOOL; (*F新风机组NJ-5AP(KT)3-2-低温断路开关*)"},"LFAU05G02_AFS           AT%I321.5      :BOOL; (*F新风机组NJ-5AP(KT)3-2-低温断路开关*)",null,"L01\\L01FAU05G02_AFS","F新风机组NJ-5AP(KT)3-2-低温断路开关",12573]
[{"$nulls":5},15,null,15,"C","F新风机组NJ-5AP(KT)3-2-新风阀开状态",{"$nulls":16},"NJ-5AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-2","05G02","新风阀开状态","F新风机组-新风阀开状态",{"$f":"VLOOKUP(AH22,[1]List!$D$3:$F$527,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G02_FDOB"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LFAU05G02_FDOB AT%I321.6 :BOOL; (*F新风机组NJ-5AP(KT)3-2-新风阀开状态*)"},"LFAU05G02_FDOB          AT%I321.6      :BOOL; (*F新风机组NJ-5AP(KT)3-2-新风阀开状态*)",null,"L01\\L01FAU05G02_FDOB","F新风机组NJ-5AP(KT)3-2-新风阀开状态",12574]
[".",{"$nulls":4},16,null,16,"C","F新风机组NJ-5AP(KT)3-2-新风阀关状态",{"$nulls":16},"NJ-5AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-2","05G02","新风阀关状态","F新风机组-新风阀关状态",{"$f":"VLOOKUP(AH23,[1]List!$D$3:$F$527,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G02_FDSB"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LFAU05G02_FDSB AT%I321.7 :BOOL; (*F新风机组NJ-5AP(KT)3-2-新风阀关状态*)"},"LFAU05G02_FDSB          AT%I321.7      :BOOL; (*F新风机组NJ-5AP(KT)3-2-新风阀关状态*)",null,"L01\\L01FAU05G02_FDSB","F新风机组NJ-5AP(KT)3-2-新风阀关状态",12575]
[null,{"$f":"B29","v":"IOM 0801D"},{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 0801D地址: 21 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH25&AA25&\"-\"&AK25","v":"F新风机组NJ-5AP(KT)3-1-启停控制"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-5AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-1","05G01","启停控制",{"$f":"AH25&\"-\"&AK25","v":"F新风机组-启停控制"},{"$f":"VLOOKUP(AH25,[1]List!$D$3:$F$527,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%Q\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LFAU05G01_C AT%Q336.0 :BOOL; (*F新风机组NJ-5AP(KT)3-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LFAU05G01_C             AT%Q336.0      :BOOL; (*F新风机组NJ-5AP(KT)3-1-启停控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L01\\L01FAU05G01_C"},{"$f":"J25","v":"F新风机组NJ-5AP(KT)3-1-启停控制"},{"$f":"($B26*16*8+F25-1)","v":2688}]
[null,21,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","F新风机组NJ-5AP(KT)3-1-新风阀开控制",{"$nulls":16},"NJ-5AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-1","05G01","新风阀开控制","F新风机组-新风阀开控制",{"$f":"VLOOKUP(AH26,[1]List!$D$3:$F$527,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G01_FDOC"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%Q\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LFAU05G01_FDOC AT%Q336.1 :BOOL; (*F新风机组NJ-5AP(KT)3-1-新风阀开控制*)"},"LFAU05G01_FDOC          AT%Q336.1      :BOOL; (*F新风机组NJ-5AP(KT)3-1-新风阀开控制*)",null,"L01\\L01FAU05G01_FDOC","F新风机组NJ-5AP(KT)3-1-新风阀开控制",{"$f":"AS25+1","v":2689}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","F新风机组NJ-5AP(KT)3-1-新风阀关控制",{"$nulls":16},"NJ-5AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-1","05G01","新风阀关控制","F新风机组-新风阀关控制",{"$f":"VLOOKUP(AH27,[1]List!$D$3:$F$527,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G01_FDSC"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%Q\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LFAU05G01_FDSC AT%Q336.2 :BOOL; (*F新风机组NJ-5AP(KT)3-1-新风阀关控制*)"},"LFAU05G01_FDSC          AT%Q336.2      :BOOL; (*F新风机组NJ-5AP(KT)3-1-新风阀关控制*)",null,"L01\\L01FAU05G01_FDSC","F新风机组NJ-5AP(KT)3-1-新风阀关控制",2690]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","F新风机组NJ-5AP(KT)3-2-启停控制",{"$nulls":16},"NJ-5AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-2","05G02","启停控制","F新风机组-启停控制",{"$f":"VLOOKUP(AH28,[1]List!$D$3:$F$527,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%Q\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LFAU05G02_C AT%Q336.3 :BOOL; (*F新风机组NJ-5AP(KT)3-2-启停控制*)"},"LFAU05G02_C             AT%Q336.3      :BOOL; (*F新风机组NJ-5AP(KT)3-2-启停控制*)",null,"L01\\L01FAU05G02_C","F新风机组NJ-5AP(KT)3-2-启停控制",2691]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":1},5,null,"5+","5-","F新风机组NJ-5AP(KT)3-2-新风阀开控制",{"$nulls":16},"NJ-5AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-2","05G02","新风阀开控制","F新风机组-新风阀开控制",{"$f":"VLOOKUP(AH29,[1]List!$D$3:$F$527,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G02_FDOC"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%Q\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LFAU05G02_FDOC AT%Q336.4 :BOOL; (*F新风机组NJ-5AP(KT)3-2-新风阀开控制*)"},"LFAU05G02_FDOC          AT%Q336.4      :BOOL; (*F新风机组NJ-5AP(KT)3-2-新风阀开控制*)",null,"L01\\L01FAU05G02_FDOC","F新风机组NJ-5AP(KT)3-2-新风阀开控制",2692]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","F新风机组NJ-5AP(KT)3-2-新风阀关控制",{"$nulls":16},"NJ-5AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-2","05G02","新风阀关控制","F新风机组-新风阀关控制",{"$f":"VLOOKUP(AH30,[1]List!$D$3:$F$527,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G02_FDSC"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%Q\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LFAU05G02_FDSC AT%Q336.5 :BOOL; (*F新风机组NJ-5AP(KT)3-2-新风阀关控制*)"},"LFAU05G02_FDSC          AT%Q336.5      :BOOL; (*F新风机组NJ-5AP(KT)3-2-新风阀关控制*)",null,"L01\\L01FAU05G02_FDSC","F新风机组NJ-5AP(KT)3-2-新风阀关控制",2693]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH31,[1]List!$D$3:$F$527,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%Q\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN31,SEARCH(\"AT%\",AN31),,REPT(\" \",30-SEARCH(\"AT%\",AN31))),SEARCH(\":\",REPLACE(AN31,SEARCH(\"AT%\",AN31),,REPT(\" \",30-SEARCH(\"AT%\",AN31)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN31,SEARCH(\"AT%\",AN31),,REPT(\" \",25-SEARCH(\"AT%\",AN31)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",2694]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH32,[1]List!$D$3:$F$527,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%Q\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2695]
[null,{"$f":"B38","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B38&\"地址: \"&B35&\" *)\"","v":"(* IOM 0801U地址: 22 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH34&AA34&\"-\"&AK34","v":"F新风机组NJ-5AP(KT)3-1-送风温度"},{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-5AP(KT)3-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,[2]List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,[2]List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"F新风机组","NJ-5AP(KT)3-1","05G01","送风温度",{"$f":"AH34&\"-\"&AK34","v":"F新风机组-送风温度"},{"$f":"VLOOKUP(AH34,[2]List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,[2]List!$K$2:$M$447,2,FALSE)","v":"FAU05G01_ST"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B35*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LFAU05G01_ST AT%I352.0 :INT ; (*F新风机组NJ-5AP(KT)3-1-送风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34))),SEARCH(\":\",REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34)))))),\" \")","v":"LFAU05G01_ST            AT%I352.0      :INT ; (*F新风机组NJ-5AP(KT)3-1-送风温度*)"},null,{"$f":"AM34","v":"FAU05G01_ST"},{"$f":"J34","v":"F新风机组NJ-5AP(KT)3-1-送风温度"},{"$f":"30000+($B35*8+F34-1)","v":30176}]
[null,22,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),4,1))","v":1},2,null,2,"0V","F新风机组NJ-5AP(KT)3-1-水阀反馈",{"$nulls":16},"NJ-5AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[2]List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[2]List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"F新风机组","NJ-5AP(KT)3-1","05G01","水阀反馈","F新风机组-水阀反馈",{"$f":"VLOOKUP(AH35,[2]List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,[2]List!$K$2:$M$447,2,FALSE)","v":"FAU05G01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B35*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LFAU05G01_WVB AT%I354.0 :INT ; (*F新风机组NJ-5AP(KT)3-1-水阀反馈*)"},"LFAU05G01_WVB           AT%I354.0      :INT ; (*F新风机组NJ-5AP(KT)3-1-水阀反馈*)",null,"FAU05G01_WVB","F新风机组NJ-5AP(KT)3-1-水阀反馈",{"$f":"AS34+1","v":30177}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),3,1))","v":1},3,null,3,"0V","F新风机组NJ-5AP(KT)3-1-变频器频率反馈",{"$nulls":16},"NJ-5AP(KT)3-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[2]List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[2]List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"F新风机组","NJ-5AP(KT)3-1","05G01","变频器频率反馈","F新风机组-变频器频率反馈",{"$f":"VLOOKUP(AH36,[2]List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,[2]List!$K$2:$M$447,2,FALSE)","v":"FAU05G01_VFB"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B35*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LFAU05G01_VFB AT%I356.0 :INT ; (*F新风机组NJ-5AP(KT)3-1-变频器频率反馈*)"},"LFAU05G01_VFB           AT%I356.0      :INT ; (*F新风机组NJ-5AP(KT)3-1-变频器频率反馈*)",null,"FAU05G01_VFB","F新风机组NJ-5AP(KT)3-1-变频器频率反馈",30178]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),2,1))","v":0},4,null,4,"0V","F新风机组NJ-5AP(KT)3-2-送风温度",{"$nulls":16},"NJ-5AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[2]List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[2]List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"F新风机组","NJ-5AP(KT)3-2","05G02","送风温度","F新风机组-送风温度",{"$f":"VLOOKUP(AH37,[2]List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,[2]List!$K$2:$M$447,2,FALSE)","v":"FAU05G02_ST"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B35*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LFAU05G02_ST AT%I358.0 :INT ; (*F新风机组NJ-5AP(KT)3-2-送风温度*)"},"LFAU05G02_ST            AT%I358.0      :INT ; (*F新风机组NJ-5AP(KT)3-2-送风温度*)",null,"FAU05G02_ST","F新风机组NJ-5AP(KT)3-2-送风温度",30179]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),1,1))","v":1},5,null,5,"0V","F新风机组NJ-5AP(KT)3-2-水阀反馈",{"$nulls":16},"NJ-5AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[2]List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[2]List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"F新风机组","NJ-5AP(KT)3-2","05G02","水阀反馈","F新风机组-水阀反馈",{"$f":"VLOOKUP(AH38,[2]List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,[2]List!$K$2:$M$447,2,FALSE)","v":"FAU05G02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B35*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LFAU05G02_WVB AT%I360.0 :INT ; (*F新风机组NJ-5AP(KT)3-2-水阀反馈*)"},"LFAU05G02_WVB           AT%I360.0      :INT ; (*F新风机组NJ-5AP(KT)3-2-水阀反馈*)",null,"FAU05G02_WVB","F新风机组NJ-5AP(KT)3-2-水阀反馈",30180]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","F新风机组NJ-5AP(KT)3-2-变频器频率反馈",{"$nulls":16},"NJ-5AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,[2]List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,[2]List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"F新风机组","NJ-5AP(KT)3-2","05G02","变频器频率反馈","F新风机组-变频器频率反馈",{"$f":"VLOOKUP(AH39,[2]List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,[2]List!$K$2:$M$447,2,FALSE)","v":"FAU05G02_VFB"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B35*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LFAU05G02_VFB AT%I362.0 :INT ; (*F新风机组NJ-5AP(KT)3-2-变频器频率反馈*)"},"LFAU05G02_VFB           AT%I362.0      :INT ; (*F新风机组NJ-5AP(KT)3-2-变频器频率反馈*)",null,"FAU05G02_VFB","F新风机组NJ-5AP(KT)3-2-变频器频率反馈",30181]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,[2]List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,[2]List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH40,[2]List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,[2]List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B35*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30182]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,[2]List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,[2]List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH41,[2]List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,[2]List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%I\"&B35*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30183]
[null,{"$f":"B47","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 0401A地址: 23 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH43&AA43&\"-\"&AK43","v":"F新风机组NJ-5AP(KT)51-水阀控制"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-5AP(KT)51"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)51","05G01","水阀控制",{"$f":"AH43&\"-\"&AK43","v":"F新风机组-水阀控制"},{"$f":"VLOOKUP(AH43,[1]List!$D$3:$F$527,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%Q\"&B44*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LFAU05G01_WVC AT%Q368.0 :INT; (*F新风机组NJ-5AP(KT)51-水阀控制*)"},"LFAU05G01_WVC           AT%Q368.0      :INT; (*F新风机组NJ-5AP(KT)51-水阀控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM43","v":"L01\\L01FAU05G01_WVC"},{"$f":"J43","v":"F新风机组NJ-5AP(KT)51-水阀控制"},{"$f":"40000+($B44*8+F43-1)","v":40184}]
[null,23,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},2,null,3,4,"F新风机组NJ-5AP(KT)51-变频器频率控制",{"$nulls":16},"NJ-5AP(KT)51",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)51","05G01","变频器频率控制","F新风机组-变频器频率控制",{"$f":"VLOOKUP(AH44,[1]List!$D$3:$F$527,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G01_VFC"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%Q\"&B44*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LFAU05G01_VFC AT%Q370.0 :INT; (*F新风机组NJ-5AP(KT)51-变频器频率控制*)"},"LFAU05G01_VFC           AT%Q370.0      :INT; (*F新风机组NJ-5AP(KT)51-变频器频率控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM44","v":"L01\\L01FAU05G01_VFC"},"F新风机组NJ-5AP(KT)51-变频器频率控制",{"$f":"AS43+1","v":40185}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":1},3,null,5,6,"F新风机组NJ-5AP(KT)3-2-水阀控制",{"$nulls":16},"NJ-5AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-2","05G02","水阀控制","F新风机组-水阀控制",{"$f":"VLOOKUP(AH45,[1]List!$D$3:$F$527,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%Q\"&B44*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LFAU05G02_WVC AT%Q372.0 :INT; (*F新风机组NJ-5AP(KT)3-2-水阀控制*)"},"LFAU05G02_WVC           AT%Q372.0      :INT; (*F新风机组NJ-5AP(KT)3-2-水阀控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM45","v":"L01\\L01FAU05G02_WVC"},"F新风机组NJ-5AP(KT)3-2-水阀控制",40186]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},4,null,7,8,"F新风机组NJ-5AP(KT)3-2-变频器频率控制",{"$nulls":16},"NJ-5AP(KT)3-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)3-2","05G02","变频器频率控制","F新风机组-变频器频率控制",{"$f":"VLOOKUP(AH46,[1]List!$D$3:$F$527,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05G02_VFC"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%Q\"&B44*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LFAU05G02_VFC AT%Q374.0 :INT; (*F新风机组NJ-5AP(KT)3-2-变频器频率控制*)"},"LFAU05G02_VFC           AT%Q374.0      :INT; (*F新风机组NJ-5AP(KT)3-2-变频器频率控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM46","v":"L01\\L01FAU05G02_VFC"},"F新风机组NJ-5AP(KT)3-2-变频器频率控制",40187]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L304","index":30,"n_rows":155,"n_cols":45,"rows_kept":155,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[6,1,6,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[84,5,84,6],[84,9,84,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[93,5,93,6],[93,9,93,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[102,5,102,6],[102,9,102,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[109,5,109,6],[109,9,109,25],[111,5,111,6],[111,9,111,25],[112,5,112,6],[112,9,112,25],[113,5,113,6],[113,9,113,25],[114,5,114,6],[114,9,114,25],[115,5,115,6],[115,9,115,25],[116,5,116,6],[116,9,116,25],[117,5,117,6],[117,9,117,25],[118,5,118,6],[118,9,118,25],[120,5,120,6],[120,9,120,25],[121,5,121,6],[121,9,121,25],[122,5,122,6],[122,9,122,25],[123,5,123,6],[123,9,123,25],[124,5,124,6],[124,9,124,25],[125,5,125,6],[125,9,125,25],[126,5,126,6],[126,9,126,25],[127,5,127,6],[127,9,127,25],[129,5,129,6],[129,9,129,25],[130,5,130,6],[130,9,130,25],[131,5,131,6],[131,9,131,25],[132,5,132,6],[132,9,132,25],[133,5,133,6],[133,9,133,25],[134,5,134,6],[134,9,134,25],[135,5,135,6],[135,9,135,25],[136,5,136,6],[136,9,136,25],[138,5,138,6],[138,9,138,25],[139,5,139,6],[139,9,139,25],[140,5,140,6],[140,9,140,25],[141,5,141,6],[141,9,141,25],[142,5,142,6],[142,9,142,25],[143,5,143,6],[143,9,143,25],[144,5,144,6],[144,9,144,25],[145,5,145,6],[145,9,145,25],[147,5,147,6],[147,9,147,25],[148,5,148,6],[148,9,148,25],[149,5,149,6],[149,9,149,25],[150,5,150,6],[150,9,150,25],[151,5,151,6],[151,9,151,25],[152,5,152,6],[152,9,152,25],[153,5,153,6],[153,9,153,25],[154,5,154,6],[154,9,154,25],[4,1,5,1],[12,1,23,1],[29,1,40,1],[46,1,57,1],[63,1,74,1],[80,1,91,1],[97,1,100,1],[106,1,109,1],[115,1,118,1],[124,1,127,1],[133,1,136,1],[142,1,145,1],[151,1,154,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[16,2,23,4],[33,2,40,4],[50,2,57,4],[84,2,91,4],[67,2,74,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L22",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"EXC-1000"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B13&\"地址: \"&B10&\" *)\"","v":"(* IOM 1601R地址: 0 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH9&AA9&\"-\"&AK9","v":"空调机组NJ-3AP(KT)4-1-运行状态"},{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-3AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-1","03D01","运行状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU03D01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B10*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU03D01_R AT%I0.0 :BOOL; (*空调机组NJ-3AP(KT)4-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9))),SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))))),\" \")","v":"LAHU03D01_R             AT%I0.0        :BOOL; (*空调机组NJ-3AP(KT)4-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM9","v":"L22\\L22AHU03D01_R"},{"$f":"J9","v":"空调机组NJ-3AP(KT)4-1-运行状态"},{"$f":"10000+($B10*16*8+F9-1)","v":10000}]
[null,0,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-3AP(KT)4-1-故障状态",{"$nulls":16},{"$f":"IF(AI10=\"\",\"\",AI10)","v":"NJ-3AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-1","03D01","故障状态",{"$f":"AH10&\"-\"&AK10","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU03D01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B10*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU03D01_F AT%I0.1 :BOOL; (*空调机组NJ-3AP(KT)4-1-故障状态*)"},"LAHU03D01_F             AT%I0.1        :BOOL; (*空调机组NJ-3AP(KT)4-1-故障状态*)",null,"L22\\L22AHU03D01_F",{"$f":"J10","v":"空调机组NJ-3AP(KT)4-1-故障状态"},{"$f":"AS9+1","v":10001}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)4-1-自动状态",{"$nulls":16},"NJ-3AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-1","03D01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU03D01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B10*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU03D01_A AT%I0.2 :BOOL; (*空调机组NJ-3AP(KT)4-1-自动状态*)"},"LAHU03D01_A             AT%I0.2        :BOOL; (*空调机组NJ-3AP(KT)4-1-自动状态*)",null,"L22\\L22AHU03D01_A","空调机组NJ-3AP(KT)4-1-自动状态",{"$f":"AS10+1","v":10002}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)4-1-风机压差",{"$nulls":16},"NJ-3AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-1","03D01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU03D01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B10*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU03D01_FPS AT%I0.3 :BOOL; (*空调机组NJ-3AP(KT)4-1-风机压差*)"},"LAHU03D01_FPS           AT%I0.3        :BOOL; (*空调机组NJ-3AP(KT)4-1-风机压差*)",null,"L22\\L22AHU03D01_FPS","空调机组NJ-3AP(KT)4-1-风机压差",10003]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)4-2-运行状态",{"$nulls":16},"NJ-3AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-2","03D02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU03D02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B10*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU03D02_R AT%I0.4 :BOOL; (*空调机组NJ-3AP(KT)4-2-运行状态*)"},"LAHU03D02_R             AT%I0.4        :BOOL; (*空调机组NJ-3AP(KT)4-2-运行状态*)",null,"L22\\L22AHU03D02_R","空调机组NJ-3AP(KT)4-2-运行状态",10004]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)4-2-故障状态",{"$nulls":16},"NJ-3AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-2","03D02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU03D02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B10*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU03D02_F AT%I0.5 :BOOL; (*空调机组NJ-3AP(KT)4-2-故障状态*)"},"LAHU03D02_F             AT%I0.5        :BOOL; (*空调机组NJ-3AP(KT)4-2-故障状态*)",null,"L22\\L22AHU03D02_F","空调机组NJ-3AP(KT)4-2-故障状态",10005]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)4-2-自动状态",{"$nulls":16},"NJ-3AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-2","03D02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU03D02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B10*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU03D02_A AT%I0.6 :BOOL; (*空调机组NJ-3AP(KT)4-2-自动状态*)"},"LAHU03D02_A             AT%I0.6        :BOOL; (*空调机组NJ-3AP(KT)4-2-自动状态*)",null,"L22\\L22AHU03D02_A","空调机组NJ-3AP(KT)4-2-自动状态",10006]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)4-2-风机压差",{"$nulls":16},"NJ-3AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-2","03D02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU03D02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B10*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU03D02_FPS AT%I0.7 :BOOL; (*空调机组NJ-3AP(KT)4-2-风机压差*)"},"LAHU03D02_FPS           AT%I0.7        :BOOL; (*空调机组NJ-3AP(KT)4-2-风机压差*)",null,"L22\\L22AHU03D02_FPS","空调机组NJ-3AP(KT)4-2-风机压差",10007]
[{"$nulls":5},9,null,17,18,"空调机组NJ-3AP(KT)4-3-运行状态",{"$nulls":16},"NJ-3AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-3","03D03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU03D03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B10*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU03D03_R AT%I1.0 :BOOL; (*空调机组NJ-3AP(KT)4-3-运行状态*)"},"LAHU03D03_R             AT%I1.0        :BOOL; (*空调机组NJ-3AP(KT)4-3-运行状态*)",null,"L22\\L22AHU03D03_R","空调机组NJ-3AP(KT)4-3-运行状态",10008]
[{"$nulls":5},10,null,19,20,"空调机组NJ-3AP(KT)4-3-故障状态",{"$nulls":16},{"$f":"IF(AI18=\"\",\"\",AI18)","v":"NJ-3AP(KT)4-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-3","03D03","故障状态",{"$f":"AH18&\"-\"&AK18","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU03D03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B10*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU03D03_F AT%I1.1 :BOOL; (*空调机组NJ-3AP(KT)4-3-故障状态*)"},"LAHU03D03_F             AT%I1.1        :BOOL; (*空调机组NJ-3AP(KT)4-3-故障状态*)",null,"L22\\L22AHU03D03_F","空调机组NJ-3AP(KT)4-3-故障状态",10009]
[{"$nulls":5},11,null,21,22,"空调机组NJ-3AP(KT)4-3-自动状态",{"$nulls":16},"NJ-3AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-3","03D03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU03D03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B10*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU03D03_A AT%I1.2 :BOOL; (*空调机组NJ-3AP(KT)4-3-自动状态*)"},"LAHU03D03_A             AT%I1.2        :BOOL; (*空调机组NJ-3AP(KT)4-3-自动状态*)",null,"L22\\L22AHU03D03_A","空调机组NJ-3AP(KT)4-3-自动状态",10010]
[{"$nulls":5},12,null,23,24,"空调机组NJ-3AP(KT)4-3-风机压差",{"$nulls":16},"NJ-3AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-3","03D03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU03D03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B10*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU03D03_FPS AT%I1.3 :BOOL; (*空调机组NJ-3AP(KT)4-3-风机压差*)"},"LAHU03D03_FPS           AT%I1.3        :BOOL; (*空调机组NJ-3AP(KT)4-3-风机压差*)",null,"L22\\L22AHU03D03_FPS","空调机组NJ-3AP(KT)4-3-风机压差",10011]
[{"$nulls":5},13,null,25,26,"空调机组NJ-3AP(KT)4-4-运行状态",{"$nulls":16},"NJ-3AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-4","03D04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU03D04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B10*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU03D04_R AT%I1.4 :BOOL; (*空调机组NJ-3AP(KT)4-4-运行状态*)"},"LAHU03D04_R             AT%I1.4        :BOOL; (*空调机组NJ-3AP(KT)4-4-运行状态*)",null,"L22\\L22AHU03D04_R","空调机组NJ-3AP(KT)4-4-运行状态",10012]
[{"$nulls":5},14,null,27,28,"空调机组NJ-3AP(KT)4-4-故障状态",{"$nulls":16},"NJ-3AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-4","03D04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU03D04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B10*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU03D04_F AT%I1.5 :BOOL; (*空调机组NJ-3AP(KT)4-4-故障状态*)"},"LAHU03D04_F             AT%I1.5        :BOOL; (*空调机组NJ-3AP(KT)4-4-故障状态*)",null,"L22\\L22AHU03D04_F","空调机组NJ-3AP(KT)4-4-故障状态",10013]
[{"$nulls":5},15,null,29,30,"空调机组NJ-3AP(KT)4-4-自动状态",{"$nulls":16},"NJ-3AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-4","03D04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU03D04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B10*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU03D04_A AT%I1.6 :BOOL; (*空调机组NJ-3AP(KT)4-4-自动状态*)"},"LAHU03D04_A             AT%I1.6        :BOOL; (*空调机组NJ-3AP(KT)4-4-自动状态*)",null,"L22\\L22AHU03D04_A","空调机组NJ-3AP(KT)4-4-自动状态",10014]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-3AP(KT)4-4-风机压差",{"$nulls":16},"NJ-3AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-4","03D04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH24,List!$B$3:$D$445,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,List!$K$2:$M$447,2,FALSE)","v":"AHU03D04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%I\"&B10*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":"LAHU03D04_FPS AT%I1.7 :BOOL; (*空调机组NJ-3AP(KT)4-4-风机压差*)"},"LAHU03D04_FPS           AT%I1.7        :BOOL; (*空调机组NJ-3AP(KT)4-4-风机压差*)",null,"L22\\L22AHU03D04_FPS","空调机组NJ-3AP(KT)4-4-风机压差",10015]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 1601R地址: 1 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH26&AA26&\"-\"&AK26","v":"空调机组NJ-3AP(KT)4-5-运行状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-3AP(KT)4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-5","03D05","运行状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU03D05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU03D05_R AT%I16.0 :BOOL; (*空调机组NJ-3AP(KT)4-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LAHU03D05_R             AT%I16.0       :BOOL; (*空调机组NJ-3AP(KT)4-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L22\\L22AHU03D05_R"},{"$f":"J26","v":"空调机组NJ-3AP(KT)4-5-运行状态"},{"$f":"10000+($B27*16*8+F26-1)","v":10128}]
[null,1,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-3AP(KT)4-5-故障状态",{"$nulls":16},{"$f":"IF(AI27=\"\",\"\",AI27)","v":"NJ-3AP(KT)4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-5","03D05","故障状态",{"$f":"AH27&\"-\"&AK27","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU03D05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU03D05_F AT%I16.1 :BOOL; (*空调机组NJ-3AP(KT)4-5-故障状态*)"},"LAHU03D05_F             AT%I16.1       :BOOL; (*空调机组NJ-3AP(KT)4-5-故障状态*)",null,"L22\\L22AHU03D05_F",{"$f":"J27","v":"空调机组NJ-3AP(KT)4-5-故障状态"},{"$f":"AS26+1","v":10129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)4-5-自动状态",{"$nulls":16},"NJ-3AP(KT)4-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-5","03D05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU03D05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU03D05_A AT%I16.2 :BOOL; (*空调机组NJ-3AP(KT)4-5-自动状态*)"},"LAHU03D05_A             AT%I16.2       :BOOL; (*空调机组NJ-3AP(KT)4-5-自动状态*)",null,"L22\\L22AHU03D05_A","空调机组NJ-3AP(KT)4-5-自动状态",{"$f":"AS27+1","v":10130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)4-5-风机压差",{"$nulls":16},"NJ-3AP(KT)4-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-5","03D05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU03D05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU03D05_FPS AT%I16.3 :BOOL; (*空调机组NJ-3AP(KT)4-5-风机压差*)"},"LAHU03D05_FPS           AT%I16.3       :BOOL; (*空调机组NJ-3AP(KT)4-5-风机压差*)",null,"L22\\L22AHU03D05_FPS","空调机组NJ-3AP(KT)4-5-风机压差",10131]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)4-6-运行状态",{"$nulls":16},"NJ-3AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-6","03D06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU03D06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B27*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU03D06_R AT%I16.4 :BOOL; (*空调机组NJ-3AP(KT)4-6-运行状态*)"},"LAHU03D06_R             AT%I16.4       :BOOL; (*空调机组NJ-3AP(KT)4-6-运行状态*)",null,"L22\\L22AHU03D06_R","空调机组NJ-3AP(KT)4-6-运行状态",10132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)4-6-故障状态",{"$nulls":16},"NJ-3AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-6","03D06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU03D06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B27*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU03D06_F AT%I16.5 :BOOL; (*空调机组NJ-3AP(KT)4-6-故障状态*)"},"LAHU03D06_F             AT%I16.5       :BOOL; (*空调机组NJ-3AP(KT)4-6-故障状态*)",null,"L22\\L22AHU03D06_F","空调机组NJ-3AP(KT)4-6-故障状态",10133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)4-6-自动状态",{"$nulls":16},"NJ-3AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-6","03D06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU03D06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B27*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU03D06_A AT%I16.6 :BOOL; (*空调机组NJ-3AP(KT)4-6-自动状态*)"},"LAHU03D06_A             AT%I16.6       :BOOL; (*空调机组NJ-3AP(KT)4-6-自动状态*)",null,"L22\\L22AHU03D06_A","空调机组NJ-3AP(KT)4-6-自动状态",10134]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)4-6-风机压差",{"$nulls":16},"NJ-3AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-6","03D06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU03D06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B27*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU03D06_FPS AT%I16.7 :BOOL; (*空调机组NJ-3AP(KT)4-6-风机压差*)"},"LAHU03D06_FPS           AT%I16.7       :BOOL; (*空调机组NJ-3AP(KT)4-6-风机压差*)",null,"L22\\L22AHU03D06_FPS","空调机组NJ-3AP(KT)4-6-风机压差",10135]
[{"$nulls":5},9,null,17,18,"空调机组NJ-3AP(KT)4-7-运行状态",{"$nulls":16},"NJ-3AP(KT)4-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-7","03D07","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU03D07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B27*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU03D07_R AT%I17.0 :BOOL; (*空调机组NJ-3AP(KT)4-7-运行状态*)"},"LAHU03D07_R             AT%I17.0       :BOOL; (*空调机组NJ-3AP(KT)4-7-运行状态*)",null,"L22\\L22AHU03D07_R","空调机组NJ-3AP(KT)4-7-运行状态",10136]
[{"$nulls":5},10,null,19,20,"空调机组NJ-3AP(KT)4-7-故障状态",{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-3AP(KT)4-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-7","03D07","故障状态",{"$f":"AH35&\"-\"&AK35","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU03D07_F"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B27*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU03D07_F AT%I17.1 :BOOL; (*空调机组NJ-3AP(KT)4-7-故障状态*)"},"LAHU03D07_F             AT%I17.1       :BOOL; (*空调机组NJ-3AP(KT)4-7-故障状态*)",null,"L22\\L22AHU03D07_F",{"$f":"J35","v":"空调机组NJ-3AP(KT)4-7-故障状态"},10137]
[{"$nulls":5},11,null,21,22,"空调机组NJ-3AP(KT)4-7-自动状态",{"$nulls":16},"NJ-3AP(KT)4-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-7","03D07","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU03D07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B27*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU03D07_A AT%I17.2 :BOOL; (*空调机组NJ-3AP(KT)4-7-自动状态*)"},"LAHU03D07_A             AT%I17.2       :BOOL; (*空调机组NJ-3AP(KT)4-7-自动状态*)",null,"L22\\L22AHU03D07_A","空调机组NJ-3AP(KT)4-7-自动状态",10138]
[{"$nulls":5},12,null,23,24,"空调机组NJ-3AP(KT)4-7-风机压差",{"$nulls":16},"NJ-3AP(KT)4-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-7","03D07","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"AHU03D07_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B27*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LAHU03D07_FPS AT%I17.3 :BOOL; (*空调机组NJ-3AP(KT)4-7-风机压差*)"},"LAHU03D07_FPS           AT%I17.3       :BOOL; (*空调机组NJ-3AP(KT)4-7-风机压差*)",null,"L22\\L22AHU03D07_FPS","空调机组NJ-3AP(KT)4-7-风机压差",10139]
[{"$nulls":5},13,null,25,26,"空调机组NJ-3AP(KT)4-8-运行状态",{"$nulls":16},"NJ-3AP(KT)4-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-8","03D08","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"AHU03D08_R"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B27*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LAHU03D08_R AT%I17.4 :BOOL; (*空调机组NJ-3AP(KT)4-8-运行状态*)"},"LAHU03D08_R             AT%I17.4       :BOOL; (*空调机组NJ-3AP(KT)4-8-运行状态*)",null,"L22\\L22AHU03D08_R","空调机组NJ-3AP(KT)4-8-运行状态",10140]
[{"$nulls":5},14,null,27,28,"空调机组NJ-3AP(KT)4-8-故障状态",{"$nulls":16},"NJ-3AP(KT)4-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-8","03D08","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"AHU03D08_F"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B27*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LAHU03D08_F AT%I17.5 :BOOL; (*空调机组NJ-3AP(KT)4-8-故障状态*)"},"LAHU03D08_F             AT%I17.5       :BOOL; (*空调机组NJ-3AP(KT)4-8-故障状态*)",null,"L22\\L22AHU03D08_F","空调机组NJ-3AP(KT)4-8-故障状态",10141]
[{"$nulls":5},15,null,29,30,"空调机组NJ-3AP(KT)4-8-自动状态",{"$nulls":16},"NJ-3AP(KT)4-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-8","03D08","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"AHU03D08_A"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B27*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LAHU03D08_A AT%I17.6 :BOOL; (*空调机组NJ-3AP(KT)4-8-自动状态*)"},"LAHU03D08_A             AT%I17.6       :BOOL; (*空调机组NJ-3AP(KT)4-8-自动状态*)",null,"L22\\L22AHU03D08_A","空调机组NJ-3AP(KT)4-8-自动状态",10142]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-3AP(KT)4-8-风机压差",{"$nulls":16},"NJ-3AP(KT)4-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-8","03D08","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":"AHU03D08_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%I\"&B27*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":"LAHU03D08_FPS AT%I17.7 :BOOL; (*空调机组NJ-3AP(KT)4-8-风机压差*)"},"LAHU03D08_FPS           AT%I17.7       :BOOL; (*空调机组NJ-3AP(KT)4-8-风机压差*)",null,"L22\\L22AHU03D08_FPS","空调机组NJ-3AP(KT)4-8-风机压差",10143]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 1601R地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH43&AA43&\"-\"&AK43","v":"空调机组NJ-3AP(KT)4-9-运行状态"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-3AP(KT)4-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-9","03D09","运行状态",{"$f":"AH43&\"-\"&AK43","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"AHU03D09_R"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B44*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LAHU03D09_R AT%I32.0 :BOOL; (*空调机组NJ-3AP(KT)4-9-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LAHU03D09_R             AT%I32.0       :BOOL; (*空调机组NJ-3AP(KT)4-9-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM43","v":"L22\\L22AHU03D09_R"},{"$f":"J43","v":"空调机组NJ-3AP(KT)4-9-运行状态"},{"$f":"10000+($B44*16*8+F43-1)","v":10256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},2,null,3,4,"空调机组NJ-3AP(KT)4-9-故障状态",{"$nulls":16},{"$f":"IF(AI44=\"\",\"\",AI44)","v":"NJ-3AP(KT)4-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-9","03D09","故障状态",{"$f":"AH44&\"-\"&AK44","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"AHU03D09_F"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B44*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LAHU03D09_F AT%I32.1 :BOOL; (*空调机组NJ-3AP(KT)4-9-故障状态*)"},"LAHU03D09_F             AT%I32.1       :BOOL; (*空调机组NJ-3AP(KT)4-9-故障状态*)",null,"L22\\L22AHU03D09_F",{"$f":"J44","v":"空调机组NJ-3AP(KT)4-9-故障状态"},{"$f":"AS43+1","v":10257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)4-9-自动状态",{"$nulls":16},"NJ-3AP(KT)4-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-9","03D09","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"AHU03D09_A"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B44*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LAHU03D09_A AT%I32.2 :BOOL; (*空调机组NJ-3AP(KT)4-9-自动状态*)"},"LAHU03D09_A             AT%I32.2       :BOOL; (*空调机组NJ-3AP(KT)4-9-自动状态*)",null,"L22\\L22AHU03D09_A","空调机组NJ-3AP(KT)4-9-自动状态",{"$f":"AS44+1","v":10258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)4-9-风机压差",{"$nulls":16},"NJ-3AP(KT)4-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-9","03D09","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"AHU03D09_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B44*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LAHU03D09_FPS AT%I32.3 :BOOL; (*空调机组NJ-3AP(KT)4-9-风机压差*)"},"LAHU03D09_FPS           AT%I32.3       :BOOL; (*空调机组NJ-3AP(KT)4-9-风机压差*)",null,"L22\\L22AHU03D09_FPS","空调机组NJ-3AP(KT)4-9-风机压差",10259]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)4-10-运行状态",{"$nulls":16},"NJ-3AP(KT)4-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-10","03D10","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"AHU03D10_R"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B44*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LAHU03D10_R AT%I32.4 :BOOL; (*空调机组NJ-3AP(KT)4-10-运行状态*)"},"LAHU03D10_R             AT%I32.4       :BOOL; (*空调机组NJ-3AP(KT)4-10-运行状态*)",null,"L22\\L22AHU03D10_R","空调机组NJ-3AP(KT)4-10-运行状态",10260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)4-10-故障状态",{"$nulls":16},"NJ-3AP(KT)4-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-10","03D10","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"AHU03D10_F"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B44*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LAHU03D10_F AT%I32.5 :BOOL; (*空调机组NJ-3AP(KT)4-10-故障状态*)"},"LAHU03D10_F             AT%I32.5       :BOOL; (*空调机组NJ-3AP(KT)4-10-故障状态*)",null,"L22\\L22AHU03D10_F","空调机组NJ-3AP(KT)4-10-故障状态",10261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)4-10-自动状态",{"$nulls":16},"NJ-3AP(KT)4-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-10","03D10","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"AHU03D10_A"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B44*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LAHU03D10_A AT%I32.6 :BOOL; (*空调机组NJ-3AP(KT)4-10-自动状态*)"},"LAHU03D10_A             AT%I32.6       :BOOL; (*空调机组NJ-3AP(KT)4-10-自动状态*)",null,"L22\\L22AHU03D10_A","空调机组NJ-3AP(KT)4-10-自动状态",10262]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)4-10-风机压差",{"$nulls":16},"NJ-3AP(KT)4-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-10","03D10","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"AHU03D10_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B44*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LAHU03D10_FPS AT%I32.7 :BOOL; (*空调机组NJ-3AP(KT)4-10-风机压差*)"},"LAHU03D10_FPS           AT%I32.7       :BOOL; (*空调机组NJ-3AP(KT)4-10-风机压差*)",null,"L22\\L22AHU03D10_FPS","空调机组NJ-3AP(KT)4-10-风机压差",10263]
[{"$nulls":5},9,null,17,18,"空调机组NJ-3AP(KT)4-11-运行状态",{"$nulls":16},"NJ-3AP(KT)4-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-11","03D11","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"AHU03D11_R"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B44*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LAHU03D11_R AT%I33.0 :BOOL; (*空调机组NJ-3AP(KT)4-11-运行状态*)"},"LAHU03D11_R             AT%I33.0       :BOOL; (*空调机组NJ-3AP(KT)4-11-运行状态*)",null,"L22\\L22AHU03D11_R","空调机组NJ-3AP(KT)4-11-运行状态",10264]
[{"$nulls":5},10,null,19,20,"空调机组NJ-3AP(KT)4-11-故障状态",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-3AP(KT)4-11"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-11","03D11","故障状态",{"$f":"AH52&\"-\"&AK52","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"AHU03D11_F"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%I\"&B44*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LAHU03D11_F AT%I33.1 :BOOL; (*空调机组NJ-3AP(KT)4-11-故障状态*)"},"LAHU03D11_F             AT%I33.1       :BOOL; (*空调机组NJ-3AP(KT)4-11-故障状态*)",null,"L22\\L22AHU03D11_F",{"$f":"J52","v":"空调机组NJ-3AP(KT)4-11-故障状态"},10265]
[{"$nulls":5},11,null,21,22,"空调机组NJ-3AP(KT)4-11-自动状态",{"$nulls":16},"NJ-3AP(KT)4-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-11","03D11","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"AHU03D11_A"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%I\"&B44*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LAHU03D11_A AT%I33.2 :BOOL; (*空调机组NJ-3AP(KT)4-11-自动状态*)"},"LAHU03D11_A             AT%I33.2       :BOOL; (*空调机组NJ-3AP(KT)4-11-自动状态*)",null,"L22\\L22AHU03D11_A","空调机组NJ-3AP(KT)4-11-自动状态",10266]
[{"$nulls":5},12,null,23,24,"空调机组NJ-3AP(KT)4-11-风机压差",{"$nulls":16},"NJ-3AP(KT)4-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-11","03D11","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"AHU03D11_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%I\"&B44*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LAHU03D11_FPS AT%I33.3 :BOOL; (*空调机组NJ-3AP(KT)4-11-风机压差*)"},"LAHU03D11_FPS           AT%I33.3       :BOOL; (*空调机组NJ-3AP(KT)4-11-风机压差*)",null,"L22\\L22AHU03D11_FPS","空调机组NJ-3AP(KT)4-11-风机压差",10267]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-3AL4-1-运行状态",{"$nulls":16},"NJ-3AL4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-1","03D01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"LCB03D01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%I\"&B44*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LLCB03D01_R AT%I33.4 :BOOL; (*照明控制箱NJ-3AL4-1-运行状态*)"},"LLCB03D01_R             AT%I33.4       :BOOL; (*照明控制箱NJ-3AL4-1-运行状态*)",null,"L22\\L22LCB03D01_R","照明控制箱NJ-3AL4-1-运行状态",10268]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-3AL4-1-自动状态",{"$nulls":16},"NJ-3AL4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-1","03D01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"LCB03D01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%I\"&B44*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LLCB03D01_A AT%I33.5 :BOOL; (*照明控制箱NJ-3AL4-1-自动状态*)"},"LLCB03D01_A             AT%I33.5       :BOOL; (*照明控制箱NJ-3AL4-1-自动状态*)",null,"L22\\L22LCB03D01_A","照明控制箱NJ-3AL4-1-自动状态",10269]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-3AL4-2-运行状态",{"$nulls":16},"NJ-3AL4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-2","03D02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"LCB03D02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%I\"&B44*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LLCB03D02_R AT%I33.6 :BOOL; (*照明控制箱NJ-3AL4-2-运行状态*)"},"LLCB03D02_R             AT%I33.6       :BOOL; (*照明控制箱NJ-3AL4-2-运行状态*)",null,"L22\\L22LCB03D02_R","照明控制箱NJ-3AL4-2-运行状态",10270]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-3AL4-2-自动状态",{"$nulls":16},"NJ-3AL4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-2","03D02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":"LCB03D02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%I\"&B44*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":"LLCB03D02_A AT%I33.7 :BOOL; (*照明控制箱NJ-3AL4-2-自动状态*)"},"LLCB03D02_A             AT%I33.7       :BOOL; (*照明控制箱NJ-3AL4-2-自动状态*)",null,"L22\\L22LCB03D02_A","照明控制箱NJ-3AL4-2-自动状态",10271]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B64&\"地址: \"&B61&\" *)\"","v":"(* IOM 1601R地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH60&AA60&\"-\"&AK60","v":"照明控制箱NJ-3AL4-3-运行状态"},{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-3AL4-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-3","03D03","运行状态",{"$f":"AH60&\"-\"&AK60","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"LCB03D03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%I\"&B61*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LLCB03D03_R AT%I48.0 :BOOL; (*照明控制箱NJ-3AL4-3-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60))),SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))))),\" \")","v":"LLCB03D03_R             AT%I48.0       :BOOL; (*照明控制箱NJ-3AL4-3-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM60","v":"L22\\L22LCB03D03_R"},{"$f":"J60","v":"照明控制箱NJ-3AL4-3-运行状态"},{"$f":"10000+($B61*16*8+F60-1)","v":10384}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},2,null,3,4,"照明控制箱NJ-3AL4-3-自动状态",{"$nulls":16},{"$f":"IF(AI61=\"\",\"\",AI61)","v":"NJ-3AL4-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-3","03D03","自动状态",{"$f":"AH61&\"-\"&AK61","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"LCB03D03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%I\"&B61*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LLCB03D03_A AT%I48.1 :BOOL; (*照明控制箱NJ-3AL4-3-自动状态*)"},"LLCB03D03_A             AT%I48.1       :BOOL; (*照明控制箱NJ-3AL4-3-自动状态*)",null,"L22\\L22LCB03D03_A",{"$f":"J61","v":"照明控制箱NJ-3AL4-3-自动状态"},{"$f":"AS60+1","v":10385}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},3,null,5,6,"照明控制箱NJ-3AL4-4-运行状态",{"$nulls":16},"NJ-3AL4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-4","03D04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"LCB03D04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B61*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LLCB03D04_R AT%I48.2 :BOOL; (*照明控制箱NJ-3AL4-4-运行状态*)"},"LLCB03D04_R             AT%I48.2       :BOOL; (*照明控制箱NJ-3AL4-4-运行状态*)",null,"L22\\L22LCB03D04_R","照明控制箱NJ-3AL4-4-运行状态",{"$f":"AS61+1","v":10386}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},4,null,7,8,"照明控制箱NJ-3AL4-4-自动状态",{"$nulls":16},"NJ-3AL4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-4","03D04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"LCB03D04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B61*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LLCB03D04_A AT%I48.3 :BOOL; (*照明控制箱NJ-3AL4-4-自动状态*)"},"LLCB03D04_A             AT%I48.3       :BOOL; (*照明控制箱NJ-3AL4-4-自动状态*)",null,"L22\\L22LCB03D04_A","照明控制箱NJ-3AL4-4-自动状态",10387]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-3AL4-5-运行状态",{"$nulls":16},"NJ-3AL4-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-5","03D05","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"LCB03D05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B61*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LLCB03D05_R AT%I48.4 :BOOL; (*照明控制箱NJ-3AL4-5-运行状态*)"},"LLCB03D05_R             AT%I48.4       :BOOL; (*照明控制箱NJ-3AL4-5-运行状态*)",null,"L22\\L22LCB03D05_R","照明控制箱NJ-3AL4-5-运行状态",10388]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-3AL4-5-自动状态",{"$nulls":16},"NJ-3AL4-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-5","03D05","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":"LCB03D05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B61*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":"LLCB03D05_A AT%I48.5 :BOOL; (*照明控制箱NJ-3AL4-5-自动状态*)"},"LLCB03D05_A             AT%I48.5       :BOOL; (*照明控制箱NJ-3AL4-5-自动状态*)",null,"L22\\L22LCB03D05_A","照明控制箱NJ-3AL4-5-自动状态",10389]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"照明控制箱NJ-3AL4-6-运行状态",{"$nulls":16},"NJ-3AL4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-6","03D06","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":"LCB03D06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B61*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":"LLCB03D06_R AT%I48.6 :BOOL; (*照明控制箱NJ-3AL4-6-运行状态*)"},"LLCB03D06_R             AT%I48.6       :BOOL; (*照明控制箱NJ-3AL4-6-运行状态*)",null,"L22\\L22LCB03D06_R","照明控制箱NJ-3AL4-6-运行状态",10390]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"照明控制箱NJ-3AL4-6-自动状态",{"$nulls":16},"NJ-3AL4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-6","03D06","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":"LCB03D06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%I\"&B61*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":"LLCB03D06_A AT%I48.7 :BOOL; (*照明控制箱NJ-3AL4-6-自动状态*)"},"LLCB03D06_A             AT%I48.7       :BOOL; (*照明控制箱NJ-3AL4-6-自动状态*)",null,"L22\\L22LCB03D06_A","照明控制箱NJ-3AL4-6-自动状态",10391]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-3AL4-7-运行状态",{"$nulls":16},"NJ-3AL4-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-7","03D07","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"LCB03D07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%I\"&B61*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LLCB03D07_R AT%I49.0 :BOOL; (*照明控制箱NJ-3AL4-7-运行状态*)"},"LLCB03D07_R             AT%I49.0       :BOOL; (*照明控制箱NJ-3AL4-7-运行状态*)",null,"L22\\L22LCB03D07_R","照明控制箱NJ-3AL4-7-运行状态",10392]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-3AL4-7-自动状态",{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-3AL4-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-7","03D07","自动状态",{"$f":"AH69&\"-\"&AK69","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"LCB03D07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%I\"&B61*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LLCB03D07_A AT%I49.1 :BOOL; (*照明控制箱NJ-3AL4-7-自动状态*)"},"LLCB03D07_A             AT%I49.1       :BOOL; (*照明控制箱NJ-3AL4-7-自动状态*)",null,"L22\\L22LCB03D07_A",{"$f":"J69","v":"照明控制箱NJ-3AL4-7-自动状态"},10393]
[{"$nulls":5},11,null,21,22,"风机盘管NJ-3AP(KT)4-1-运行状态",{"$nulls":16},"NJ-3AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-3AP(KT)4-1","03D01","运行状态","风机盘管-运行状态",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"FCU03D01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%I\"&B61*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LFCU03D01_R AT%I49.2 :BOOL; (*风机盘管NJ-3AP(KT)4-1-运行状态*)"},"LFCU03D01_R             AT%I49.2       :BOOL; (*风机盘管NJ-3AP(KT)4-1-运行状态*)",null,"L22\\L22FCU03D01_R","风机盘管NJ-3AP(KT)4-1-运行状态",10394]
[{"$nulls":5},12,null,23,24,"风机盘管NJ-3AP(KT)4-1-自动状态",{"$nulls":16},"NJ-3AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-3AP(KT)4-1","03D01","自动状态","风机盘管-自动状态",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"FCU03D01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%I\"&B61*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LFCU03D01_A AT%I49.3 :BOOL; (*风机盘管NJ-3AP(KT)4-1-自动状态*)"},"LFCU03D01_A             AT%I49.3       :BOOL; (*风机盘管NJ-3AP(KT)4-1-自动状态*)",null,"L22\\L22FCU03D01_A","风机盘管NJ-3AP(KT)4-1-自动状态",10395]
[{"$nulls":5},13,null,25,26,"风机盘管NJ-3AP(KT)4-1-电磁阀开启状态",{"$nulls":16},"NJ-3AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-3AP(KT)4-1","03D01","电磁阀开启状态","风机盘管-电磁阀开启状态",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"FCU03D01_EVR"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%I\"&B61*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LFCU03D01_EVR AT%I49.4 :BOOL; (*风机盘管NJ-3AP(KT)4-1-电磁阀开启状态*)"},"LFCU03D01_EVR           AT%I49.4       :BOOL; (*风机盘管NJ-3AP(KT)4-1-电磁阀开启状态*)",null,"L22\\L22FCU03D01_EVR","风机盘管NJ-3AP(KT)4-1-电磁阀开启状态",10396]
[{"$nulls":5},14,null,27,28,"风机盘管NJ-3AP(KT)4-1-电磁阀自动状态",{"$nulls":16},"NJ-3AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-3AP(KT)4-1","03D01","电磁阀自动状态","风机盘管-电磁阀自动状态",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"FCU03D01_EVA"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%I\"&B61*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LFCU03D01_EVA AT%I49.5 :BOOL; (*风机盘管NJ-3AP(KT)4-1-电磁阀自动状态*)"},"LFCU03D01_EVA           AT%I49.5       :BOOL; (*风机盘管NJ-3AP(KT)4-1-电磁阀自动状态*)",null,"L22\\L22FCU03D01_EVA","风机盘管NJ-3AP(KT)4-1-电磁阀自动状态",10397]
[{"$nulls":5},15,null,29,30,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%I\"&B61*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10398]
[".",{"$nulls":4},16,null,31,32,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%I\"&B61*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN75,SEARCH(\"AT%\",AN75),,REPT(\" \",30-SEARCH(\"AT%\",AN75))),SEARCH(\":\",REPLACE(AN75,SEARCH(\"AT%\",AN75),,REPT(\" \",30-SEARCH(\"AT%\",AN75)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN75,SEARCH(\"AT%\",AN75),,REPT(\" \",25-SEARCH(\"AT%\",AN75)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",10399]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B81&\"地址: \"&B78&\" *)\"","v":"(* IOM 1601D地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH77&AA77&\"-\"&AK77","v":"空调机组NJ-3AP(KT)4-1-启停控制"},{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-3AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-1","03D01","启停控制",{"$f":"AH77&\"-\"&AK77","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"AHU03D01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%Q\"&B78*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LAHU03D01_C AT%Q64.0 :BOOL; (*空调机组NJ-3AP(KT)4-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77))),SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))))),\" \")","v":"LAHU03D01_C             AT%Q64.0       :BOOL; (*空调机组NJ-3AP(KT)4-1-启停控制*)"},null,{"$f":"AM77","v":"AHU03D01_C"},{"$f":"J77","v":"空调机组NJ-3AP(KT)4-1-启停控制"},{"$f":"($B78*16*8+F77-1)","v":512}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","空调机组NJ-3AP(KT)4-2-启停控制",{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-3AP(KT)4-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-2","03D02","启停控制",{"$f":"AH78&\"-\"&AK78","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU03D02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B78*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU03D02_C AT%Q64.1 :BOOL; (*空调机组NJ-3AP(KT)4-2-启停控制*)"},"LAHU03D02_C             AT%Q64.1       :BOOL; (*空调机组NJ-3AP(KT)4-2-启停控制*)",null,"AHU03D02_C",{"$f":"J78","v":"空调机组NJ-3AP(KT)4-2-启停控制"},{"$f":"AS77+1","v":513}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-3AP(KT)4-3-启停控制",{"$nulls":16},"NJ-3AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-3","03D03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU03D03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B78*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU03D03_C AT%Q64.2 :BOOL; (*空调机组NJ-3AP(KT)4-3-启停控制*)"},"LAHU03D03_C             AT%Q64.2       :BOOL; (*空调机组NJ-3AP(KT)4-3-启停控制*)",null,"AHU03D03_C","空调机组NJ-3AP(KT)4-3-启停控制",{"$f":"AS78+1","v":514}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","空调机组NJ-3AP(KT)4-4-启停控制",{"$nulls":16},"NJ-3AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-4","03D04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU03D04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B78*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU03D04_C AT%Q64.3 :BOOL; (*空调机组NJ-3AP(KT)4-4-启停控制*)"},"LAHU03D04_C             AT%Q64.3       :BOOL; (*空调机组NJ-3AP(KT)4-4-启停控制*)",null,"AHU03D04_C","空调机组NJ-3AP(KT)4-4-启停控制",515]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-3AP(KT)4-5-启停控制",{"$nulls":16},"NJ-3AP(KT)4-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-5","03D05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"AHU03D05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%Q\"&B78*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LAHU03D05_C AT%Q64.4 :BOOL; (*空调机组NJ-3AP(KT)4-5-启停控制*)"},"LAHU03D05_C             AT%Q64.4       :BOOL; (*空调机组NJ-3AP(KT)4-5-启停控制*)",null,"AHU03D05_C","空调机组NJ-3AP(KT)4-5-启停控制",516]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-3AP(KT)4-6-启停控制",{"$nulls":16},"NJ-3AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-6","03D06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":"AHU03D06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%Q\"&B78*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":"LAHU03D06_C AT%Q64.5 :BOOL; (*空调机组NJ-3AP(KT)4-6-启停控制*)"},"LAHU03D06_C             AT%Q64.5       :BOOL; (*空调机组NJ-3AP(KT)4-6-启停控制*)",null,"AHU03D06_C","空调机组NJ-3AP(KT)4-6-启停控制",517]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","空调机组NJ-3AP(KT)4-7-启停控制",{"$nulls":16},"NJ-3AP(KT)4-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-7","03D07","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":"AHU03D07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%Q\"&B78*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":"LAHU03D07_C AT%Q64.6 :BOOL; (*空调机组NJ-3AP(KT)4-7-启停控制*)"},"LAHU03D07_C             AT%Q64.6       :BOOL; (*空调机组NJ-3AP(KT)4-7-启停控制*)",null,"AHU03D07_C","空调机组NJ-3AP(KT)4-7-启停控制",518]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","空调机组NJ-3AP(KT)4-8-启停控制",{"$nulls":16},"NJ-3AP(KT)4-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-8","03D08","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH84,List!$B$3:$D$445,2,FALSE)&AJ84&\"_\"&VLOOKUP(AK84,List!$K$2:$M$447,2,FALSE)","v":"AHU03D08_C"},{"$f":"_xlfn.IFNA(\"L\"&AM84&\" \"&\"AT%Q\"&B78*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J84&\"*)\",\" \")","v":"LAHU03D08_C AT%Q64.7 :BOOL; (*空调机组NJ-3AP(KT)4-8-启停控制*)"},"LAHU03D08_C             AT%Q64.7       :BOOL; (*空调机组NJ-3AP(KT)4-8-启停控制*)",null,"AHU03D08_C","空调机组NJ-3AP(KT)4-8-启停控制",519]
[{"$nulls":5},9,null,"9+","9-","空调机组NJ-3AP(KT)4-9-启停控制",{"$nulls":16},"NJ-3AP(KT)4-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-9","03D09","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH85,List!$B$3:$D$445,2,FALSE)&AJ85&\"_\"&VLOOKUP(AK85,List!$K$2:$M$447,2,FALSE)","v":"AHU03D09_C"},{"$f":"_xlfn.IFNA(\"L\"&AM85&\" \"&\"AT%Q\"&B78*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J85&\"*)\",\" \")","v":"LAHU03D09_C AT%Q65.0 :BOOL; (*空调机组NJ-3AP(KT)4-9-启停控制*)"},"LAHU03D09_C             AT%Q65.0       :BOOL; (*空调机组NJ-3AP(KT)4-9-启停控制*)",null,"AHU03D09_C","空调机组NJ-3AP(KT)4-9-启停控制",520]
[{"$nulls":5},10,null,"10+","10-","空调机组NJ-3AP(KT)4-10-启停控制",{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-3AP(KT)4-10"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-10","03D10","启停控制",{"$f":"AH86&\"-\"&AK86","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"AHU03D10_C"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%Q\"&B78*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LAHU03D10_C AT%Q65.1 :BOOL; (*空调机组NJ-3AP(KT)4-10-启停控制*)"},"LAHU03D10_C             AT%Q65.1       :BOOL; (*空调机组NJ-3AP(KT)4-10-启停控制*)",null,"AHU03D10_C",{"$f":"J86","v":"空调机组NJ-3AP(KT)4-10-启停控制"},521]
[{"$nulls":5},11,null,"11+","11-","空调机组NJ-3AP(KT)4-11-启停控制",{"$nulls":16},"NJ-3AP(KT)4-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-11","03D11","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"AHU03D11_C"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%Q\"&B78*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LAHU03D11_C AT%Q65.2 :BOOL; (*空调机组NJ-3AP(KT)4-11-启停控制*)"},"LAHU03D11_C             AT%Q65.2       :BOOL; (*空调机组NJ-3AP(KT)4-11-启停控制*)",null,"AHU03D11_C","空调机组NJ-3AP(KT)4-11-启停控制",522]
[{"$nulls":5},12,null,"12+","12-","照明控制箱NJ-3AL4-1-启停控制",{"$nulls":16},"NJ-3AL4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-1","03D01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"LCB03D01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%Q\"&B78*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LLCB03D01_C AT%Q65.3 :BOOL; (*照明控制箱NJ-3AL4-1-启停控制*)"},"LLCB03D01_C             AT%Q65.3       :BOOL; (*照明控制箱NJ-3AL4-1-启停控制*)",null,"LCB03D01_C","照明控制箱NJ-3AL4-1-启停控制",523]
[{"$nulls":5},13,null,"13+","13-","照明控制箱NJ-3AL4-2-启停控制",{"$nulls":16},"NJ-3AL4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-2","03D02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"LCB03D02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%Q\"&B78*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LLCB03D02_C AT%Q65.4 :BOOL; (*照明控制箱NJ-3AL4-2-启停控制*)"},"LLCB03D02_C             AT%Q65.4       :BOOL; (*照明控制箱NJ-3AL4-2-启停控制*)",null,"LCB03D02_C","照明控制箱NJ-3AL4-2-启停控制",524]
[{"$nulls":5},14,null,"14+","14-","照明控制箱NJ-3AL4-3-启停控制",{"$nulls":16},"NJ-3AL4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-3","03D03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":"LCB03D03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%Q\"&B78*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":"LLCB03D03_C AT%Q65.5 :BOOL; (*照明控制箱NJ-3AL4-3-启停控制*)"},"LLCB03D03_C             AT%Q65.5       :BOOL; (*照明控制箱NJ-3AL4-3-启停控制*)",null,"LCB03D03_C","照明控制箱NJ-3AL4-3-启停控制",525]
[{"$nulls":5},15,null,"15+","15-","照明控制箱NJ-3AL4-4-启停控制",{"$nulls":16},"NJ-3AL4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-4","03D04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH91,List!$B$3:$D$445,2,FALSE)&AJ91&\"_\"&VLOOKUP(AK91,List!$K$2:$M$447,2,FALSE)","v":"LCB03D04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM91&\" \"&\"AT%Q\"&B78*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J91&\"*)\",\" \")","v":"LLCB03D04_C AT%Q65.6 :BOOL; (*照明控制箱NJ-3AL4-4-启停控制*)"},"LLCB03D04_C             AT%Q65.6       :BOOL; (*照明控制箱NJ-3AL4-4-启停控制*)",null,"LCB03D04_C","照明控制箱NJ-3AL4-4-启停控制",526]
[".",{"$nulls":4},16,null,"16+","16-","照明控制箱NJ-3AL4-5-启停控制",{"$nulls":16},"NJ-3AL4-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-5","03D05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH92,List!$B$3:$D$445,2,FALSE)&AJ92&\"_\"&VLOOKUP(AK92,List!$K$2:$M$447,2,FALSE)","v":"LCB03D05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM92&\" \"&\"AT%Q\"&B78*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J92&\"*)\",\" \")","v":"LLCB03D05_C AT%Q65.7 :BOOL; (*照明控制箱NJ-3AL4-5-启停控制*)"},"LLCB03D05_C             AT%Q65.7       :BOOL; (*照明控制箱NJ-3AL4-5-启停控制*)",null,"LCB03D05_C","照明控制箱NJ-3AL4-5-启停控制",527]
[null,"IOM 0801D",{"$nulls":38},{"$f":"\"(* \"&B98&\"地址: \"&B95&\" *)\"","v":"(* IOM 0801D地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH94&AA94&\"-\"&AK94","v":"照明控制箱NJ-3AL4-6-启停控制"},{"$nulls":16},{"$f":"IF(AI94=\"\",\"\",AI94)","v":"NJ-3AL4-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-6","03D06","启停控制",{"$f":"AH94&\"-\"&AK94","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH94,List!$B$3:$D$445,2,FALSE)&AJ94&\"_\"&VLOOKUP(AK94,List!$K$2:$M$447,2,FALSE)","v":"LCB03D06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM94&\" \"&\"AT%Q\"&B95*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J94&\"*)\",\" \")","v":"LLCB03D06_C AT%Q80.0 :BOOL; (*照明控制箱NJ-3AL4-6-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94))),SEARCH(\":\",REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94)))))),\" \")","v":"LLCB03D06_C             AT%Q80.0       :BOOL; (*照明控制箱NJ-3AL4-6-启停控制*)"},null,{"$f":"AM94","v":"LCB03D06_C"},{"$f":"J94","v":"照明控制箱NJ-3AL4-6-启停控制"},{"$f":"($B95*16*8+F94-1)","v":640}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","照明控制箱NJ-3AL4-7-启停控制",{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-3AL4-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL4-7","03D07","启停控制",{"$f":"AH95&\"-\"&AK95","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"LCB03D07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%Q\"&B95*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LLCB03D07_C AT%Q80.1 :BOOL; (*照明控制箱NJ-3AL4-7-启停控制*)"},"LLCB03D07_C             AT%Q80.1       :BOOL; (*照明控制箱NJ-3AL4-7-启停控制*)",null,"LCB03D07_C",{"$f":"J95","v":"照明控制箱NJ-3AL4-7-启停控制"},{"$f":"AS94+1","v":641}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","风机盘管NJ-3AP(KT)4-1-启停控制",{"$nulls":16},"NJ-3AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-3AP(KT)4-1","03D01","启停控制","风机盘管-启停控制",{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"FCU03D01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%Q\"&B95*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LFCU03D01_C AT%Q80.2 :BOOL; (*风机盘管NJ-3AP(KT)4-1-启停控制*)"},"LFCU03D01_C             AT%Q80.2       :BOOL; (*风机盘管NJ-3AP(KT)4-1-启停控制*)",null,"FCU03D01_C","风机盘管NJ-3AP(KT)4-1-启停控制",{"$f":"AS95+1","v":642}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","风机盘管NJ-3AP(KT)4-1-电磁阀开关控制",{"$nulls":16},"NJ-3AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-3AP(KT)4-1","03D01","电磁阀开关控制","风机盘管-电磁阀开关控制",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":"FCU03D01_EVC"},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%Q\"&B95*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":"LFCU03D01_EVC AT%Q80.3 :BOOL; (*风机盘管NJ-3AP(KT)4-1-电磁阀开关控制*)"},"LFCU03D01_EVC           AT%Q80.3       :BOOL; (*风机盘管NJ-3AP(KT)4-1-电磁阀开关控制*)",null,"FCU03D01_EVC","风机盘管NJ-3AP(KT)4-1-电磁阀开关控制",643]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%Q\"&B95*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",644]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH99,List!$B$3:$D$445,2,FALSE)&AJ99&\"_\"&VLOOKUP(AK99,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM99&\" \"&\"AT%Q\"&B95*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J99&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",645]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH100,List!$B$3:$D$445,2,FALSE)&AJ100&\"_\"&VLOOKUP(AK100,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM100&\" \"&\"AT%Q\"&B95*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J100&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",646]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH101,List!$B$3:$D$445,2,FALSE)&AJ101&\"_\"&VLOOKUP(AK101,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM101&\" \"&\"AT%Q\"&B95*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J101&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",647]
[null,{"$f":"B107","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B107&\"地址: \"&B104&\" *)\"","v":"(* IOM 0801U地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH103&AA103&\"-\"&AK103","v":"空调机组NJ-3AP(KT)4-1-回风温度"},{"$nulls":16},{"$f":"IF(AI103=\"\",\"\",AI103)","v":"NJ-3AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-1","03D01","回风温度",{"$f":"AH103&\"-\"&AK103","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH103,List!$B$3:$D$445,2,FALSE)&AJ103&\"_\"&VLOOKUP(AK103,List!$K$2:$M$447,2,FALSE)","v":"AHU03D01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM103&\" \"&\"AT%I\"&B104*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J103&\"*)\",\" \")","v":"LAHU03D01_RT AT%I96.0 :INT ; (*空调机组NJ-3AP(KT)4-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103))),SEARCH(\":\",REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103)))))),\" \")","v":"LAHU03D01_RT            AT%I96.0       :INT ; (*空调机组NJ-3AP(KT)4-1-回风温度*)"},null,{"$f":"AM103","v":"AHU03D01_RT"},{"$f":"J103","v":"空调机组NJ-3AP(KT)4-1-回风温度"},{"$f":"30000+($B104*8+F103-1)","v":30048}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-3AP(KT)4-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI104=\"\",\"\",AI104)","v":"NJ-3AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-1","03D01","水阀反馈",{"$f":"AH104&\"-\"&AK104","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"AHU03D01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%I\"&B104*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LAHU03D01_WVB AT%I98.0 :INT ; (*空调机组NJ-3AP(KT)4-1-水阀反馈*)"},"LAHU03D01_WVB           AT%I98.0       :INT ; (*空调机组NJ-3AP(KT)4-1-水阀反馈*)",null,"AHU03D01_WVB",{"$f":"J104","v":"空调机组NJ-3AP(KT)4-1-水阀反馈"},{"$f":"AS103+1","v":30049}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)4-2-回风温度",{"$nulls":16},"NJ-3AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-2","03D02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"AHU03D02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%I\"&B104*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LAHU03D02_RT AT%I100.0 :INT ; (*空调机组NJ-3AP(KT)4-2-回风温度*)"},"LAHU03D02_RT            AT%I100.0      :INT ; (*空调机组NJ-3AP(KT)4-2-回风温度*)",null,"AHU03D02_RT","空调机组NJ-3AP(KT)4-2-回风温度",{"$f":"AS104+1","v":30050}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-3AP(KT)4-2-水阀反馈",{"$nulls":16},"NJ-3AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-2","03D02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":"AHU03D02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%I\"&B104*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":"LAHU03D02_WVB AT%I102.0 :INT ; (*空调机组NJ-3AP(KT)4-2-水阀反馈*)"},"LAHU03D02_WVB           AT%I102.0      :INT ; (*空调机组NJ-3AP(KT)4-2-水阀反馈*)",null,"AHU03D02_WVB","空调机组NJ-3AP(KT)4-2-水阀反馈",30051]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-3AP(KT)4-3-回风温度",{"$nulls":16},"NJ-3AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-3","03D03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH107,List!$B$3:$D$445,2,FALSE)&AJ107&\"_\"&VLOOKUP(AK107,List!$K$2:$M$447,2,FALSE)","v":"AHU03D03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM107&\" \"&\"AT%I\"&B104*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J107&\"*)\",\" \")","v":"LAHU03D03_RT AT%I104.0 :INT ; (*空调机组NJ-3AP(KT)4-3-回风温度*)"},"LAHU03D03_RT            AT%I104.0      :INT ; (*空调机组NJ-3AP(KT)4-3-回风温度*)",null,"AHU03D03_RT","空调机组NJ-3AP(KT)4-3-回风温度",30052]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-3AP(KT)4-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI108=\"\",\"\",AI108)","v":"NJ-3AP(KT)4-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-3","03D03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH108,List!$B$3:$D$445,2,FALSE)&AJ108&\"_\"&VLOOKUP(AK108,List!$K$2:$M$447,2,FALSE)","v":"AHU03D03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM108&\" \"&\"AT%I\"&B104*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J108&\"*)\",\" \")","v":"LAHU03D03_WVB AT%I106.0 :INT ; (*空调机组NJ-3AP(KT)4-3-水阀反馈*)"},"LAHU03D03_WVB           AT%I106.0      :INT ; (*空调机组NJ-3AP(KT)4-3-水阀反馈*)",null,"AHU03D03_WVB",{"$f":"J108","v":"空调机组NJ-3AP(KT)4-3-水阀反馈"},30053]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-3AP(KT)4-4-回风温度",{"$nulls":16},"NJ-3AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-4","03D04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH109,List!$B$3:$D$445,2,FALSE)&AJ109&\"_\"&VLOOKUP(AK109,List!$K$2:$M$447,2,FALSE)","v":"AHU03D04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM109&\" \"&\"AT%I\"&B104*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J109&\"*)\",\" \")","v":"LAHU03D04_RT AT%I108.0 :INT ; (*空调机组NJ-3AP(KT)4-4-回风温度*)"},"LAHU03D04_RT            AT%I108.0      :INT ; (*空调机组NJ-3AP(KT)4-4-回风温度*)",null,"AHU03D04_RT","空调机组NJ-3AP(KT)4-4-回风温度",30054]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0+B+I109","空调机组NJ-3AP(KT)4-4-水阀反馈",{"$nulls":16},"NJ-3AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL110,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL110,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-4","03D04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH110,List!$B$3:$D$445,2,FALSE)&AJ110&\"_\"&VLOOKUP(AK110,List!$K$2:$M$447,2,FALSE)","v":"AHU03D04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM110&\" \"&\"AT%I\"&B104*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J110&\"*)\",\" \")","v":"LAHU03D04_WVB AT%I110.0 :INT ; (*空调机组NJ-3AP(KT)4-4-水阀反馈*)"},"LAHU03D04_WVB           AT%I110.0      :INT ; (*空调机组NJ-3AP(KT)4-4-水阀反馈*)",null,"AHU03D04_WVB","空调机组NJ-3AP(KT)4-4-水阀反馈",30055]
[null,{"$f":"B116","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B116&\"地址: \"&B113&\" *)\"","v":"(* IOM 0801U地址: 7 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH112&AA112&\"-\"&AK112","v":"空调机组NJ-3AP(KT)4-5-回风温度"},{"$nulls":16},{"$f":"IF(AI112=\"\",\"\",AI112)","v":"NJ-3AP(KT)4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-5","03D05","回风温度",{"$f":"AH112&\"-\"&AK112","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH112,List!$B$3:$D$445,2,FALSE)&AJ112&\"_\"&VLOOKUP(AK112,List!$K$2:$M$447,2,FALSE)","v":"AHU03D05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM112&\" \"&\"AT%I\"&B113*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J112&\"*)\",\" \")","v":"LAHU03D05_RT AT%I112.0 :INT ; (*空调机组NJ-3AP(KT)4-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112))),SEARCH(\":\",REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112)))))),\" \")","v":"LAHU03D05_RT            AT%I112.0      :INT ; (*空调机组NJ-3AP(KT)4-5-回风温度*)"},null,{"$f":"AM112","v":"AHU03D05_RT"},{"$f":"J112","v":"空调机组NJ-3AP(KT)4-5-回风温度"},{"$f":"30000+($B113*8+F112-1)","v":30056}]
[null,7,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-3AP(KT)4-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI113=\"\",\"\",AI113)","v":"NJ-3AP(KT)4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-5","03D05","水阀反馈",{"$f":"AH113&\"-\"&AK113","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH113,List!$B$3:$D$445,2,FALSE)&AJ113&\"_\"&VLOOKUP(AK113,List!$K$2:$M$447,2,FALSE)","v":"AHU03D05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM113&\" \"&\"AT%I\"&B113*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J113&\"*)\",\" \")","v":"LAHU03D05_WVB AT%I114.0 :INT ; (*空调机组NJ-3AP(KT)4-5-水阀反馈*)"},"LAHU03D05_WVB           AT%I114.0      :INT ; (*空调机组NJ-3AP(KT)4-5-水阀反馈*)",null,"AHU03D05_WVB",{"$f":"J113","v":"空调机组NJ-3AP(KT)4-5-水阀反馈"},{"$f":"AS112+1","v":30057}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)4-6-回风温度",{"$nulls":16},"NJ-3AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-6","03D06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH114,List!$B$3:$D$445,2,FALSE)&AJ114&\"_\"&VLOOKUP(AK114,List!$K$2:$M$447,2,FALSE)","v":"AHU03D06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM114&\" \"&\"AT%I\"&B113*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J114&\"*)\",\" \")","v":"LAHU03D06_RT AT%I116.0 :INT ; (*空调机组NJ-3AP(KT)4-6-回风温度*)"},"LAHU03D06_RT            AT%I116.0      :INT ; (*空调机组NJ-3AP(KT)4-6-回风温度*)",null,"AHU03D06_RT","空调机组NJ-3AP(KT)4-6-回风温度",{"$f":"AS113+1","v":30058}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),2,1))","v":0},4,null,4,"0V",{"$nulls":17},"NJ-3AP(KT)4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-6","03D06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH115,List!$B$3:$D$445,2,FALSE)&AJ115&\"_\"&VLOOKUP(AK115,List!$K$2:$M$447,2,FALSE)","v":"AHU03D06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM115&\" \"&\"AT%I\"&B113*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J115&\"*)\",\" \")","v":"LAHU03D06_WVB AT%I118.0 :INT ; (**)"},"LAHU03D06_WVB           AT%I118.0      :INT ; (**)",null,"AHU03D06_WVB",0,30059]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-3AP(KT)4-7-回风温度",{"$nulls":16},"NJ-3AP(KT)4-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-7","03D07","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH116,List!$B$3:$D$445,2,FALSE)&AJ116&\"_\"&VLOOKUP(AK116,List!$K$2:$M$447,2,FALSE)","v":"AHU03D07_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM116&\" \"&\"AT%I\"&B113*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J116&\"*)\",\" \")","v":"LAHU03D07_RT AT%I120.0 :INT ; (*空调机组NJ-3AP(KT)4-7-回风温度*)"},"LAHU03D07_RT            AT%I120.0      :INT ; (*空调机组NJ-3AP(KT)4-7-回风温度*)",null,"AHU03D07_RT","空调机组NJ-3AP(KT)4-7-回风温度",30060]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-3AP(KT)4-7-水阀反馈",{"$nulls":16},"NJ-3AP(KT)4-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL117,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL117,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-7","03D07","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH117,List!$B$3:$D$445,2,FALSE)&AJ117&\"_\"&VLOOKUP(AK117,List!$K$2:$M$447,2,FALSE)","v":"AHU03D07_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM117&\" \"&\"AT%I\"&B113*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J117&\"*)\",\" \")","v":"LAHU03D07_WVB AT%I122.0 :INT ; (*空调机组NJ-3AP(KT)4-7-水阀反馈*)"},"LAHU03D07_WVB           AT%I122.0      :INT ; (*空调机组NJ-3AP(KT)4-7-水阀反馈*)",null,"AHU03D07_WVB",{"$f":"J117","v":"空调机组NJ-3AP(KT)4-7-水阀反馈"},30061]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-3AP(KT)4-8-回风温度",{"$nulls":16},"NJ-3AP(KT)4-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL118,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL118,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-8","03D08","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH118,List!$B$3:$D$445,2,FALSE)&AJ118&\"_\"&VLOOKUP(AK118,List!$K$2:$M$447,2,FALSE)","v":"AHU03D08_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM118&\" \"&\"AT%I\"&B113*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J118&\"*)\",\" \")","v":"LAHU03D08_RT AT%I124.0 :INT ; (*空调机组NJ-3AP(KT)4-8-回风温度*)"},"LAHU03D08_RT            AT%I124.0      :INT ; (*空调机组NJ-3AP(KT)4-8-回风温度*)",null,"AHU03D08_RT","空调机组NJ-3AP(KT)4-8-回风温度",30062]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-3AP(KT)4-8-水阀反馈",{"$nulls":16},{"$f":"IF(AI119=\"\",\"\",AI119)","v":"NJ-3AP(KT)4-8"},{"$f":"_xlfn.IFNA(VLOOKUP(AL119,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL119,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-8","03D08","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH119,List!$B$3:$D$445,2,FALSE)&AJ119&\"_\"&VLOOKUP(AK119,List!$K$2:$M$447,2,FALSE)","v":"AHU03D08_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM119&\" \"&\"AT%I\"&B113*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J119&\"*)\",\" \")","v":"LAHU03D08_WVB AT%I126.0 :INT ; (*空调机组NJ-3AP(KT)4-8-水阀反馈*)"},"LAHU03D08_WVB           AT%I126.0      :INT ; (*空调机组NJ-3AP(KT)4-8-水阀反馈*)",null,"AHU03D08_WVB","空调机组NJ-3AP(KT)4-8-水阀反馈",30063]
[null,{"$f":"B50","v":0},{"$nulls":38},{"$f":"\"(* \"&B125&\"地址: \"&B122&\" *)\"","v":"(* IOM 0801U地址: 8 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH121&AA121&\"-\"&AK121","v":"空调机组NJ-3AP(KT)4-9-回风温度"},{"$nulls":16},{"$f":"IF(AI121=\"\",\"\",AI121)","v":"NJ-3AP(KT)4-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-9","03D09","回风温度",{"$f":"AH121&\"-\"&AK121","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH121,List!$B$3:$D$445,2,FALSE)&AJ121&\"_\"&VLOOKUP(AK121,List!$K$2:$M$447,2,FALSE)","v":"AHU03D09_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM121&\" \"&\"AT%I\"&B122*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J121&\"*)\",\" \")","v":"LAHU03D09_RT AT%I128.0 :INT ; (*空调机组NJ-3AP(KT)4-9-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121))),SEARCH(\":\",REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121)))))),\" \")","v":"LAHU03D09_RT            AT%I128.0      :INT ; (*空调机组NJ-3AP(KT)4-9-回风温度*)"},null,{"$f":"AM121","v":"AHU03D09_RT"},{"$f":"J121","v":"空调机组NJ-3AP(KT)4-9-回风温度"},{"$f":"30000+($B122*8+F121-1)","v":30064}]
[null,8,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-3AP(KT)4-9-水阀反馈",{"$nulls":16},{"$f":"IF(AI122=\"\",\"\",AI122)","v":"NJ-3AP(KT)4-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-9","03D09","水阀反馈",{"$f":"AH122&\"-\"&AK122","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH122,List!$B$3:$D$445,2,FALSE)&AJ122&\"_\"&VLOOKUP(AK122,List!$K$2:$M$447,2,FALSE)","v":"AHU03D09_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM122&\" \"&\"AT%I\"&B122*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J122&\"*)\",\" \")","v":"LAHU03D09_WVB AT%I130.0 :INT ; (*空调机组NJ-3AP(KT)4-9-水阀反馈*)"},"LAHU03D09_WVB           AT%I130.0      :INT ; (*空调机组NJ-3AP(KT)4-9-水阀反馈*)",null,"AHU03D09_WVB",{"$f":"J122","v":"空调机组NJ-3AP(KT)4-9-水阀反馈"},{"$f":"AS121+1","v":30065}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-3AP(KT)4-10-回风温度",{"$nulls":16},"NJ-3AP(KT)4-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-10","03D10","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH123,List!$B$3:$D$445,2,FALSE)&AJ123&\"_\"&VLOOKUP(AK123,List!$K$2:$M$447,2,FALSE)","v":"AHU03D10_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM123&\" \"&\"AT%I\"&B122*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J123&\"*)\",\" \")","v":"LAHU03D10_RT AT%I132.0 :INT ; (*空调机组NJ-3AP(KT)4-10-回风温度*)"},"LAHU03D10_RT            AT%I132.0      :INT ; (*空调机组NJ-3AP(KT)4-10-回风温度*)",null,"AHU03D10_RT","空调机组NJ-3AP(KT)4-10-回风温度",{"$f":"AS122+1","v":30066}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-3AP(KT)4-10-水阀反馈",{"$nulls":16},"NJ-3AP(KT)4-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-10","03D10","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH124,List!$B$3:$D$445,2,FALSE)&AJ124&\"_\"&VLOOKUP(AK124,List!$K$2:$M$447,2,FALSE)","v":"AHU03D10_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM124&\" \"&\"AT%I\"&B122*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J124&\"*)\",\" \")","v":"LAHU03D10_WVB AT%I134.0 :INT ; (*空调机组NJ-3AP(KT)4-10-水阀反馈*)"},"LAHU03D10_WVB           AT%I134.0      :INT ; (*空调机组NJ-3AP(KT)4-10-水阀反馈*)",null,"AHU03D10_WVB","空调机组NJ-3AP(KT)4-10-水阀反馈",30067]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-3AP(KT)4-11-回风温度",{"$nulls":16},"NJ-3AP(KT)4-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-11","03D11","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH125,List!$B$3:$D$445,2,FALSE)&AJ125&\"_\"&VLOOKUP(AK125,List!$K$2:$M$447,2,FALSE)","v":"AHU03D11_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM125&\" \"&\"AT%I\"&B122*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J125&\"*)\",\" \")","v":"LAHU03D11_RT AT%I136.0 :INT ; (*空调机组NJ-3AP(KT)4-11-回风温度*)"},"LAHU03D11_RT            AT%I136.0      :INT ; (*空调机组NJ-3AP(KT)4-11-回风温度*)",null,"AHU03D11_RT","空调机组NJ-3AP(KT)4-11-回风温度",30068]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-3AP(KT)4-11-水阀反馈",{"$nulls":16},"NJ-3AP(KT)4-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL126,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL126,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-11","03D11","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH126,List!$B$3:$D$445,2,FALSE)&AJ126&\"_\"&VLOOKUP(AK126,List!$K$2:$M$447,2,FALSE)","v":"AHU03D11_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM126&\" \"&\"AT%I\"&B122*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J126&\"*)\",\" \")","v":"LAHU03D11_WVB AT%I138.0 :INT ; (*空调机组NJ-3AP(KT)4-11-水阀反馈*)"},"LAHU03D11_WVB           AT%I138.0      :INT ; (*空调机组NJ-3AP(KT)4-11-水阀反馈*)",null,"AHU03D11_WVB",{"$f":"J126","v":"空调机组NJ-3AP(KT)4-11-水阀反馈"},30069]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","风机盘管NJ-3AP(KT)4-1-温度状态",{"$nulls":16},"NJ-3AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL127,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL127,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-3AP(KT)4-1","03D01","温度状态","风机盘管-温度状态",{"$f":"VLOOKUP(AH127,List!$B$3:$D$445,2,FALSE)&AJ127&\"_\"&VLOOKUP(AK127,List!$K$2:$M$447,2,FALSE)","v":"FCU03D01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM127&\" \"&\"AT%I\"&B122*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J127&\"*)\",\" \")","v":"LFCU03D01_T AT%I140.0 :INT ; (*风机盘管NJ-3AP(KT)4-1-温度状态*)"},"LFCU03D01_T             AT%I140.0      :INT ; (*风机盘管NJ-3AP(KT)4-1-温度状态*)",null,"FCU03D01_T","风机盘管NJ-3AP(KT)4-1-温度状态",30070]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},{"$f":"IF(AI128=\"\",\"\",AI128)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL128,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL128,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH128,List!$B$3:$D$445,2,FALSE)&AJ128&\"_\"&VLOOKUP(AK128,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM128&\" \"&\"AT%I\"&B122*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J128&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30071]
[null,{"$f":"B134","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B134&\"地址: \"&B131&\" *)\"","v":"(* IOM 0401A地址: 9 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH130&AA130&\"-\"&AK130","v":"空调机组NJ-3AP(KT)4-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI130=\"\",\"\",AI130)","v":"NJ-3AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL130,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL130,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-1","03D01","水阀控制",{"$f":"AH130&\"-\"&AK130","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH130,List!$B$3:$D$445,2,FALSE)&AJ130&\"_\"&VLOOKUP(AK130,List!$K$2:$M$447,2,FALSE)","v":"AHU03D01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM130&\" \"&\"AT%Q\"&B131*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J130&\"*)\",\" \")","v":"LAHU03D01_WVC AT%Q144.0 :INT ; (*空调机组NJ-3AP(KT)4-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN130,SEARCH(\"AT%\",AN130),,REPT(\" \",25-SEARCH(\"AT%\",AN130))),SEARCH(\":\",REPLACE(AN130,SEARCH(\"AT%\",AN130),,REPT(\" \",25-SEARCH(\"AT%\",AN130)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN130,SEARCH(\"AT%\",AN130),,REPT(\" \",25-SEARCH(\"AT%\",AN130)))))),\" \")","v":"LAHU03D01_WVC           AT%Q144.0      :INT ; (*空调机组NJ-3AP(KT)4-1-水阀控制*)"},null,{"$f":"AM130","v":"AHU03D01_WVC"},{"$f":"J130","v":"空调机组NJ-3AP(KT)4-1-水阀控制"},{"$f":"40000+($B131*8+F130-1)","v":40072}]
[null,9,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH131&AA131&\"-\"&AK131","v":"空调机组NJ-3AP(KT)4-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI131=\"\",\"\",AI131)","v":"NJ-3AP(KT)4-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL131,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL131,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-2","03D02","水阀控制",{"$f":"AH131&\"-\"&AK131","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH131,List!$B$3:$D$445,2,FALSE)&AJ131&\"_\"&VLOOKUP(AK131,List!$K$2:$M$447,2,FALSE)","v":"AHU03D02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM131&\" \"&\"AT%Q\"&B131*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J131&\"*)\",\" \")","v":"LAHU03D02_WVC AT%Q146.0 :INT ; (*空调机组NJ-3AP(KT)4-2-水阀控制*)"},"LAHU03D02_WVC           AT%Q146.0      :INT ; (*空调机组NJ-3AP(KT)4-2-水阀控制*)",null,"AHU03D02_WVC",{"$f":"J131","v":"空调机组NJ-3AP(KT)4-2-水阀控制"},{"$f":"AS130+1","v":40073}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH132&AA132&\"-\"&AK132","v":"空调机组NJ-3AP(KT)4-3-水阀控制"},{"$nulls":16},"NJ-3AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL132,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL132,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-3","03D03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH132,List!$B$3:$D$445,2,FALSE)&AJ132&\"_\"&VLOOKUP(AK132,List!$K$2:$M$447,2,FALSE)","v":"AHU03D03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM132&\" \"&\"AT%Q\"&B131*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J132&\"*)\",\" \")","v":"LAHU03D03_WVC AT%Q148.0 :INT ; (*空调机组NJ-3AP(KT)4-3-水阀控制*)"},"LAHU03D03_WVC           AT%Q148.0      :INT ; (*空调机组NJ-3AP(KT)4-3-水阀控制*)",null,"AHU03D03_WVC","空调机组NJ-3AP(KT)4-3-水阀控制",{"$f":"AS131+1","v":40074}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH133&AA133&\"-\"&AK133","v":"空调机组NJ-3AP(KT)4-4-水阀控制"},{"$nulls":16},"NJ-3AP(KT)4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL133,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL133,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-4","03D04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH133,List!$B$3:$D$445,2,FALSE)&AJ133&\"_\"&VLOOKUP(AK133,List!$K$2:$M$447,2,FALSE)","v":"AHU03D04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM133&\" \"&\"AT%Q\"&B131*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J133&\"*)\",\" \")","v":"LAHU03D04_WVC AT%Q150.0 :INT ; (*空调机组NJ-3AP(KT)4-4-水阀控制*)"},"LAHU03D04_WVC           AT%Q150.0      :INT ; (*空调机组NJ-3AP(KT)4-4-水阀控制*)",null,"AHU03D04_WVC","空调机组NJ-3AP(KT)4-4-水阀控制",40075]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B143","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B143&\"地址: \"&B140&\" *)\"","v":"(* IOM 0401A地址: 10 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH139&AA139&\"-\"&AK139","v":"空调机组NJ-3AP(KT)4-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI139=\"\",\"\",AI139)","v":"NJ-3AP(KT)4-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL139,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL139,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-5","03D05","水阀控制",{"$f":"AH139&\"-\"&AK139","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH139,List!$B$3:$D$445,2,FALSE)&AJ139&\"_\"&VLOOKUP(AK139,List!$K$2:$M$447,2,FALSE)","v":"AHU03D05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM139&\" \"&\"AT%Q\"&B140*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J139&\"*)\",\" \")","v":"LAHU03D05_WVC AT%Q160.0 :INT ; (*空调机组NJ-3AP(KT)4-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN139,SEARCH(\"AT%\",AN139),,REPT(\" \",25-SEARCH(\"AT%\",AN139))),SEARCH(\":\",REPLACE(AN139,SEARCH(\"AT%\",AN139),,REPT(\" \",25-SEARCH(\"AT%\",AN139)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN139,SEARCH(\"AT%\",AN139),,REPT(\" \",25-SEARCH(\"AT%\",AN139)))))),\" \")","v":"LAHU03D05_WVC           AT%Q160.0      :INT ; (*空调机组NJ-3AP(KT)4-5-水阀控制*)"},null,{"$f":"AM139","v":"AHU03D05_WVC"},{"$f":"J139","v":"空调机组NJ-3AP(KT)4-5-水阀控制"},{"$f":"40000+($B140*8+F139-1)","v":40080}]
[null,10,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH140&AA140&\"-\"&AK140","v":"空调机组NJ-3AP(KT)4-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI140=\"\",\"\",AI140)","v":"NJ-3AP(KT)4-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL140,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL140,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-6","03D06","水阀控制",{"$f":"AH140&\"-\"&AK140","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH140,List!$B$3:$D$445,2,FALSE)&AJ140&\"_\"&VLOOKUP(AK140,List!$K$2:$M$447,2,FALSE)","v":"AHU03D06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM140&\" \"&\"AT%Q\"&B140*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J140&\"*)\",\" \")","v":"LAHU03D06_WVC AT%Q162.0 :INT ; (*空调机组NJ-3AP(KT)4-6-水阀控制*)"},"LAHU03D06_WVC           AT%Q162.0      :INT ; (*空调机组NJ-3AP(KT)4-6-水阀控制*)",null,"AHU03D06_WVC",{"$f":"J140","v":"空调机组NJ-3AP(KT)4-6-水阀控制"},{"$f":"AS139+1","v":40081}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH141&AA141&\"-\"&AK141","v":"空调机组NJ-3AP(KT)4-7-水阀控制"},{"$nulls":16},"NJ-3AP(KT)4-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL141,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL141,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-7","03D07","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH141,List!$B$3:$D$445,2,FALSE)&AJ141&\"_\"&VLOOKUP(AK141,List!$K$2:$M$447,2,FALSE)","v":"AHU03D07_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM141&\" \"&\"AT%Q\"&B140*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J141&\"*)\",\" \")","v":"LAHU03D07_WVC AT%Q164.0 :INT ; (*空调机组NJ-3AP(KT)4-7-水阀控制*)"},"LAHU03D07_WVC           AT%Q164.0      :INT ; (*空调机组NJ-3AP(KT)4-7-水阀控制*)",null,"AHU03D07_WVC","空调机组NJ-3AP(KT)4-7-水阀控制",{"$f":"AS140+1","v":40082}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH142&AA142&\"-\"&AK142","v":"空调机组NJ-3AP(KT)4-8-水阀控制"},{"$nulls":16},"NJ-3AP(KT)4-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL142,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL142,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-8","03D08","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH142,List!$B$3:$D$445,2,FALSE)&AJ142&\"_\"&VLOOKUP(AK142,List!$K$2:$M$447,2,FALSE)","v":"AHU03D08_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM142&\" \"&\"AT%Q\"&B140*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J142&\"*)\",\" \")","v":"LAHU03D08_WVC AT%Q166.0 :INT ; (*空调机组NJ-3AP(KT)4-8-水阀控制*)"},"LAHU03D08_WVC           AT%Q166.0      :INT ; (*空调机组NJ-3AP(KT)4-8-水阀控制*)",null,"AHU03D08_WVC","空调机组NJ-3AP(KT)4-8-水阀控制",40083]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},{"$f":"AH143&\"-\"&AK143","v":"-"}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B142=20,1,IF(B142=50,10,IF(B142=125,11,IF(B142=250,100,IF(B142=500,101,IF(B142=800,110,IF(B142=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B142=20,1,IF(B142=50,10,IF(B142=125,11,IF(B142=250,100,IF(B142=500,101,IF(B142=800,110,IF(B142=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B142=20,1,IF(B142=50,10,IF(B142=125,11,IF(B142=250,100,IF(B142=500,101,IF(B142=800,110,IF(B142=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B142=20,1,IF(B142=50,10,IF(B142=125,11,IF(B142=250,100,IF(B142=500,101,IF(B142=800,110,IF(B142=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B142=20,1,IF(B142=50,10,IF(B142=125,11,IF(B142=250,100,IF(B142=500,101,IF(B142=800,110,IF(B142=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B142=20,1,IF(B142=50,10,IF(B142=125,11,IF(B142=250,100,IF(B142=500,101,IF(B142=800,110,IF(B142=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B152","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B152&\"地址: \"&B149&\" *)\"","v":"(* IOM 0401A地址: 11 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH148&AA148&\"-\"&AK148","v":"空调机组NJ-3AP(KT)4-9-水阀控制"},{"$nulls":16},{"$f":"IF(AI148=\"\",\"\",AI148)","v":"NJ-3AP(KT)4-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL148,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL148,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-9","03D09","水阀控制",{"$f":"AH148&\"-\"&AK148","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH148,List!$B$3:$D$445,2,FALSE)&AJ148&\"_\"&VLOOKUP(AK148,List!$K$2:$M$447,2,FALSE)","v":"AHU03D09_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM148&\" \"&\"AT%Q\"&B149*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J148&\"*)\",\" \")","v":"LAHU03D09_WVC AT%Q176.0 :INT ; (*空调机组NJ-3AP(KT)4-9-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN148,SEARCH(\"AT%\",AN148),,REPT(\" \",25-SEARCH(\"AT%\",AN148))),SEARCH(\":\",REPLACE(AN148,SEARCH(\"AT%\",AN148),,REPT(\" \",25-SEARCH(\"AT%\",AN148)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN148,SEARCH(\"AT%\",AN148),,REPT(\" \",25-SEARCH(\"AT%\",AN148)))))),\" \")","v":"LAHU03D09_WVC           AT%Q176.0      :INT ; (*空调机组NJ-3AP(KT)4-9-水阀控制*)"},null,{"$f":"AM148","v":"AHU03D09_WVC"},{"$f":"J148","v":"空调机组NJ-3AP(KT)4-9-水阀控制"},{"$f":"40000+($B149*8+F148-1)","v":40088}]
[null,11,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH149&AA149&\"-\"&AK149","v":"空调机组NJ-3AP(KT)4-10-水阀控制"},{"$nulls":16},{"$f":"IF(AI149=\"\",\"\",AI149)","v":"NJ-3AP(KT)4-10"},{"$f":"_xlfn.IFNA(VLOOKUP(AL149,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL149,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-10","03D10","水阀控制",{"$f":"AH149&\"-\"&AK149","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH149,List!$B$3:$D$445,2,FALSE)&AJ149&\"_\"&VLOOKUP(AK149,List!$K$2:$M$447,2,FALSE)","v":"AHU03D10_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM149&\" \"&\"AT%Q\"&B149*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J149&\"*)\",\" \")","v":"LAHU03D10_WVC AT%Q178.0 :INT ; (*空调机组NJ-3AP(KT)4-10-水阀控制*)"},"LAHU03D10_WVC           AT%Q178.0      :INT ; (*空调机组NJ-3AP(KT)4-10-水阀控制*)",null,"AHU03D10_WVC",{"$f":"J149","v":"空调机组NJ-3AP(KT)4-10-水阀控制"},{"$f":"AS148+1","v":40089}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH150&AA150&\"-\"&AK150","v":"空调机组NJ-3AP(KT)4-11-水阀控制"},{"$nulls":16},"NJ-3AP(KT)4-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL150,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL150,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)4-11","03D11","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH150,List!$B$3:$D$445,2,FALSE)&AJ150&\"_\"&VLOOKUP(AK150,List!$K$2:$M$447,2,FALSE)","v":"AHU03D11_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM150&\" \"&\"AT%Q\"&B149*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J150&\"*)\",\" \")","v":"LAHU03D11_WVC AT%Q180.0 :INT ; (*空调机组NJ-3AP(KT)4-11-水阀控制*)"},"LAHU03D11_WVC           AT%Q180.0      :INT ; (*空调机组NJ-3AP(KT)4-11-水阀控制*)",null,"AHU03D11_WVC","空调机组NJ-3AP(KT)4-11-水阀控制",{"$f":"AS149+1","v":40090}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH151&AA151&\"-\"&AK151","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL151,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL151,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH151,List!$B$3:$D$445,2,FALSE)&AJ151&\"_\"&VLOOKUP(AK151,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM151&\" \"&\"AT%Q\"&B149*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J151&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40091]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B151=20,1,IF(B151=50,10,IF(B151=125,11,IF(B151=250,100,IF(B151=500,101,IF(B151=800,110,IF(B151=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B151=20,1,IF(B151=50,10,IF(B151=125,11,IF(B151=250,100,IF(B151=500,101,IF(B151=800,110,IF(B151=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B151=20,1,IF(B151=50,10,IF(B151=125,11,IF(B151=250,100,IF(B151=500,101,IF(B151=800,110,IF(B151=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B151=20,1,IF(B151=50,10,IF(B151=125,11,IF(B151=250,100,IF(B151=500,101,IF(B151=800,110,IF(B151=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B151=20,1,IF(B151=50,10,IF(B151=125,11,IF(B151=250,100,IF(B151=500,101,IF(B151=800,110,IF(B151=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B151=20,1,IF(B151=50,10,IF(B151=125,11,IF(B151=250,100,IF(B151=500,101,IF(B151=800,110,IF(B151=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L404","index":31,"n_rows":84,"n_cols":45,"rows_kept":84,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[41,5,41,6],[41,9,41,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[4,1,5,1],[11,1,22,1],[28,1,39,1],[45,1,48,1],[54,1,65,1],[71,1,74,1],[80,1,83,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4],[32,2,39,4],[58,2,65,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L22",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 12 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH8&AA8&\"-\"&AK8","v":"空调机组NJ-4AP(KT)4-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-4AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-1","04D01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH8,List!$B$3:$D$445,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,List!$K$2:$M$447,2,FALSE)","v":"AHU04D01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LAHU04D01_R AT%I192.0 :BOOL; (*空调机组NJ-4AP(KT)4-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LAHU04D01_R             AT%I192.0      :BOOL; (*空调机组NJ-4AP(KT)4-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L22\\L22AHU04D01_R"},{"$f":"J8","v":"空调机组NJ-4AP(KT)4-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":11536}]
[null,12,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-4AP(KT)4-1-故障状态",{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-4AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-1","04D01","故障状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU04D01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU04D01_F AT%I192.1 :BOOL; (*空调机组NJ-4AP(KT)4-1-故障状态*)"},"LAHU04D01_F             AT%I192.1      :BOOL; (*空调机组NJ-4AP(KT)4-1-故障状态*)",null,"L22\\L22AHU04D01_F",{"$f":"J9","v":"空调机组NJ-4AP(KT)4-1-故障状态"},{"$f":"AS8+1","v":11537}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},3,null,5,6,"空调机组NJ-4AP(KT)4-1-自动状态",{"$nulls":16},"NJ-4AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-1","04D01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU04D01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU04D01_A AT%I192.2 :BOOL; (*空调机组NJ-4AP(KT)4-1-自动状态*)"},"LAHU04D01_A             AT%I192.2      :BOOL; (*空调机组NJ-4AP(KT)4-1-自动状态*)",null,"L22\\L22AHU04D01_A","空调机组NJ-4AP(KT)4-1-自动状态",{"$f":"AS9+1","v":11538}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-4AP(KT)4-1-风机压差",{"$nulls":16},"NJ-4AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-1","04D01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU04D01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU04D01_FPS AT%I192.3 :BOOL; (*空调机组NJ-4AP(KT)4-1-风机压差*)"},"LAHU04D01_FPS           AT%I192.3      :BOOL; (*空调机组NJ-4AP(KT)4-1-风机压差*)",null,"L22\\L22AHU04D01_FPS","空调机组NJ-4AP(KT)4-1-风机压差",11539]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-4AP(KT)4-2-运行状态",{"$nulls":16},"NJ-4AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-2","04D02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU04D02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU04D02_R AT%I192.4 :BOOL; (*空调机组NJ-4AP(KT)4-2-运行状态*)"},"LAHU04D02_R             AT%I192.4      :BOOL; (*空调机组NJ-4AP(KT)4-2-运行状态*)",null,"L22\\L22AHU04D02_R","空调机组NJ-4AP(KT)4-2-运行状态",11540]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-4AP(KT)4-2-故障状态",{"$nulls":16},"NJ-4AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-2","04D02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU04D02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU04D02_F AT%I192.5 :BOOL; (*空调机组NJ-4AP(KT)4-2-故障状态*)"},"LAHU04D02_F             AT%I192.5      :BOOL; (*空调机组NJ-4AP(KT)4-2-故障状态*)",null,"L22\\L22AHU04D02_F","空调机组NJ-4AP(KT)4-2-故障状态",11541]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-4AP(KT)4-2-自动状态",{"$nulls":16},"NJ-4AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-2","04D02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU04D02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU04D02_A AT%I192.6 :BOOL; (*空调机组NJ-4AP(KT)4-2-自动状态*)"},"LAHU04D02_A             AT%I192.6      :BOOL; (*空调机组NJ-4AP(KT)4-2-自动状态*)",null,"L22\\L22AHU04D02_A","空调机组NJ-4AP(KT)4-2-自动状态",11542]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-4AP(KT)4-2-风机压差",{"$nulls":16},"NJ-4AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-2","04D02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU04D02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU04D02_FPS AT%I192.7 :BOOL; (*空调机组NJ-4AP(KT)4-2-风机压差*)"},"LAHU04D02_FPS           AT%I192.7      :BOOL; (*空调机组NJ-4AP(KT)4-2-风机压差*)",null,"L22\\L22AHU04D02_FPS","空调机组NJ-4AP(KT)4-2-风机压差",11543]
[{"$nulls":5},9,null,17,18,"空调机组NJ-4AP(KT)4-3-运行状态",{"$nulls":16},"NJ-4AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-3","04D03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU04D03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU04D03_R AT%I193.0 :BOOL; (*空调机组NJ-4AP(KT)4-3-运行状态*)"},"LAHU04D03_R             AT%I193.0      :BOOL; (*空调机组NJ-4AP(KT)4-3-运行状态*)",null,"L22\\L22AHU04D03_R","空调机组NJ-4AP(KT)4-3-运行状态",11544]
[{"$nulls":5},10,null,19,20,"空调机组NJ-4AP(KT)4-3-故障状态",{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-4AP(KT)4-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-3","04D03","故障状态",{"$f":"AH17&\"-\"&AK17","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU04D03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU04D03_F AT%I193.1 :BOOL; (*空调机组NJ-4AP(KT)4-3-故障状态*)"},"LAHU04D03_F             AT%I193.1      :BOOL; (*空调机组NJ-4AP(KT)4-3-故障状态*)",null,"L22\\L22AHU04D03_F","空调机组NJ-4AP(KT)4-3-故障状态",11545]
[{"$nulls":5},11,null,21,22,"空调机组NJ-4AP(KT)4-3-自动状态",{"$nulls":16},"NJ-4AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-3","04D03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU04D03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU04D03_A AT%I193.2 :BOOL; (*空调机组NJ-4AP(KT)4-3-自动状态*)"},"LAHU04D03_A             AT%I193.2      :BOOL; (*空调机组NJ-4AP(KT)4-3-自动状态*)",null,"L22\\L22AHU04D03_A","空调机组NJ-4AP(KT)4-3-自动状态",11546]
[{"$nulls":5},12,null,23,24,"空调机组NJ-4AP(KT)4-3-风机压差",{"$nulls":16},"NJ-4AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-3","04D03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU04D03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU04D03_FPS AT%I193.3 :BOOL; (*空调机组NJ-4AP(KT)4-3-风机压差*)"},"LAHU04D03_FPS           AT%I193.3      :BOOL; (*空调机组NJ-4AP(KT)4-3-风机压差*)",null,"L22\\L22AHU04D03_FPS","空调机组NJ-4AP(KT)4-3-风机压差",11547]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-4AL4-1-运行状态",{"$nulls":16},"NJ-4AL4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-1","04D01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"LCB04D01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LLCB04D01_R AT%I193.4 :BOOL; (*照明控制箱NJ-4AL4-1-运行状态*)"},"LLCB04D01_R             AT%I193.4      :BOOL; (*照明控制箱NJ-4AL4-1-运行状态*)",null,"L22\\L22LCB04D01_R","照明控制箱NJ-4AL4-1-运行状态",11548]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-4AL4-1-自动状态",{"$nulls":16},"NJ-4AL4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-1","04D01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"LCB04D01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LLCB04D01_A AT%I193.5 :BOOL; (*照明控制箱NJ-4AL4-1-自动状态*)"},"LLCB04D01_A             AT%I193.5      :BOOL; (*照明控制箱NJ-4AL4-1-自动状态*)",null,"L22\\L22LCB04D01_A","照明控制箱NJ-4AL4-1-自动状态",11549]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-4AL4-2-运行状态",{"$nulls":16},"NJ-4AL4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-2","04D02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"LCB04D02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LLCB04D02_R AT%I193.6 :BOOL; (*照明控制箱NJ-4AL4-2-运行状态*)"},"LLCB04D02_R             AT%I193.6      :BOOL; (*照明控制箱NJ-4AL4-2-运行状态*)",null,"L22\\L22LCB04D02_R","照明控制箱NJ-4AL4-2-运行状态",11550]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-4AL4-2-自动状态",{"$nulls":16},"NJ-4AL4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-2","04D02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"LCB04D02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LLCB04D02_A AT%I193.7 :BOOL; (*照明控制箱NJ-4AL4-2-自动状态*)"},"LLCB04D02_A             AT%I193.7      :BOOL; (*照明控制箱NJ-4AL4-2-自动状态*)",null,"L22\\L22LCB04D02_A","照明控制箱NJ-4AL4-2-自动状态",11551]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 1601R地址: 13 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH25&AA25&\"-\"&AK25","v":"照明控制箱NJ-4AL4-3-运行状态"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-4AL4-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-3","04D03","运行状态",{"$f":"AH25&\"-\"&AK25","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"LCB04D03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LLCB04D03_R AT%I208.0 :BOOL; (*照明控制箱NJ-4AL4-3-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LLCB04D03_R             AT%I208.0      :BOOL; (*照明控制箱NJ-4AL4-3-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L22\\L22LCB04D03_R"},{"$f":"J25","v":"照明控制箱NJ-4AL4-3-运行状态"},{"$f":"10000+($B26*16*8+F25-1)","v":11664}]
[null,13,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},2,null,3,4,"照明控制箱NJ-4AL4-3-自动状态",{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-4AL4-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-3","04D03","自动状态",{"$f":"AH26&\"-\"&AK26","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"LCB04D03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LLCB04D03_A AT%I208.1 :BOOL; (*照明控制箱NJ-4AL4-3-自动状态*)"},"LLCB04D03_A             AT%I208.1      :BOOL; (*照明控制箱NJ-4AL4-3-自动状态*)",null,"L22\\L22LCB04D03_A",{"$f":"J26","v":"照明控制箱NJ-4AL4-3-自动状态"},{"$f":"AS25+1","v":11665}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},3,null,5,6,"照明控制箱NJ-4AL4-4-运行状态",{"$nulls":16},"NJ-4AL4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-4","04D04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"LCB04D04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LLCB04D04_R AT%I208.2 :BOOL; (*照明控制箱NJ-4AL4-4-运行状态*)"},"LLCB04D04_R             AT%I208.2      :BOOL; (*照明控制箱NJ-4AL4-4-运行状态*)",null,"L22\\L22LCB04D04_R","照明控制箱NJ-4AL4-4-运行状态",{"$f":"AS26+1","v":11666}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},4,null,7,8,"照明控制箱NJ-4AL4-4-自动状态",{"$nulls":16},"NJ-4AL4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-4","04D04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"LCB04D04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LLCB04D04_A AT%I208.3 :BOOL; (*照明控制箱NJ-4AL4-4-自动状态*)"},"LLCB04D04_A             AT%I208.3      :BOOL; (*照明控制箱NJ-4AL4-4-自动状态*)",null,"L22\\L22LCB04D04_A","照明控制箱NJ-4AL4-4-自动状态",11667]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-4AL4-5-运行状态",{"$nulls":16},"NJ-4AL4-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-5","04D05","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"LCB04D05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LLCB04D05_R AT%I208.4 :BOOL; (*照明控制箱NJ-4AL4-5-运行状态*)"},"LLCB04D05_R             AT%I208.4      :BOOL; (*照明控制箱NJ-4AL4-5-运行状态*)",null,"L22\\L22LCB04D05_R","照明控制箱NJ-4AL4-5-运行状态",11668]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-4AL4-5-自动状态",{"$nulls":16},"NJ-4AL4-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-5","04D05","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"LCB04D05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LLCB04D05_A AT%I208.5 :BOOL; (*照明控制箱NJ-4AL4-5-自动状态*)"},"LLCB04D05_A             AT%I208.5      :BOOL; (*照明控制箱NJ-4AL4-5-自动状态*)",null,"L22\\L22LCB04D05_A","照明控制箱NJ-4AL4-5-自动状态",11669]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"照明控制箱NJ-4AL4-6-运行状态",{"$nulls":16},"NJ-4AL4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-6","04D06","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"LCB04D06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LLCB04D06_R AT%I208.6 :BOOL; (*照明控制箱NJ-4AL4-6-运行状态*)"},"LLCB04D06_R             AT%I208.6      :BOOL; (*照明控制箱NJ-4AL4-6-运行状态*)",null,"L22\\L22LCB04D06_R","照明控制箱NJ-4AL4-6-运行状态",11670]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"照明控制箱NJ-4AL4-6-自动状态",{"$nulls":16},"NJ-4AL4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-6","04D06","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"LCB04D06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LLCB04D06_A AT%I208.7 :BOOL; (*照明控制箱NJ-4AL4-6-自动状态*)"},"LLCB04D06_A             AT%I208.7      :BOOL; (*照明控制箱NJ-4AL4-6-自动状态*)",null,"L22\\L22LCB04D06_A","照明控制箱NJ-4AL4-6-自动状态",11671]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-4AL4-7-运行状态",{"$nulls":16},"NJ-4AL4-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-7","04D07","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"LCB04D07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B26*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LLCB04D07_R AT%I209.0 :BOOL; (*照明控制箱NJ-4AL4-7-运行状态*)"},"LLCB04D07_R             AT%I209.0      :BOOL; (*照明控制箱NJ-4AL4-7-运行状态*)",null,"L22\\L22LCB04D07_R","照明控制箱NJ-4AL4-7-运行状态",11672]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-4AL4-7-自动状态",{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-4AL4-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-7","04D07","自动状态",{"$f":"AH34&\"-\"&AK34","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"LCB04D07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B26*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LLCB04D07_A AT%I209.1 :BOOL; (*照明控制箱NJ-4AL4-7-自动状态*)"},"LLCB04D07_A             AT%I209.1      :BOOL; (*照明控制箱NJ-4AL4-7-自动状态*)",null,"L22\\L22LCB04D07_A",{"$f":"J34","v":"照明控制箱NJ-4AL4-7-自动状态"},11673]
[{"$nulls":5},11,null,21,22,"照明控制箱NJ-4AL4-8-运行状态",{"$nulls":16},"NJ-4AL4-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-8","04D08","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"LCB04D08_R"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B26*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LLCB04D08_R AT%I209.2 :BOOL; (*照明控制箱NJ-4AL4-8-运行状态*)"},"LLCB04D08_R             AT%I209.2      :BOOL; (*照明控制箱NJ-4AL4-8-运行状态*)",null,"L22\\L22LCB04D08_R","照明控制箱NJ-4AL4-8-运行状态",11674]
[{"$nulls":5},12,null,23,24,"照明控制箱NJ-4AL4-8-自动状态",{"$nulls":16},"NJ-4AL4-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-8","04D08","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"LCB04D08_A"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B26*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LLCB04D08_A AT%I209.3 :BOOL; (*照明控制箱NJ-4AL4-8-自动状态*)"},"LLCB04D08_A             AT%I209.3      :BOOL; (*照明控制箱NJ-4AL4-8-自动状态*)",null,"L22\\L22LCB04D08_A","照明控制箱NJ-4AL4-8-自动状态",11675]
[{"$nulls":5},13,null,25,26,"排风机NJ-4AP(KT)4-1-运行状态",{"$nulls":16},"NJ-4AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)4-1","04D01","运行状态","排风机-运行状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"EAF04D01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B26*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LEAF04D01_R AT%I209.4 :BOOL; (*排风机NJ-4AP(KT)4-1-运行状态*)"},"LEAF04D01_R             AT%I209.4      :BOOL; (*排风机NJ-4AP(KT)4-1-运行状态*)",null,"L22\\L22EAF04D01_R","排风机NJ-4AP(KT)4-1-运行状态",11676]
[{"$nulls":5},14,null,27,28,"排风机NJ-4AP(KT)4-1-故障状态",{"$nulls":16},"NJ-4AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)4-1","04D01","故障状态","排风机-故障状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"EAF04D01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B26*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LEAF04D01_F AT%I209.5 :BOOL; (*排风机NJ-4AP(KT)4-1-故障状态*)"},"LEAF04D01_F             AT%I209.5      :BOOL; (*排风机NJ-4AP(KT)4-1-故障状态*)",null,"L22\\L22EAF04D01_F","排风机NJ-4AP(KT)4-1-故障状态",11677]
[{"$nulls":5},15,null,29,30,"排风机NJ-4AP(KT)4-1-自动状态",{"$nulls":16},"NJ-4AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)4-1","04D01","自动状态","排风机-自动状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"EAF04D01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B26*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LEAF04D01_A AT%I209.6 :BOOL; (*排风机NJ-4AP(KT)4-1-自动状态*)"},"LEAF04D01_A             AT%I209.6      :BOOL; (*排风机NJ-4AP(KT)4-1-自动状态*)",null,"L22\\L22EAF04D01_A","排风机NJ-4AP(KT)4-1-自动状态",11678]
[".",{"$nulls":4},16,null,31,32,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B26*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN40,SEARCH(\"AT%\",AN40),,REPT(\" \",30-SEARCH(\"AT%\",AN40))),SEARCH(\":\",REPLACE(AN40,SEARCH(\"AT%\",AN40),,REPT(\" \",30-SEARCH(\"AT%\",AN40)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN40,SEARCH(\"AT%\",AN40),,REPT(\" \",25-SEARCH(\"AT%\",AN40)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",11679]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B46&\"地址: \"&B43&\" *)\"","v":"(* IOM 0801R 地址: 14 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH42&AA42&\"-\"&AK42","v":"风机盘管NJ-4AP(KT)4-1-运行状态"},{"$nulls":16},{"$f":"IF(AI42=\"\",\"\",AI42)","v":"NJ-4AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)4-1","04D01","运行状态",{"$f":"AH42&\"-\"&AK42","v":"风机盘管-运行状态"},{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":"FCU04D01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%I\"&B43*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":"LFCU04D01_R AT%I224.0 :BOOL; (*风机盘管NJ-4AP(KT)4-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42))),SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))))),\" \")","v":"LFCU04D01_R             AT%I224.0      :BOOL; (*风机盘管NJ-4AP(KT)4-1-运行状态*)"},null,{"$f":"AM42","v":"FCU04D01_R"},{"$f":"J42","v":"风机盘管NJ-4AP(KT)4-1-运行状态"},{"$f":"10000+($B43*16*8+F42-1)","v":11792}]
[null,14,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},2,null,2,"C",{"$f":"AH43&AA43&\"-\"&AK43","v":"风机盘管NJ-4AP(KT)4-1-自动状态"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-4AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)4-1","04D01","自动状态",{"$f":"AH43&\"-\"&AK43","v":"风机盘管-自动状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"FCU04D01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B43*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LFCU04D01_A AT%I224.1 :BOOL; (*风机盘管NJ-4AP(KT)4-1-自动状态*)"},"LFCU04D01_A             AT%I224.1      :BOOL; (*风机盘管NJ-4AP(KT)4-1-自动状态*)",null,{"$f":"AM43","v":"FCU04D01_A"},{"$f":"J43","v":"风机盘管NJ-4AP(KT)4-1-自动状态"},{"$f":"AS42+1","v":11793}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":1},3,null,3,"C",{"$f":"AH44&AA44&\"-\"&AK44","v":"风机盘管NJ-4AP(KT)4-1-电磁阀开启状态"},{"$nulls":16},"NJ-4AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)4-1","04D01","电磁阀开启状态","风机盘管-电磁阀开启状态",{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"FCU04D01_EVR"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B43*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LFCU04D01_EVR AT%I224.2 :BOOL; (*风机盘管NJ-4AP(KT)4-1-电磁阀开启状态*)"},"LFCU04D01_EVR           AT%I224.2      :BOOL; (*风机盘管NJ-4AP(KT)4-1-电磁阀开启状态*)",null,"FCU04D01_EVR","风机盘管NJ-4AP(KT)4-1-电磁阀开启状态",{"$f":"AS43+1","v":11794}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},4,null,4,"C",{"$f":"AH45&AA45&\"-\"&AK45","v":"风机盘管NJ-4AP(KT)4-1-电磁阀自动状态"},{"$nulls":16},"NJ-4AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)4-1","04D01","电磁阀自动状态","风机盘管-电磁阀自动状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"FCU04D01_EVA"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B43*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LFCU04D01_EVA AT%I224.3 :BOOL; (*风机盘管NJ-4AP(KT)4-1-电磁阀自动状态*)"},"LFCU04D01_EVA           AT%I224.3      :BOOL; (*风机盘管NJ-4AP(KT)4-1-电磁阀自动状态*)",null,"FCU04D01_EVA","风机盘管NJ-4AP(KT)4-1-电磁阀自动状态",11795]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},5,null,5,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B43*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11796]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B43*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11797]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B43*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11798]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B43*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11799]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B55&\"地址: \"&B52&\" *)\"","v":"(* IOM 1601D地址: 15 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH51&AA51&\"-\"&AK51","v":"空调机组NJ-4AP(KT)4-1-启停控制"},{"$nulls":16},{"$f":"IF(AI51=\"\",\"\",AI51)","v":"NJ-4AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-1","04D01","启停控制",{"$f":"AH51&\"-\"&AK51","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"AHU04D01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%Q\"&B52*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LAHU04D01_C AT%Q240.0 :BOOL; (*空调机组NJ-4AP(KT)4-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN51,SEARCH(\"AT%\",AN51),,REPT(\" \",25-SEARCH(\"AT%\",AN51))),SEARCH(\":\",REPLACE(AN51,SEARCH(\"AT%\",AN51),,REPT(\" \",25-SEARCH(\"AT%\",AN51)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN51,SEARCH(\"AT%\",AN51),,REPT(\" \",25-SEARCH(\"AT%\",AN51)))))),\" \")","v":"LAHU04D01_C             AT%Q240.0      :BOOL; (*空调机组NJ-4AP(KT)4-1-启停控制*)"},null,{"$f":"AM51","v":"AHU04D01_C"},{"$f":"J51","v":"空调机组NJ-4AP(KT)4-1-启停控制"},{"$f":"($B52*16*8+F51-1)","v":1920}]
[null,15,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-4AP(KT)4-2-启停控制",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-4AP(KT)4-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-2","04D02","启停控制",{"$f":"AH52&\"-\"&AK52","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"AHU04D02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%Q\"&B52*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LAHU04D02_C AT%Q240.1 :BOOL; (*空调机组NJ-4AP(KT)4-2-启停控制*)"},"LAHU04D02_C             AT%Q240.1      :BOOL; (*空调机组NJ-4AP(KT)4-2-启停控制*)",null,"AHU04D02_C",{"$f":"J52","v":"空调机组NJ-4AP(KT)4-2-启停控制"},{"$f":"AS51+1","v":1921}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-4AP(KT)4-3-启停控制",{"$nulls":16},"NJ-4AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-3","04D03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"AHU04D03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%Q\"&B52*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LAHU04D03_C AT%Q240.2 :BOOL; (*空调机组NJ-4AP(KT)4-3-启停控制*)"},"LAHU04D03_C             AT%Q240.2      :BOOL; (*空调机组NJ-4AP(KT)4-3-启停控制*)",null,"AHU04D03_C","空调机组NJ-4AP(KT)4-3-启停控制",{"$f":"AS52+1","v":1922}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","照明控制箱NJ-4AL4-1-启停控制",{"$nulls":16},"NJ-4AL4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-1","04D01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"LCB04D01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%Q\"&B52*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LLCB04D01_C AT%Q240.3 :BOOL; (*照明控制箱NJ-4AL4-1-启停控制*)"},"LLCB04D01_C             AT%Q240.3      :BOOL; (*照明控制箱NJ-4AL4-1-启停控制*)",null,"LCB04D01_C","照明控制箱NJ-4AL4-1-启停控制",1923]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","照明控制箱NJ-4AL4-2-启停控制",{"$nulls":16},"NJ-4AL4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-2","04D02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"LCB04D02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%Q\"&B52*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LLCB04D02_C AT%Q240.4 :BOOL; (*照明控制箱NJ-4AL4-2-启停控制*)"},"LLCB04D02_C             AT%Q240.4      :BOOL; (*照明控制箱NJ-4AL4-2-启停控制*)",null,"LCB04D02_C","照明控制箱NJ-4AL4-2-启停控制",1924]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","照明控制箱NJ-4AL4-3-启停控制",{"$nulls":16},"NJ-4AL4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-3","04D03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"LCB04D03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%Q\"&B52*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LLCB04D03_C AT%Q240.5 :BOOL; (*照明控制箱NJ-4AL4-3-启停控制*)"},"LLCB04D03_C             AT%Q240.5      :BOOL; (*照明控制箱NJ-4AL4-3-启停控制*)",null,"LCB04D03_C","照明控制箱NJ-4AL4-3-启停控制",1925]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","照明控制箱NJ-4AL4-4-启停控制",{"$nulls":16},"NJ-4AL4-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-4","04D04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"LCB04D04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%Q\"&B52*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LLCB04D04_C AT%Q240.6 :BOOL; (*照明控制箱NJ-4AL4-4-启停控制*)"},"LLCB04D04_C             AT%Q240.6      :BOOL; (*照明控制箱NJ-4AL4-4-启停控制*)",null,"LCB04D04_C","照明控制箱NJ-4AL4-4-启停控制",1926]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-4AL4-5-启停控制",{"$nulls":16},"NJ-4AL4-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-5","04D05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":"LCB04D05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%Q\"&B52*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":"LLCB04D05_C AT%Q240.7 :BOOL; (*照明控制箱NJ-4AL4-5-启停控制*)"},"LLCB04D05_C             AT%Q240.7      :BOOL; (*照明控制箱NJ-4AL4-5-启停控制*)",null,"LCB04D05_C","照明控制箱NJ-4AL4-5-启停控制",1927]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-4AL4-6-启停控制",{"$nulls":16},"NJ-4AL4-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-6","04D06","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH59,List!$B$3:$D$445,2,FALSE)&AJ59&\"_\"&VLOOKUP(AK59,List!$K$2:$M$447,2,FALSE)","v":"LCB04D06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM59&\" \"&\"AT%Q\"&B52*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J59&\"*)\",\" \")","v":"LLCB04D06_C AT%Q241.0 :BOOL; (*照明控制箱NJ-4AL4-6-启停控制*)"},"LLCB04D06_C             AT%Q241.0      :BOOL; (*照明控制箱NJ-4AL4-6-启停控制*)",null,"LCB04D06_C","照明控制箱NJ-4AL4-6-启停控制",1928]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-4AL4-7-启停控制",{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-4AL4-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-7","04D07","启停控制",{"$f":"AH60&\"-\"&AK60","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"LCB04D07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%Q\"&B52*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LLCB04D07_C AT%Q241.1 :BOOL; (*照明控制箱NJ-4AL4-7-启停控制*)"},"LLCB04D07_C             AT%Q241.1      :BOOL; (*照明控制箱NJ-4AL4-7-启停控制*)",null,"LCB04D07_C",{"$f":"J60","v":"照明控制箱NJ-4AL4-7-启停控制"},1929]
[{"$nulls":5},11,null,"11+","11-","照明控制箱NJ-4AL4-8-启停控制",{"$nulls":16},"NJ-4AL4-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL4-8","04D08","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"LCB04D08_C"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%Q\"&B52*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LLCB04D08_C AT%Q241.2 :BOOL; (*照明控制箱NJ-4AL4-8-启停控制*)"},"LLCB04D08_C             AT%Q241.2      :BOOL; (*照明控制箱NJ-4AL4-8-启停控制*)",null,"LCB04D08_C","照明控制箱NJ-4AL4-8-启停控制",1930]
[{"$nulls":5},12,null,"12+","12-","排风机NJ-4AP(KT)4-1-启停控制",{"$nulls":16},"NJ-4AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)4-1","04D01","启停控制","排风机-启停控制",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"EAF04D01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%Q\"&B52*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LEAF04D01_C AT%Q241.3 :BOOL; (*排风机NJ-4AP(KT)4-1-启停控制*)"},"LEAF04D01_C             AT%Q241.3      :BOOL; (*排风机NJ-4AP(KT)4-1-启停控制*)",null,"EAF04D01_C","排风机NJ-4AP(KT)4-1-启停控制",1931]
[{"$nulls":5},13,null,"13+","13-","风机盘管NJ-4AP(KT)4-1-启停控制",{"$nulls":16},"NJ-4AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)4-1","04D01","启停控制","风机盘管-启停控制",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"FCU04D01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%Q\"&B52*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LFCU04D01_C AT%Q241.4 :BOOL; (*风机盘管NJ-4AP(KT)4-1-启停控制*)"},"LFCU04D01_C             AT%Q241.4      :BOOL; (*风机盘管NJ-4AP(KT)4-1-启停控制*)",null,"FCU04D01_C","风机盘管NJ-4AP(KT)4-1-启停控制",1932]
[{"$nulls":5},14,null,"14+","14-","风机盘管NJ-4AP(KT)4-1-电磁阀开关控制",{"$nulls":16},"NJ-4AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)4-1","04D01","电磁阀开关控制","风机盘管-电磁阀开关控制",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"FCU04D01_EVC"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%Q\"&B52*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LFCU04D01_EVC AT%Q241.5 :BOOL; (*风机盘管NJ-4AP(KT)4-1-电磁阀开关控制*)"},"LFCU04D01_EVC           AT%Q241.5      :BOOL; (*风机盘管NJ-4AP(KT)4-1-电磁阀开关控制*)",null,"FCU04D01_EVC","风机盘管NJ-4AP(KT)4-1-电磁阀开关控制",1933]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%Q\"&B52*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1934]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%Q\"&B52*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1935]
[null,{"$f":"B72","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B72&\"地址: \"&B69&\" *)\"","v":"(* IOM 0801U地址: 16 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH68&AA68&\"-\"&AK68","v":"空调机组NJ-4AP(KT)4-1-回风温度"},{"$nulls":16},{"$f":"IF(AI68=\"\",\"\",AI68)","v":"NJ-4AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-1","04D01","回风温度",{"$f":"AH68&\"-\"&AK68","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"AHU04D01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%I\"&B69*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LAHU04D01_RT AT%I256.0 :INT ; (*空调机组NJ-4AP(KT)4-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68))),SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))))),\" \")","v":"LAHU04D01_RT            AT%I256.0      :INT ; (*空调机组NJ-4AP(KT)4-1-回风温度*)"},null,{"$f":"AM68","v":"AHU04D01_RT"},{"$f":"J68","v":"空调机组NJ-4AP(KT)4-1-回风温度"},{"$f":"30000+($B69*8+F68-1)","v":30128}]
[null,16,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-4AP(KT)4-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-4AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-1","04D01","水阀反馈",{"$f":"AH69&\"-\"&AK69","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU04D01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%I\"&B69*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU04D01_WVB AT%I258.0 :INT ; (*空调机组NJ-4AP(KT)4-1-水阀反馈*)"},"LAHU04D01_WVB           AT%I258.0      :INT ; (*空调机组NJ-4AP(KT)4-1-水阀反馈*)",null,"AHU04D01_WVB",{"$f":"J69","v":"空调机组NJ-4AP(KT)4-1-水阀反馈"},{"$f":"AS68+1","v":30129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-4AP(KT)4-2-回风温度",{"$nulls":16},"NJ-4AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-2","04D02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"AHU04D02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%I\"&B69*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LAHU04D02_RT AT%I260.0 :INT ; (*空调机组NJ-4AP(KT)4-2-回风温度*)"},"LAHU04D02_RT            AT%I260.0      :INT ; (*空调机组NJ-4AP(KT)4-2-回风温度*)",null,"AHU04D02_RT","空调机组NJ-4AP(KT)4-2-回风温度",{"$f":"AS69+1","v":30130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-4AP(KT)4-2-水阀反馈",{"$nulls":16},"NJ-4AP(KT)4-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-2","04D02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"AHU04D02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%I\"&B69*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LAHU04D02_WVB AT%I262.0 :INT ; (*空调机组NJ-4AP(KT)4-2-水阀反馈*)"},"LAHU04D02_WVB           AT%I262.0      :INT ; (*空调机组NJ-4AP(KT)4-2-水阀反馈*)",null,"AHU04D02_WVB","空调机组NJ-4AP(KT)4-2-水阀反馈",30131]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":1},5,null,5,"0V","空调机组NJ-4AP(KT)4-3-回风温度",{"$nulls":16},"NJ-4AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-3","04D03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"AHU04D03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%I\"&B69*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LAHU04D03_RT AT%I264.0 :INT ; (*空调机组NJ-4AP(KT)4-3-回风温度*)"},"LAHU04D03_RT            AT%I264.0      :INT ; (*空调机组NJ-4AP(KT)4-3-回风温度*)",null,"AHU04D03_RT","空调机组NJ-4AP(KT)4-3-回风温度",30132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-4AP(KT)4-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI73=\"\",\"\",AI73)","v":"NJ-4AP(KT)4-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-3","04D03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"AHU04D03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%I\"&B69*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LAHU04D03_WVB AT%I266.0 :INT ; (*空调机组NJ-4AP(KT)4-3-水阀反馈*)"},"LAHU04D03_WVB           AT%I266.0      :INT ; (*空调机组NJ-4AP(KT)4-3-水阀反馈*)",null,"AHU04D03_WVB",{"$f":"J73","v":"空调机组NJ-4AP(KT)4-3-水阀反馈"},30133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","风机盘管NJ-4AP(KT)4-1-温度状态",{"$nulls":16},"NJ-4AP(KT)4-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)4-1","04D01","温度状态","风机盘管-温度状态",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":"FCU04D01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%I\"&B69*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":"LFCU04D01_T AT%I268.0 :INT ; (*风机盘管NJ-4AP(KT)4-1-温度状态*)"},"LFCU04D01_T             AT%I268.0      :INT ; (*风机盘管NJ-4AP(KT)4-1-温度状态*)",null,"FCU04D01_T","风机盘管NJ-4AP(KT)4-1-温度状态",30134]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%I\"&B69*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30135]
[null,{"$f":"B81","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B81&\"地址: \"&B78&\" *)\"","v":"(* IOM 0401A地址: 17 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH77&AA77&\"-\"&AK77","v":"空调机组NJ-4AP(KT)4-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-4AP(KT)4-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-1","04D01","水阀控制",{"$f":"AH77&\"-\"&AK77","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"AHU04D01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%Q\"&B78*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LAHU04D01_WVC AT%Q272.0 :INT ; (*空调机组NJ-4AP(KT)4-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77))),SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))))),\" \")","v":"LAHU04D01_WVC           AT%Q272.0      :INT ; (*空调机组NJ-4AP(KT)4-1-水阀控制*)"},null,{"$f":"AM77","v":"AHU04D01_WVC"},{"$f":"J77","v":"空调机组NJ-4AP(KT)4-1-水阀控制"},{"$f":"40000+($B78*8+F77-1)","v":40136}]
[null,17,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH78&AA78&\"-\"&AK78","v":"空调机组NJ-4AP(KT)4-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-4AP(KT)4-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-2","04D02","水阀控制",{"$f":"AH78&\"-\"&AK78","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU04D02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B78*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU04D02_WVC AT%Q274.0 :INT ; (*空调机组NJ-4AP(KT)4-2-水阀控制*)"},"LAHU04D02_WVC           AT%Q274.0      :INT ; (*空调机组NJ-4AP(KT)4-2-水阀控制*)",null,"AHU04D02_WVC",{"$f":"J78","v":"空调机组NJ-4AP(KT)4-2-水阀控制"},{"$f":"AS77+1","v":40137}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH79&AA79&\"-\"&AK79","v":"空调机组NJ-4AP(KT)4-3-水阀控制"},{"$nulls":16},"NJ-4AP(KT)4-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)4-3","04D03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU04D03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B78*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU04D03_WVC AT%Q276.0 :INT ; (*空调机组NJ-4AP(KT)4-3-水阀控制*)"},"LAHU04D03_WVC           AT%Q276.0      :INT ; (*空调机组NJ-4AP(KT)4-3-水阀控制*)",null,"AHU04D03_WVC","空调机组NJ-4AP(KT)4-3-水阀控制",{"$f":"AS78+1","v":40138}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH80&AA80&\"-\"&AK80","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B78*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40139]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L510","index":32,"n_rows":42,"n_cols":45,"rows_kept":42,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[41,5,41,6],[41,9,41,25],[4,1,5,1],[11,1,14,1],[20,1,23,1],[29,1,32,1],[38,1,41,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L01",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.0801R D7",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 0801R地址: 18 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH8&AA8&\"-\"&AK8","v":"F新风机组NJ-5AP(KT)4-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-5AP(KT)4"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)4","05J01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"F新风机组-运行状态"},{"$f":"VLOOKUP(AH8,[1]List!$D$3:$F$527,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05J01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LFAU05J01_R AT%I288.0 :BOOL; (*F新风机组NJ-5AP(KT)4-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LFAU05J01_R             AT%I288.0      :BOOL; (*F新风机组NJ-5AP(KT)4-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L01\\L01FAU05J01_R"},{"$f":"J8","v":"F新风机组NJ-5AP(KT)4-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":12304}]
[null,18,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},2,null,2,"C","F新风机组NJ-5AP(KT)4-故障状态",{"$nulls":16},"NJ-5AP(KT)4",{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)4","05J01","故障状态","F新风机组-故障状态",{"$f":"VLOOKUP(AH9,[1]List!$D$3:$F$527,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05J01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LFAU05J01_F AT%I288.1 :BOOL; (*F新风机组NJ-5AP(KT)4-故障状态*)"},"LFAU05J01_F             AT%I288.1      :BOOL; (*F新风机组NJ-5AP(KT)4-故障状态*)",null,"L01\\L01FAU05J01_F","F新风机组NJ-5AP(KT)4-故障状态",{"$f":"AS8+1","v":12305}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},3,null,3,"C","F新风机组NJ-5AP(KT)4-自动状态",{"$nulls":16},"NJ-5AP(KT)4",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)4","05J01","自动状态","F新风机组-自动状态",{"$f":"VLOOKUP(AH10,[1]List!$D$3:$F$527,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05J01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LFAU05J01_A AT%I288.2 :BOOL; (*F新风机组NJ-5AP(KT)4-自动状态*)"},"LFAU05J01_A             AT%I288.2      :BOOL; (*F新风机组NJ-5AP(KT)4-自动状态*)",null,"L01\\L01FAU05J01_A","F新风机组NJ-5AP(KT)4-自动状态",12306]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},4,null,4,"C","F新风机组NJ-5AP(KT)4-风机压差",{"$nulls":16},"NJ-5AP(KT)4",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)4","05J01","风机压差","F新风机组-风机压差",{"$f":"VLOOKUP(AH11,[1]List!$D$3:$F$527,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05J01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LFAU05J01_FPS AT%I288.3 :BOOL; (*F新风机组NJ-5AP(KT)4-风机压差*)"},"LFAU05J01_FPS           AT%I288.3      :BOOL; (*F新风机组NJ-5AP(KT)4-风机压差*)",null,"L01\\L01FAU05J01_FPS","F新风机组NJ-5AP(KT)4-风机压差",12307]
[null,"IOM 0801R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},5,null,5,"C","F新风机组NJ-5AP(KT)4-初效滤网压差",{"$nulls":16},"NJ-5AP(KT)4",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)4","05J01","初效滤网压差","F新风机组-初效滤网压差",{"$f":"VLOOKUP(AH12,[1]List!$D$3:$F$527,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05J01_IPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LFAU05J01_IPS AT%I288.4 :BOOL; (*F新风机组NJ-5AP(KT)4-初效滤网压差*)"},"LFAU05J01_IPS           AT%I288.4      :BOOL; (*F新风机组NJ-5AP(KT)4-初效滤网压差*)",null,"L01\\L01FAU05J01_IPS","F新风机组NJ-5AP(KT)4-初效滤网压差",12308]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","F新风机组NJ-5AP(KT)4-低温断路开关",{"$nulls":16},"NJ-5AP(KT)4",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)4","05J01","低温断路开关","F新风机组-低温断路开关",{"$f":"VLOOKUP(AH13,[1]List!$D$3:$F$527,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05J01_AFS"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LFAU05J01_AFS AT%I288.5 :BOOL; (*F新风机组NJ-5AP(KT)4-低温断路开关*)"},"LFAU05J01_AFS           AT%I288.5      :BOOL; (*F新风机组NJ-5AP(KT)4-低温断路开关*)",null,"L01\\L01FAU05J01_AFS","F新风机组NJ-5AP(KT)4-低温断路开关",12309]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","F新风机组NJ-5AP(KT)4-新风阀开状态",{"$nulls":16},"NJ-5AP(KT)4",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)4","05J01","新风阀开状态","F新风机组-新风阀开状态",{"$f":"VLOOKUP(AH14,[1]List!$D$3:$F$527,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05J01_FDOB"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LFAU05J01_FDOB AT%I288.6 :BOOL; (*F新风机组NJ-5AP(KT)4-新风阀开状态*)"},"LFAU05J01_FDOB          AT%I288.6      :BOOL; (*F新风机组NJ-5AP(KT)4-新风阀开状态*)",null,"L01\\L01FAU05J01_FDOB","F新风机组NJ-5AP(KT)4-新风阀开状态",12310]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","F新风机组NJ-5AP(KT)4-新风阀关状态",{"$nulls":16},"NJ-5AP(KT)4",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)4","05J01","新风阀关状态","F新风机组-新风阀关状态",{"$f":"VLOOKUP(AH15,[1]List!$D$3:$F$527,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05J01_FDSB"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LFAU05J01_FDSB AT%I288.7 :BOOL; (*F新风机组NJ-5AP(KT)4-新风阀关状态*)"},"LFAU05J01_FDSB          AT%I288.7      :BOOL; (*F新风机组NJ-5AP(KT)4-新风阀关状态*)",null,"L01\\L01FAU05J01_FDSB","F新风机组NJ-5AP(KT)4-新风阀关状态",12311]
[null,{"$f":"B21","v":"IOM 0801D"},{"$nulls":38},{"$f":"\"(* \"&B21&\"地址: \"&B18&\" *)\"","v":"(* IOM 0801D地址: 19 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH17&AA17&\"-\"&AK17","v":"F新风机组NJ-5AP(KT)4-启停控制"},{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-5AP(KT)4"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)4","05J01","启停控制",{"$f":"AH17&\"-\"&AK17","v":"F新风机组-启停控制"},{"$f":"VLOOKUP(AH17,[1]List!$D$3:$F$527,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05J01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%Q\"&B18*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LFAU05J01_C AT%Q304.0 :BOOL; (*F新风机组NJ-5AP(KT)4-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",25-SEARCH(\"AT%\",AN17))),SEARCH(\":\",REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",25-SEARCH(\"AT%\",AN17)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",25-SEARCH(\"AT%\",AN17)))))),\" \")","v":"LFAU05J01_C             AT%Q304.0      :BOOL; (*F新风机组NJ-5AP(KT)4-启停控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM17","v":"L01\\L01FAU05J01_C"},{"$f":"J17","v":"F新风机组NJ-5AP(KT)4-启停控制"},{"$f":"($B18*16*8+F17-1)","v":2432}]
[null,19,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","F新风机组NJ-5AP(KT)4-新风阀开控制",{"$nulls":16},"NJ-5AP(KT)4",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)4","05J01","新风阀开控制","F新风机组-新风阀开控制",{"$f":"VLOOKUP(AH18,[1]List!$D$3:$F$527,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05J01_FDOC"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%Q\"&B18*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LFAU05J01_FDOC AT%Q304.1 :BOOL; (*F新风机组NJ-5AP(KT)4-新风阀开控制*)"},"LFAU05J01_FDOC          AT%Q304.1      :BOOL; (*F新风机组NJ-5AP(KT)4-新风阀开控制*)",null,"L01\\L01FAU05J01_FDOC","F新风机组NJ-5AP(KT)4-新风阀开控制",{"$f":"AS17+1","v":2433}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","F新风机组NJ-5AP(KT)4-新风阀关控制",{"$nulls":16},"NJ-5AP(KT)4",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)4","05J01","新风阀关控制","F新风机组-新风阀关控制",{"$f":"VLOOKUP(AH19,[1]List!$D$3:$F$527,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05J01_FDSC"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%Q\"&B18*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LFAU05J01_FDSC AT%Q304.2 :BOOL; (*F新风机组NJ-5AP(KT)4-新风阀关控制*)"},"LFAU05J01_FDSC          AT%Q304.2      :BOOL; (*F新风机组NJ-5AP(KT)4-新风阀关控制*)",null,"L01\\L01FAU05J01_FDSC","F新风机组NJ-5AP(KT)4-新风阀关控制",2434]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH20,[1]List!$D$3:$F$527,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%Q\"&B18*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN20,SEARCH(\"AT%\",AN20),,REPT(\" \",30-SEARCH(\"AT%\",AN20))),SEARCH(\":\",REPLACE(AN20,SEARCH(\"AT%\",AN20),,REPT(\" \",30-SEARCH(\"AT%\",AN20)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN20,SEARCH(\"AT%\",AN20),,REPT(\" \",25-SEARCH(\"AT%\",AN20)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",2435]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),1,1))","v":1},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH21,[1]List!$D$3:$F$527,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%Q\"&B18*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2436]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH22,[1]List!$D$3:$F$527,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%Q\"&B18*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2437]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH23,[1]List!$D$3:$F$527,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%Q\"&B18*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2438]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH24,[1]List!$D$3:$F$527,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%Q\"&B18*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2439]
[null,{"$f":"B30","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 0401U地址: 20 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH26&AA26&\"-\"&AK26","v":"F新风机组NJ-5AP(KT)4-送风温度"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-5AP(KT)4"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)4","05J01","送风温度",{"$f":"AH26&\"-\"&AK26","v":"F新风机组-送风温度"},{"$f":"VLOOKUP(AH26,[1]List!$D$3:$F$527,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05J01_ST"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LFAU05J01_ST AT%I320.0 :INT; (*F新风机组NJ-5AP(KT)4-送风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LFAU05J01_ST            AT%I320.0      :INT; (*F新风机组NJ-5AP(KT)4-送风温度*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L01\\L01FAU05J01_ST"},{"$f":"J26","v":"F新风机组NJ-5AP(KT)4-送风温度"},{"$f":"30000+($B27*8+F26-1)","v":30160}]
[null,20,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,2,"0V","F新风机组NJ-5AP(KT)4-水阀反馈",{"$nulls":16},"NJ-5AP(KT)4",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)4","05J01","水阀反馈","F新风机组-水阀反馈",{"$f":"VLOOKUP(AH27,[1]List!$D$3:$F$527,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05J01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LFAU05J01_WVB AT%I322.0 :INT; (*F新风机组NJ-5AP(KT)4-水阀反馈*)"},"LFAU05J01_WVB           AT%I322.0      :INT; (*F新风机组NJ-5AP(KT)4-水阀反馈*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM27","v":"L01\\L01FAU05J01_WVB"},"F新风机组NJ-5AP(KT)4-水阀反馈",{"$f":"AS26+1","v":30161}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":1},3,null,3,"0V","F新风机组NJ-5AP(KT)4-变频器频率反馈",{"$nulls":16},"NJ-5AP(KT)4",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)4","05J01","变频器频率反馈","F新风机组-变频器频率反馈",{"$f":"VLOOKUP(AH28,[1]List!$D$3:$F$527,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05J01_VFB"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LFAU05J01_VFB AT%I324.0 :INT; (*F新风机组NJ-5AP(KT)4-变频器频率反馈*)"},"LFAU05J01_VFB           AT%I324.0      :INT; (*F新风机组NJ-5AP(KT)4-变频器频率反馈*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM28","v":"L01\\L01FAU05J01_VFB"},"F新风机组NJ-5AP(KT)4-变频器频率反馈",30162]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH29,[1]List!$D$3:$F$527,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN29,SEARCH(\"AT%\",AN29),,REPT(\" \",30-SEARCH(\"AT%\",AN29))),SEARCH(\":\",REPLACE(AN29,SEARCH(\"AT%\",AN29),,REPT(\" \",30-SEARCH(\"AT%\",AN29)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN29,SEARCH(\"AT%\",AN29),,REPT(\" \",25-SEARCH(\"AT%\",AN29)))))),\" \")","v":" "},null,{"$f":"$B$2&\"\\\"&$B$2&AM29","v":{"$error":"#N/A"}},"-",30163]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":1}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B39","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B39&\"地址: \"&B36&\" *)\"","v":"(* IOM 0401A地址: 21 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH35&AA35&\"-\"&AK35","v":"F新风机组NJ-5AP(KT)4-水阀控制"},{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-5AP(KT)4"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)4","05J01","水阀控制",{"$f":"AH35&\"-\"&AK35","v":"F新风机组-水阀控制"},{"$f":"VLOOKUP(AH35,[1]List!$D$3:$F$527,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05J01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%Q\"&B36*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LFAU05J01_WVC AT%Q336.0 :INT; (*F新风机组NJ-5AP(KT)4-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35))),SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35)))))),\" \")","v":"LFAU05J01_WVC           AT%Q336.0      :INT; (*F新风机组NJ-5AP(KT)4-水阀控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM35","v":"L01\\L01FAU05J01_WVC"},{"$f":"J35","v":"F新风机组NJ-5AP(KT)4-水阀控制"},{"$f":"40000+($B36*8+F35-1)","v":40168}]
[null,21,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":0},2,null,3,4,"F新风机组NJ-5AP(KT)4-变频器频率控制",{"$nulls":16},"NJ-5AP(KT)4",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)4","05J01","变频器频率控制","F新风机组-变频器频率控制",{"$f":"VLOOKUP(AH36,[1]List!$D$3:$F$527,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05J01_VFC"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%Q\"&B36*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LFAU05J01_VFC AT%Q338.0 :INT; (*F新风机组NJ-5AP(KT)4-变频器频率控制*)"},"LFAU05J01_VFC           AT%Q338.0      :INT; (*F新风机组NJ-5AP(KT)4-变频器频率控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM36","v":"L01\\L01FAU05J01_VFC"},"F新风机组NJ-5AP(KT)4-变频器频率控制",{"$f":"AS35+1","v":40169}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":1},3,null,5,6,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH37,[1]List!$D$3:$F$527,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%Q\"&B36*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN37,SEARCH(\"AT%\",AN37),,REPT(\" \",30-SEARCH(\"AT%\",AN37))),SEARCH(\":\",REPLACE(AN37,SEARCH(\"AT%\",AN37),,REPT(\" \",30-SEARCH(\"AT%\",AN37)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN37,SEARCH(\"AT%\",AN37),,REPT(\" \",25-SEARCH(\"AT%\",AN37)))))),\" \")","v":" "},null,{"$f":"$B$2&\"\\\"&$B$2&AM37","v":{"$error":"#N/A"}},"-",40170]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":0},4,null,7,8,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH38,[1]List!$D$3:$F$527,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%Q\"&B36*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM38","v":{"$error":"#N/A"}},"-",40171]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L305","index":33,"n_rows":129,"n_cols":45,"rows_kept":129,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[6,1,6,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[75,5,75,6],[75,9,75,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[92,5,92,6],[92,9,92,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[101,5,101,6],[101,9,101,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[109,5,109,6],[109,9,109,25],[110,5,110,6],[110,9,110,25],[112,5,112,6],[112,9,112,25],[113,5,113,6],[113,9,113,25],[114,5,114,6],[114,9,114,25],[115,5,115,6],[115,9,115,25],[116,5,116,6],[116,9,116,25],[117,5,117,6],[117,9,117,25],[118,5,118,6],[118,9,118,25],[119,5,119,6],[119,9,119,25],[121,5,121,6],[121,9,121,25],[122,5,122,6],[122,9,122,25],[123,5,123,6],[123,9,123,25],[124,5,124,6],[124,9,124,25],[125,5,125,6],[125,9,125,25],[126,5,126,6],[126,9,126,25],[127,5,127,6],[127,9,127,25],[128,5,128,6],[128,9,128,25],[4,1,5,1],[12,1,23,1],[29,1,40,1],[46,1,57,1],[63,1,66,1],[72,1,83,1],[89,1,92,1],[98,1,101,1],[107,1,110,1],[116,1,119,1],[125,1,128,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[16,2,23,4],[33,2,40,4],[50,2,57,4],[76,2,83,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L23",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"EXC-1000"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B13&\"地址: \"&B10&\" *)\"","v":"(* IOM 1601R地址: 0 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH9&AA9&\"-\"&AK9","v":"空调机组NJ-3AP(KT)5-1-运行状态"},{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-3AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-1","03E01","运行状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU03E01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B10*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU03E01_R AT%I0.0 :BOOL; (*空调机组NJ-3AP(KT)5-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9))),SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))))),\" \")","v":"LAHU03E01_R             AT%I0.0        :BOOL; (*空调机组NJ-3AP(KT)5-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM9","v":"L23\\L23AHU03E01_R"},{"$f":"J9","v":"空调机组NJ-3AP(KT)5-1-运行状态"},{"$f":"10000+($B10*16*8+F9-1)","v":10000}]
[null,0,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-3AP(KT)5-1-故障状态",{"$nulls":16},{"$f":"IF(AI10=\"\",\"\",AI10)","v":"NJ-3AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-1","03E01","故障状态",{"$f":"AH10&\"-\"&AK10","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU03E01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B10*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU03E01_F AT%I0.1 :BOOL; (*空调机组NJ-3AP(KT)5-1-故障状态*)"},"LAHU03E01_F             AT%I0.1        :BOOL; (*空调机组NJ-3AP(KT)5-1-故障状态*)",null,"L23\\L23AHU03E01_F",{"$f":"J10","v":"空调机组NJ-3AP(KT)5-1-故障状态"},{"$f":"AS9+1","v":10001}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)5-1-自动状态",{"$nulls":16},"NJ-3AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-1","03E01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU03E01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B10*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU03E01_A AT%I0.2 :BOOL; (*空调机组NJ-3AP(KT)5-1-自动状态*)"},"LAHU03E01_A             AT%I0.2        :BOOL; (*空调机组NJ-3AP(KT)5-1-自动状态*)",null,"L23\\L23AHU03E01_A","空调机组NJ-3AP(KT)5-1-自动状态",{"$f":"AS10+1","v":10002}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)5-1-风机压差",{"$nulls":16},"NJ-3AP(KT)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-1","03E01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU03E01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B10*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU03E01_FPS AT%I0.3 :BOOL; (*空调机组NJ-3AP(KT)5-1-风机压差*)"},"LAHU03E01_FPS           AT%I0.3        :BOOL; (*空调机组NJ-3AP(KT)5-1-风机压差*)",null,"L23\\L23AHU03E01_FPS","空调机组NJ-3AP(KT)5-1-风机压差",10003]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)5-2-运行状态",{"$nulls":16},"NJ-3AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-2","03E02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU03E02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B10*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU03E02_R AT%I0.4 :BOOL; (*空调机组NJ-3AP(KT)5-2-运行状态*)"},"LAHU03E02_R             AT%I0.4        :BOOL; (*空调机组NJ-3AP(KT)5-2-运行状态*)",null,"L23\\L23AHU03E02_R","空调机组NJ-3AP(KT)5-2-运行状态",10004]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)5-2-故障状态",{"$nulls":16},"NJ-3AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-2","03E02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU03E02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B10*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU03E02_F AT%I0.5 :BOOL; (*空调机组NJ-3AP(KT)5-2-故障状态*)"},"LAHU03E02_F             AT%I0.5        :BOOL; (*空调机组NJ-3AP(KT)5-2-故障状态*)",null,"L23\\L23AHU03E02_F","空调机组NJ-3AP(KT)5-2-故障状态",10005]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)5-2-自动状态",{"$nulls":16},"NJ-3AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-2","03E02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU03E02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B10*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU03E02_A AT%I0.6 :BOOL; (*空调机组NJ-3AP(KT)5-2-自动状态*)"},"LAHU03E02_A             AT%I0.6        :BOOL; (*空调机组NJ-3AP(KT)5-2-自动状态*)",null,"L23\\L23AHU03E02_A","空调机组NJ-3AP(KT)5-2-自动状态",10006]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)5-2-风机压差",{"$nulls":16},"NJ-3AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-2","03E02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU03E02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B10*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU03E02_FPS AT%I0.7 :BOOL; (*空调机组NJ-3AP(KT)5-2-风机压差*)"},"LAHU03E02_FPS           AT%I0.7        :BOOL; (*空调机组NJ-3AP(KT)5-2-风机压差*)",null,"L23\\L23AHU03E02_FPS","空调机组NJ-3AP(KT)5-2-风机压差",10007]
[{"$nulls":5},9,null,17,18,"空调机组NJ-3AP(KT)5-3-运行状态",{"$nulls":16},"NJ-3AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-3","03E03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU03E03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B10*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU03E03_R AT%I1.0 :BOOL; (*空调机组NJ-3AP(KT)5-3-运行状态*)"},"LAHU03E03_R             AT%I1.0        :BOOL; (*空调机组NJ-3AP(KT)5-3-运行状态*)",null,"L23\\L23AHU03E03_R","空调机组NJ-3AP(KT)5-3-运行状态",10008]
[{"$nulls":5},10,null,19,20,"空调机组NJ-3AP(KT)5-3-故障状态",{"$nulls":16},{"$f":"IF(AI18=\"\",\"\",AI18)","v":"NJ-3AP(KT)5-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-3","03E03","故障状态",{"$f":"AH18&\"-\"&AK18","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU03E03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B10*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU03E03_F AT%I1.1 :BOOL; (*空调机组NJ-3AP(KT)5-3-故障状态*)"},"LAHU03E03_F             AT%I1.1        :BOOL; (*空调机组NJ-3AP(KT)5-3-故障状态*)",null,"L23\\L23AHU03E03_F","空调机组NJ-3AP(KT)5-3-故障状态",10009]
[{"$nulls":5},11,null,21,22,"空调机组NJ-3AP(KT)5-3-自动状态",{"$nulls":16},"NJ-3AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-3","03E03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU03E03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B10*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU03E03_A AT%I1.2 :BOOL; (*空调机组NJ-3AP(KT)5-3-自动状态*)"},"LAHU03E03_A             AT%I1.2        :BOOL; (*空调机组NJ-3AP(KT)5-3-自动状态*)",null,"L23\\L23AHU03E03_A","空调机组NJ-3AP(KT)5-3-自动状态",10010]
[{"$nulls":5},12,null,23,24,"空调机组NJ-3AP(KT)5-3-风机压差",{"$nulls":16},"NJ-3AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-3","03E03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU03E03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B10*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU03E03_FPS AT%I1.3 :BOOL; (*空调机组NJ-3AP(KT)5-3-风机压差*)"},"LAHU03E03_FPS           AT%I1.3        :BOOL; (*空调机组NJ-3AP(KT)5-3-风机压差*)",null,"L23\\L23AHU03E03_FPS","空调机组NJ-3AP(KT)5-3-风机压差",10011]
[{"$nulls":5},13,null,25,26,"空调机组NJ-3AP(KT)5-4-运行状态",{"$nulls":16},"NJ-3AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-4","03E04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU03E04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B10*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU03E04_R AT%I1.4 :BOOL; (*空调机组NJ-3AP(KT)5-4-运行状态*)"},"LAHU03E04_R             AT%I1.4        :BOOL; (*空调机组NJ-3AP(KT)5-4-运行状态*)",null,"L23\\L23AHU03E04_R","空调机组NJ-3AP(KT)5-4-运行状态",10012]
[{"$nulls":5},14,null,27,28,"空调机组NJ-3AP(KT)5-4-故障状态",{"$nulls":16},"NJ-3AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-4","03E04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU03E04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B10*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU03E04_F AT%I1.5 :BOOL; (*空调机组NJ-3AP(KT)5-4-故障状态*)"},"LAHU03E04_F             AT%I1.5        :BOOL; (*空调机组NJ-3AP(KT)5-4-故障状态*)",null,"L23\\L23AHU03E04_F","空调机组NJ-3AP(KT)5-4-故障状态",10013]
[{"$nulls":5},15,null,29,30,"空调机组NJ-3AP(KT)5-4-自动状态",{"$nulls":16},"NJ-3AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-4","03E04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU03E04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B10*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU03E04_A AT%I1.6 :BOOL; (*空调机组NJ-3AP(KT)5-4-自动状态*)"},"LAHU03E04_A             AT%I1.6        :BOOL; (*空调机组NJ-3AP(KT)5-4-自动状态*)",null,"L23\\L23AHU03E04_A","空调机组NJ-3AP(KT)5-4-自动状态",10014]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-3AP(KT)5-4-风机压差",{"$nulls":16},"NJ-3AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-4","03E04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH24,List!$B$3:$D$445,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,List!$K$2:$M$447,2,FALSE)","v":"AHU03E04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%I\"&B10*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":"LAHU03E04_FPS AT%I1.7 :BOOL; (*空调机组NJ-3AP(KT)5-4-风机压差*)"},"LAHU03E04_FPS           AT%I1.7        :BOOL; (*空调机组NJ-3AP(KT)5-4-风机压差*)",null,"L23\\L23AHU03E04_FPS","空调机组NJ-3AP(KT)5-4-风机压差",10015]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 1601R地址: 1 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH26&AA26&\"-\"&AK26","v":"空调机组NJ-3AP(KT)5-5-运行状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-3AP(KT)5-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-5","03E05","运行状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU03E05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU03E05_R AT%I16.0 :BOOL; (*空调机组NJ-3AP(KT)5-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LAHU03E05_R             AT%I16.0       :BOOL; (*空调机组NJ-3AP(KT)5-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L23\\L23AHU03E05_R"},{"$f":"J26","v":"空调机组NJ-3AP(KT)5-5-运行状态"},{"$f":"10000+($B27*16*8+F26-1)","v":10128}]
[null,1,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-3AP(KT)5-5-故障状态",{"$nulls":16},{"$f":"IF(AI27=\"\",\"\",AI27)","v":"NJ-3AP(KT)5-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-5","03E05","故障状态",{"$f":"AH27&\"-\"&AK27","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU03E05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU03E05_F AT%I16.1 :BOOL; (*空调机组NJ-3AP(KT)5-5-故障状态*)"},"LAHU03E05_F             AT%I16.1       :BOOL; (*空调机组NJ-3AP(KT)5-5-故障状态*)",null,"L23\\L23AHU03E05_F",{"$f":"J27","v":"空调机组NJ-3AP(KT)5-5-故障状态"},{"$f":"AS26+1","v":10129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)5-5-自动状态",{"$nulls":16},"NJ-3AP(KT)5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-5","03E05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU03E05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU03E05_A AT%I16.2 :BOOL; (*空调机组NJ-3AP(KT)5-5-自动状态*)"},"LAHU03E05_A             AT%I16.2       :BOOL; (*空调机组NJ-3AP(KT)5-5-自动状态*)",null,"L23\\L23AHU03E05_A","空调机组NJ-3AP(KT)5-5-自动状态",{"$f":"AS27+1","v":10130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)5-5-风机压差",{"$nulls":16},"NJ-3AP(KT)5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-5","03E05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU03E05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU03E05_FPS AT%I16.3 :BOOL; (*空调机组NJ-3AP(KT)5-5-风机压差*)"},"LAHU03E05_FPS           AT%I16.3       :BOOL; (*空调机组NJ-3AP(KT)5-5-风机压差*)",null,"L23\\L23AHU03E05_FPS","空调机组NJ-3AP(KT)5-5-风机压差",10131]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)5-6-运行状态",{"$nulls":16},"NJ-3AP(KT)5-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-6","03E06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU03E06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B27*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU03E06_R AT%I16.4 :BOOL; (*空调机组NJ-3AP(KT)5-6-运行状态*)"},"LAHU03E06_R             AT%I16.4       :BOOL; (*空调机组NJ-3AP(KT)5-6-运行状态*)",null,"L23\\L23AHU03E06_R","空调机组NJ-3AP(KT)5-6-运行状态",10132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)5-6-故障状态",{"$nulls":16},"NJ-3AP(KT)5-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-6","03E06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU03E06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B27*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU03E06_F AT%I16.5 :BOOL; (*空调机组NJ-3AP(KT)5-6-故障状态*)"},"LAHU03E06_F             AT%I16.5       :BOOL; (*空调机组NJ-3AP(KT)5-6-故障状态*)",null,"L23\\L23AHU03E06_F","空调机组NJ-3AP(KT)5-6-故障状态",10133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)5-6-自动状态",{"$nulls":16},"NJ-3AP(KT)5-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-6","03E06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU03E06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B27*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU03E06_A AT%I16.6 :BOOL; (*空调机组NJ-3AP(KT)5-6-自动状态*)"},"LAHU03E06_A             AT%I16.6       :BOOL; (*空调机组NJ-3AP(KT)5-6-自动状态*)",null,"L23\\L23AHU03E06_A","空调机组NJ-3AP(KT)5-6-自动状态",10134]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)5-6-风机压差",{"$nulls":16},"NJ-3AP(KT)5-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-6","03E06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU03E06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B27*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU03E06_FPS AT%I16.7 :BOOL; (*空调机组NJ-3AP(KT)5-6-风机压差*)"},"LAHU03E06_FPS           AT%I16.7       :BOOL; (*空调机组NJ-3AP(KT)5-6-风机压差*)",null,"L23\\L23AHU03E06_FPS","空调机组NJ-3AP(KT)5-6-风机压差",10135]
[{"$nulls":5},9,null,17,18,"空调机组NJ-3AP(KT)5-7-运行状态",{"$nulls":16},"NJ-3AP(KT)5-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-7","03E07","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU03E07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B27*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU03E07_R AT%I17.0 :BOOL; (*空调机组NJ-3AP(KT)5-7-运行状态*)"},"LAHU03E07_R             AT%I17.0       :BOOL; (*空调机组NJ-3AP(KT)5-7-运行状态*)",null,"L23\\L23AHU03E07_R","空调机组NJ-3AP(KT)5-7-运行状态",10136]
[{"$nulls":5},10,null,19,20,"空调机组NJ-3AP(KT)5-7-故障状态",{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-3AP(KT)5-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-7","03E07","故障状态",{"$f":"AH35&\"-\"&AK35","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU03E07_F"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B27*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU03E07_F AT%I17.1 :BOOL; (*空调机组NJ-3AP(KT)5-7-故障状态*)"},"LAHU03E07_F             AT%I17.1       :BOOL; (*空调机组NJ-3AP(KT)5-7-故障状态*)",null,"L23\\L23AHU03E07_F",{"$f":"J35","v":"空调机组NJ-3AP(KT)5-7-故障状态"},10137]
[{"$nulls":5},11,null,21,22,"空调机组NJ-3AP(KT)5-7-自动状态",{"$nulls":16},"NJ-3AP(KT)5-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-7","03E07","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU03E07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B27*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU03E07_A AT%I17.2 :BOOL; (*空调机组NJ-3AP(KT)5-7-自动状态*)"},"LAHU03E07_A             AT%I17.2       :BOOL; (*空调机组NJ-3AP(KT)5-7-自动状态*)",null,"L23\\L23AHU03E07_A","空调机组NJ-3AP(KT)5-7-自动状态",10138]
[{"$nulls":5},12,null,23,24,"空调机组NJ-3AP(KT)5-7-风机压差",{"$nulls":16},"NJ-3AP(KT)5-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-7","03E07","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"AHU03E07_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B27*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LAHU03E07_FPS AT%I17.3 :BOOL; (*空调机组NJ-3AP(KT)5-7-风机压差*)"},"LAHU03E07_FPS           AT%I17.3       :BOOL; (*空调机组NJ-3AP(KT)5-7-风机压差*)",null,"L23\\L23AHU03E07_FPS","空调机组NJ-3AP(KT)5-7-风机压差",10139]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-3AL5-1-运行状态",{"$nulls":16},"NJ-3AL5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL5-1","03E01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB03E01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B27*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB03E01_R AT%I17.4 :BOOL; (*照明控制箱NJ-3AL5-1-运行状态*)"},"LLCB03E01_R             AT%I17.4       :BOOL; (*照明控制箱NJ-3AL5-1-运行状态*)",null,"L23\\L23LCB03E01_R","照明控制箱NJ-3AL5-1-运行状态",10140]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-3AL5-1-自动状态",{"$nulls":16},"NJ-3AL5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL5-1","03E01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB03E01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B27*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB03E01_A AT%I17.5 :BOOL; (*照明控制箱NJ-3AL5-1-自动状态*)"},"LLCB03E01_A             AT%I17.5       :BOOL; (*照明控制箱NJ-3AL5-1-自动状态*)",null,"L23\\L23LCB03E01_A","照明控制箱NJ-3AL5-1-自动状态",10141]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-3AL5-2-运行状态",{"$nulls":16},"NJ-3AL5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL5-2","03E02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"LCB03E02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B27*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LLCB03E02_R AT%I17.6 :BOOL; (*照明控制箱NJ-3AL5-2-运行状态*)"},"LLCB03E02_R             AT%I17.6       :BOOL; (*照明控制箱NJ-3AL5-2-运行状态*)",null,"L23\\L23LCB03E02_R","照明控制箱NJ-3AL5-2-运行状态",10142]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-3AL5-2-自动状态",{"$nulls":16},"NJ-3AL5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL5-2","03E02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":"LCB03E02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%I\"&B27*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":"LLCB03E02_A AT%I17.7 :BOOL; (*照明控制箱NJ-3AL5-2-自动状态*)"},"LLCB03E02_A             AT%I17.7       :BOOL; (*照明控制箱NJ-3AL5-2-自动状态*)",null,"L23\\L23LCB03E02_A","照明控制箱NJ-3AL5-2-自动状态",10143]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 1601R地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH43&AA43&\"-\"&AK43","v":"照明控制箱NJ-3AL5-3-运行状态"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-3AL5-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL5-3","03E03","运行状态",{"$f":"AH43&\"-\"&AK43","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"LCB03E03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B44*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LLCB03E03_R AT%I32.0 :BOOL; (*照明控制箱NJ-3AL5-3-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LLCB03E03_R             AT%I32.0       :BOOL; (*照明控制箱NJ-3AL5-3-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM43","v":"L23\\L23LCB03E03_R"},{"$f":"J43","v":"照明控制箱NJ-3AL5-3-运行状态"},{"$f":"10000+($B44*16*8+F43-1)","v":10256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},2,null,3,4,"照明控制箱NJ-3AL5-3-自动状态",{"$nulls":16},{"$f":"IF(AI44=\"\",\"\",AI44)","v":"NJ-3AL5-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL5-3","03E03","自动状态",{"$f":"AH44&\"-\"&AK44","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"LCB03E03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B44*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LLCB03E03_A AT%I32.1 :BOOL; (*照明控制箱NJ-3AL5-3-自动状态*)"},"LLCB03E03_A             AT%I32.1       :BOOL; (*照明控制箱NJ-3AL5-3-自动状态*)",null,"L23\\L23LCB03E03_A",{"$f":"J44","v":"照明控制箱NJ-3AL5-3-自动状态"},{"$f":"AS43+1","v":10257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,5,6,"照明控制箱NJ-3AL5-4-运行状态",{"$nulls":16},"NJ-3AL5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL5-4","03E04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"LCB03E04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B44*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LLCB03E04_R AT%I32.2 :BOOL; (*照明控制箱NJ-3AL5-4-运行状态*)"},"LLCB03E04_R             AT%I32.2       :BOOL; (*照明控制箱NJ-3AL5-4-运行状态*)",null,"L23\\L23LCB03E04_R","照明控制箱NJ-3AL5-4-运行状态",{"$f":"AS44+1","v":10258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},4,null,7,8,"照明控制箱NJ-3AL5-4-自动状态",{"$nulls":16},"NJ-3AL5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-3AL5-4","03E04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"LCB03E04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B44*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LLCB03E04_A AT%I32.3 :BOOL; (*照明控制箱NJ-3AL5-4-自动状态*)"},"LLCB03E04_A             AT%I32.3       :BOOL; (*照明控制箱NJ-3AL5-4-自动状态*)",null,"L23\\L23LCB03E04_A","照明控制箱NJ-3AL5-4-自动状态",10259]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-3AL5-5-运行状态",{"$nulls":16},"NJ-3AL5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL5-5","03E05","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"LCB03E05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B44*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LLCB03E05_R AT%I32.4 :BOOL; (*照明控制箱NJ-3AL5-5-运行状态*)"},"LLCB03E05_R             AT%I32.4       :BOOL; (*照明控制箱NJ-3AL5-5-运行状态*)",null,"L23\\L23LCB03E05_R","照明控制箱NJ-3AL5-5-运行状态",10260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-3AL5-5-自动状态",{"$nulls":16},"NJ-3AL5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"照明控制箱","NJ-3AL5-5","03E05","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"LCB03E05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B44*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LLCB03E05_A AT%I32.5 :BOOL; (*照明控制箱NJ-3AL5-5-自动状态*)"},"LLCB03E05_A             AT%I32.5       :BOOL; (*照明控制箱NJ-3AL5-5-自动状态*)",null,"L23\\L23LCB03E05_A","照明控制箱NJ-3AL5-5-自动状态",10261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"照明控制箱NJ-3AL(GG)5-1-运行状态",{"$nulls":16},"NJ-3AL(GG)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)5-1","03E06","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"LCB03E06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B44*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LLCB03E06_R AT%I32.6 :BOOL; (*照明控制箱NJ-3AL(GG)5-1-运行状态*)"},"LLCB03E06_R             AT%I32.6       :BOOL; (*照明控制箱NJ-3AL(GG)5-1-运行状态*)",null,"L23\\L23LCB03E06_R","照明控制箱NJ-3AL(GG)5-1-运行状态",10262]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"照明控制箱NJ-3AL(GG)5-1-自动状态",{"$nulls":16},"NJ-3AL(GG)5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)5-1","03E06","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"LCB03E06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B44*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LLCB03E06_A AT%I32.7 :BOOL; (*照明控制箱NJ-3AL(GG)5-1-自动状态*)"},"LLCB03E06_A             AT%I32.7       :BOOL; (*照明控制箱NJ-3AL(GG)5-1-自动状态*)",null,"L23\\L23LCB03E06_A","照明控制箱NJ-3AL(GG)5-1-自动状态",10263]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-3AL(GG)5-2-运行状态",{"$nulls":16},"NJ-3AL(GG)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)5-2","03E07","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"LCB03E07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B44*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LLCB03E07_R AT%I33.0 :BOOL; (*照明控制箱NJ-3AL(GG)5-2-运行状态*)"},"LLCB03E07_R             AT%I33.0       :BOOL; (*照明控制箱NJ-3AL(GG)5-2-运行状态*)",null,"L23\\L23LCB03E07_R","照明控制箱NJ-3AL(GG)5-2-运行状态",10264]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-3AL(GG)5-2-自动状态",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-3AL(GG)5-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)5-2","03E07","自动状态",{"$f":"AH52&\"-\"&AK52","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"LCB03E07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%I\"&B44*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LLCB03E07_A AT%I33.1 :BOOL; (*照明控制箱NJ-3AL(GG)5-2-自动状态*)"},"LLCB03E07_A             AT%I33.1       :BOOL; (*照明控制箱NJ-3AL(GG)5-2-自动状态*)",null,"L23\\L23LCB03E07_A",{"$f":"J52","v":"照明控制箱NJ-3AL(GG)5-2-自动状态"},10265]
[{"$nulls":5},11,null,21,22,"照明控制箱NJ-3AL(GG)5-3-运行状态",{"$nulls":16},"NJ-3AL(GG)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)5-3","03E08","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"LCB03E08_R"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%I\"&B44*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LLCB03E08_R AT%I33.2 :BOOL; (*照明控制箱NJ-3AL(GG)5-3-运行状态*)"},"LLCB03E08_R             AT%I33.2       :BOOL; (*照明控制箱NJ-3AL(GG)5-3-运行状态*)",null,"L23\\L23LCB03E08_R","照明控制箱NJ-3AL(GG)5-3-运行状态",10266]
[{"$nulls":5},12,null,23,24,"照明控制箱NJ-3AL(GG)5-3-自动状态",{"$nulls":16},"NJ-3AL(GG)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)5-3","03E08","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"LCB03E08_A"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%I\"&B44*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LLCB03E08_A AT%I33.3 :BOOL; (*照明控制箱NJ-3AL(GG)5-3-自动状态*)"},"LLCB03E08_A             AT%I33.3       :BOOL; (*照明控制箱NJ-3AL(GG)5-3-自动状态*)",null,"L23\\L23LCB03E08_A","照明控制箱NJ-3AL(GG)5-3-自动状态",10267]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-3AL(GG)5-4-运行状态",{"$nulls":16},"NJ-3AL(GG)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)5-4","03E09","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"LCB03E09_R"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%I\"&B44*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LLCB03E09_R AT%I33.4 :BOOL; (*照明控制箱NJ-3AL(GG)5-4-运行状态*)"},"LLCB03E09_R             AT%I33.4       :BOOL; (*照明控制箱NJ-3AL(GG)5-4-运行状态*)",null,"L23\\L23LCB03E09_R","照明控制箱NJ-3AL(GG)5-4-运行状态",10268]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-3AL(GG)5-4-自动状态",{"$nulls":16},"NJ-3AL(GG)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)5-4","03E09","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"LCB03E09_A"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%I\"&B44*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LLCB03E09_A AT%I33.5 :BOOL; (*照明控制箱NJ-3AL(GG)5-4-自动状态*)"},"LLCB03E09_A             AT%I33.5       :BOOL; (*照明控制箱NJ-3AL(GG)5-4-自动状态*)",null,"L23\\L23LCB03E09_A","照明控制箱NJ-3AL(GG)5-4-自动状态",10269]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-3AL(GG)5-5-运行状态",{"$nulls":16},"NJ-3AL(GG)5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)5-5","03E10","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"LCB03E10_R"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%I\"&B44*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LLCB03E10_R AT%I33.6 :BOOL; (*照明控制箱NJ-3AL(GG)5-5-运行状态*)"},"LLCB03E10_R             AT%I33.6       :BOOL; (*照明控制箱NJ-3AL(GG)5-5-运行状态*)",null,"L23\\L23LCB03E10_R","照明控制箱NJ-3AL(GG)5-5-运行状态",10270]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-3AL(GG)5-5-自动状态",{"$nulls":16},"NJ-3AL(GG)5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)5-5","03E10","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":"LCB03E10_A"},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%I\"&B44*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":"LLCB03E10_A AT%I33.7 :BOOL; (*照明控制箱NJ-3AL(GG)5-5-自动状态*)"},"LLCB03E10_A             AT%I33.7       :BOOL; (*照明控制箱NJ-3AL(GG)5-5-自动状态*)",null,"L23\\L23LCB03E10_A","照明控制箱NJ-3AL(GG)5-5-自动状态",10271]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B64&\"地址: \"&B61&\" *)\"","v":"(* IOM 0801R 地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},1,null,1,"C",{"$f":"AH60&AA60&\"-\"&AK60","v":"膨胀水箱-超高液位"},{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"膨胀水箱",null,"03E01","超高液位",{"$f":"AH60&\"-\"&AK60","v":"膨胀水箱-超高液位"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"EWT03E01_SHL"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%I\"&B61*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LEWT03E01_SHL AT%I48.0 :BOOL; (*膨胀水箱-超高液位*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60))),SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))))),\" \")","v":"LEWT03E01_SHL           AT%I48.0       :BOOL; (*膨胀水箱-超高液位*)"},null,{"$f":"AM60","v":"EWT03E01_SHL"},{"$f":"J60","v":"膨胀水箱-超高液位"},{"$f":"10000+($B61*16*8+F60-1)","v":10384}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},2,null,2,"C",{"$f":"AH61&AA61&\"-\"&AK61","v":"膨胀水箱-超低液位"},{"$nulls":16},{"$f":"IF(AI61=\"\",\"\",AI61)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"膨胀水箱",null,"03E01","超低液位",{"$f":"AH61&\"-\"&AK61","v":"膨胀水箱-超低液位"},{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"EWT03E01_SLL"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%I\"&B61*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LEWT03E01_SLL AT%I48.1 :BOOL; (*膨胀水箱-超低液位*)"},"LEWT03E01_SLL           AT%I48.1       :BOOL; (*膨胀水箱-超低液位*)",null,{"$f":"AM61","v":"EWT03E01_SLL"},{"$f":"J61","v":"膨胀水箱-超低液位"},{"$f":"AS60+1","v":10385}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},3,null,3,"C",{"$f":"AH62&AA62&\"-\"&AK62","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B61*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS61+1","v":10386}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},4,null,4,"C",{"$f":"AH63&AA63&\"-\"&AK63","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B61*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10387]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},5,null,5,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B61*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10388]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B61*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10389]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B61*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10390]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%I\"&B61*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10391]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B73&\"地址: \"&B70&\" *)\"","v":"(* IOM 1601D地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH69&AA69&\"-\"&AK69","v":"空调机组NJ-3AP(KT)5-1-启停控制"},{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-3AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-1","03E01","启停控制",{"$f":"AH69&\"-\"&AK69","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU03E01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%Q\"&B70*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU03E01_C AT%Q64.0 :BOOL; (*空调机组NJ-3AP(KT)5-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69))),SEARCH(\":\",REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69)))))),\" \")","v":"LAHU03E01_C             AT%Q64.0       :BOOL; (*空调机组NJ-3AP(KT)5-1-启停控制*)"},null,{"$f":"AM69","v":"AHU03E01_C"},{"$f":"J69","v":"空调机组NJ-3AP(KT)5-1-启停控制"},{"$f":"($B70*16*8+F69-1)","v":512}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","空调机组NJ-3AP(KT)5-2-启停控制",{"$nulls":16},{"$f":"IF(AI70=\"\",\"\",AI70)","v":"NJ-3AP(KT)5-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-2","03E02","启停控制",{"$f":"AH70&\"-\"&AK70","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"AHU03E02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%Q\"&B70*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LAHU03E02_C AT%Q64.1 :BOOL; (*空调机组NJ-3AP(KT)5-2-启停控制*)"},"LAHU03E02_C             AT%Q64.1       :BOOL; (*空调机组NJ-3AP(KT)5-2-启停控制*)",null,"AHU03E02_C",{"$f":"J70","v":"空调机组NJ-3AP(KT)5-2-启停控制"},{"$f":"AS69+1","v":513}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-3AP(KT)5-3-启停控制",{"$nulls":16},"NJ-3AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-3","03E03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"AHU03E03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%Q\"&B70*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LAHU03E03_C AT%Q64.2 :BOOL; (*空调机组NJ-3AP(KT)5-3-启停控制*)"},"LAHU03E03_C             AT%Q64.2       :BOOL; (*空调机组NJ-3AP(KT)5-3-启停控制*)",null,"AHU03E03_C","空调机组NJ-3AP(KT)5-3-启停控制",{"$f":"AS70+1","v":514}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","空调机组NJ-3AP(KT)5-4-启停控制",{"$nulls":16},"NJ-3AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-4","03E04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"AHU03E04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%Q\"&B70*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LAHU03E04_C AT%Q64.3 :BOOL; (*空调机组NJ-3AP(KT)5-4-启停控制*)"},"LAHU03E04_C             AT%Q64.3       :BOOL; (*空调机组NJ-3AP(KT)5-4-启停控制*)",null,"AHU03E04_C","空调机组NJ-3AP(KT)5-4-启停控制",515]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-3AP(KT)5-5-启停控制",{"$nulls":16},"NJ-3AP(KT)5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-5","03E05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"AHU03E05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%Q\"&B70*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LAHU03E05_C AT%Q64.4 :BOOL; (*空调机组NJ-3AP(KT)5-5-启停控制*)"},"LAHU03E05_C             AT%Q64.4       :BOOL; (*空调机组NJ-3AP(KT)5-5-启停控制*)",null,"AHU03E05_C","空调机组NJ-3AP(KT)5-5-启停控制",516]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-3AP(KT)5-6-启停控制",{"$nulls":16},"NJ-3AP(KT)5-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-6","03E06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":"AHU03E06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%Q\"&B70*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":"LAHU03E06_C AT%Q64.5 :BOOL; (*空调机组NJ-3AP(KT)5-6-启停控制*)"},"LAHU03E06_C             AT%Q64.5       :BOOL; (*空调机组NJ-3AP(KT)5-6-启停控制*)",null,"AHU03E06_C","空调机组NJ-3AP(KT)5-6-启停控制",517]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","空调机组NJ-3AP(KT)5-7-启停控制",{"$nulls":16},"NJ-3AP(KT)5-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-7","03E07","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":"AHU03E07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%Q\"&B70*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":"LAHU03E07_C AT%Q64.6 :BOOL; (*空调机组NJ-3AP(KT)5-7-启停控制*)"},"LAHU03E07_C             AT%Q64.6       :BOOL; (*空调机组NJ-3AP(KT)5-7-启停控制*)",null,"AHU03E07_C","空调机组NJ-3AP(KT)5-7-启停控制",518]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-3AL5-1-启停控制",{"$nulls":16},"NJ-3AL5-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL5-1","03E01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH76,List!$B$3:$D$445,2,FALSE)&AJ76&\"_\"&VLOOKUP(AK76,List!$K$2:$M$447,2,FALSE)","v":"LCB03E01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM76&\" \"&\"AT%Q\"&B70*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J76&\"*)\",\" \")","v":"LLCB03E01_C AT%Q64.7 :BOOL; (*照明控制箱NJ-3AL5-1-启停控制*)"},"LLCB03E01_C             AT%Q64.7       :BOOL; (*照明控制箱NJ-3AL5-1-启停控制*)",null,"LCB03E01_C","照明控制箱NJ-3AL5-1-启停控制",519]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-3AL5-2-启停控制",{"$nulls":16},"NJ-3AL5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL5-2","03E02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"LCB03E02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%Q\"&B70*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LLCB03E02_C AT%Q65.0 :BOOL; (*照明控制箱NJ-3AL5-2-启停控制*)"},"LLCB03E02_C             AT%Q65.0       :BOOL; (*照明控制箱NJ-3AL5-2-启停控制*)",null,"LCB03E02_C","照明控制箱NJ-3AL5-2-启停控制",520]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-3AL5-3-启停控制",{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-3AL5-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL5-3","03E03","启停控制",{"$f":"AH78&\"-\"&AK78","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"LCB03E03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B70*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LLCB03E03_C AT%Q65.1 :BOOL; (*照明控制箱NJ-3AL5-3-启停控制*)"},"LLCB03E03_C             AT%Q65.1       :BOOL; (*照明控制箱NJ-3AL5-3-启停控制*)",null,"LCB03E03_C",{"$f":"J78","v":"照明控制箱NJ-3AL5-3-启停控制"},521]
[{"$nulls":5},11,null,"11+","11-","照明控制箱NJ-3AL5-4-启停控制",{"$nulls":16},"NJ-3AL5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL5-4","03E04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"LCB03E04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B70*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LLCB03E04_C AT%Q65.2 :BOOL; (*照明控制箱NJ-3AL5-4-启停控制*)"},"LLCB03E04_C             AT%Q65.2       :BOOL; (*照明控制箱NJ-3AL5-4-启停控制*)",null,"LCB03E04_C","照明控制箱NJ-3AL5-4-启停控制",522]
[{"$nulls":5},12,null,"12+","12-","照明控制箱NJ-3AL5-5-启停控制",{"$nulls":16},"NJ-3AL5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL5-5","03E05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"LCB03E05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B70*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LLCB03E05_C AT%Q65.3 :BOOL; (*照明控制箱NJ-3AL5-5-启停控制*)"},"LLCB03E05_C             AT%Q65.3       :BOOL; (*照明控制箱NJ-3AL5-5-启停控制*)",null,"LCB03E05_C","照明控制箱NJ-3AL5-5-启停控制",523]
[{"$nulls":5},13,null,"13+","13-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%Q\"&B70*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",524]
[{"$nulls":5},14,null,"14+","14-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%Q\"&B70*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",525]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%Q\"&B70*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",526]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH84,List!$B$3:$D$445,2,FALSE)&AJ84&\"_\"&VLOOKUP(AK84,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM84&\" \"&\"AT%Q\"&B70*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J84&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",527]
[null,"IOM 0801D",{"$nulls":38},{"$f":"\"(* \"&B90&\"地址: \"&B87&\" *)\"","v":"(* IOM 0801D地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH86&AA86&\"-\"&AK86","v":"照明控制箱NJ-3AL(GG)5-1-启停控制"},{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-3AL(GG)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)5-1","03E06","启停控制",{"$f":"AH86&\"-\"&AK86","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"LCB03E06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%Q\"&B87*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LLCB03E06_C AT%Q80.0 :BOOL; (*照明控制箱NJ-3AL(GG)5-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86))),SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))))),\" \")","v":"LLCB03E06_C             AT%Q80.0       :BOOL; (*照明控制箱NJ-3AL(GG)5-1-启停控制*)"},null,{"$f":"AM86","v":"LCB03E06_C"},{"$f":"J86","v":"照明控制箱NJ-3AL(GG)5-1-启停控制"},{"$f":"($B87*16*8+F86-1)","v":640}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","照明控制箱NJ-3AL(GG)5-2-启停控制",{"$nulls":16},{"$f":"IF(AI87=\"\",\"\",AI87)","v":"NJ-3AL(GG)5-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)5-2","03E07","启停控制",{"$f":"AH87&\"-\"&AK87","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"LCB03E07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%Q\"&B87*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LLCB03E07_C AT%Q80.1 :BOOL; (*照明控制箱NJ-3AL(GG)5-2-启停控制*)"},"LLCB03E07_C             AT%Q80.1       :BOOL; (*照明控制箱NJ-3AL(GG)5-2-启停控制*)",null,"LCB03E07_C",{"$f":"J87","v":"照明控制箱NJ-3AL(GG)5-2-启停控制"},{"$f":"AS86+1","v":641}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","照明控制箱NJ-3AL(GG)5-3-启停控制",{"$nulls":16},"NJ-3AL(GG)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)5-3","03E08","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"LCB03E08_C"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%Q\"&B87*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LLCB03E08_C AT%Q80.2 :BOOL; (*照明控制箱NJ-3AL(GG)5-3-启停控制*)"},"LLCB03E08_C             AT%Q80.2       :BOOL; (*照明控制箱NJ-3AL(GG)5-3-启停控制*)",null,"LCB03E08_C","照明控制箱NJ-3AL(GG)5-3-启停控制",{"$f":"AS87+1","v":642}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","照明控制箱NJ-3AL(GG)5-4-启停控制",{"$nulls":16},"NJ-3AL(GG)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)5-4","03E09","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"LCB03E09_C"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%Q\"&B87*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LLCB03E09_C AT%Q80.3 :BOOL; (*照明控制箱NJ-3AL(GG)5-4-启停控制*)"},"LLCB03E09_C             AT%Q80.3       :BOOL; (*照明控制箱NJ-3AL(GG)5-4-启停控制*)",null,"LCB03E09_C","照明控制箱NJ-3AL(GG)5-4-启停控制",643]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","照明控制箱NJ-3AL(GG)5-5-启停控制",{"$nulls":16},"NJ-3AL(GG)5-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)5-5","03E10","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":"LCB03E10_C"},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%Q\"&B87*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":"LLCB03E10_C AT%Q80.4 :BOOL; (*照明控制箱NJ-3AL(GG)5-5-启停控制*)"},"LLCB03E10_C             AT%Q80.4       :BOOL; (*照明控制箱NJ-3AL(GG)5-5-启停控制*)",null,"LCB03E10_C","照明控制箱NJ-3AL(GG)5-5-启停控制",644]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH91,List!$B$3:$D$445,2,FALSE)&AJ91&\"_\"&VLOOKUP(AK91,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM91&\" \"&\"AT%Q\"&B87*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J91&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",645]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH92,List!$B$3:$D$445,2,FALSE)&AJ92&\"_\"&VLOOKUP(AK92,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM92&\" \"&\"AT%Q\"&B87*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J92&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",646]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL93,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL93,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH93,List!$B$3:$D$445,2,FALSE)&AJ93&\"_\"&VLOOKUP(AK93,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM93&\" \"&\"AT%Q\"&B87*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J93&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",647]
[null,{"$f":"B99","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B99&\"地址: \"&B96&\" *)\"","v":"(* IOM 0801U地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH95&AA95&\"-\"&AK95","v":"空调机组NJ-3AP(KT)5-1-回风温度"},{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-3AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-1","03E01","回风温度",{"$f":"AH95&\"-\"&AK95","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"AHU03E01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%I\"&B96*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LAHU03E01_RT AT%I96.0 :INT ; (*空调机组NJ-3AP(KT)5-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95))),SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))))),\" \")","v":"LAHU03E01_RT            AT%I96.0       :INT ; (*空调机组NJ-3AP(KT)5-1-回风温度*)"},null,{"$f":"AM95","v":"AHU03E01_RT"},{"$f":"J95","v":"空调机组NJ-3AP(KT)5-1-回风温度"},{"$f":"30000+($B96*8+F95-1)","v":30048}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-3AP(KT)5-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI96=\"\",\"\",AI96)","v":"NJ-3AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-1","03E01","水阀反馈",{"$f":"AH96&\"-\"&AK96","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"AHU03E01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%I\"&B96*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LAHU03E01_WVB AT%I98.0 :INT ; (*空调机组NJ-3AP(KT)5-1-水阀反馈*)"},"LAHU03E01_WVB           AT%I98.0       :INT ; (*空调机组NJ-3AP(KT)5-1-水阀反馈*)",null,"AHU03E01_WVB",{"$f":"J96","v":"空调机组NJ-3AP(KT)5-1-水阀反馈"},{"$f":"AS95+1","v":30049}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)5-2-回风温度",{"$nulls":16},"NJ-3AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-2","03E02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":"AHU03E02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%I\"&B96*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":"LAHU03E02_RT AT%I100.0 :INT ; (*空调机组NJ-3AP(KT)5-2-回风温度*)"},"LAHU03E02_RT            AT%I100.0      :INT ; (*空调机组NJ-3AP(KT)5-2-回风温度*)",null,"AHU03E02_RT","空调机组NJ-3AP(KT)5-2-回风温度",{"$f":"AS96+1","v":30050}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-3AP(KT)5-2-水阀反馈",{"$nulls":16},"NJ-3AP(KT)5-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-2","03E02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":"AHU03E02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%I\"&B96*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":"LAHU03E02_WVB AT%I102.0 :INT ; (*空调机组NJ-3AP(KT)5-2-水阀反馈*)"},"LAHU03E02_WVB           AT%I102.0      :INT ; (*空调机组NJ-3AP(KT)5-2-水阀反馈*)",null,"AHU03E02_WVB","空调机组NJ-3AP(KT)5-2-水阀反馈",30051]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-3AP(KT)5-3-回风温度",{"$nulls":16},"NJ-3AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-3","03E03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH99,List!$B$3:$D$445,2,FALSE)&AJ99&\"_\"&VLOOKUP(AK99,List!$K$2:$M$447,2,FALSE)","v":"AHU03E03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM99&\" \"&\"AT%I\"&B96*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J99&\"*)\",\" \")","v":"LAHU03E03_RT AT%I104.0 :INT ; (*空调机组NJ-3AP(KT)5-3-回风温度*)"},"LAHU03E03_RT            AT%I104.0      :INT ; (*空调机组NJ-3AP(KT)5-3-回风温度*)",null,"AHU03E03_RT","空调机组NJ-3AP(KT)5-3-回风温度",30052]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-3AP(KT)5-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI100=\"\",\"\",AI100)","v":"NJ-3AP(KT)5-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-3","03E03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH100,List!$B$3:$D$445,2,FALSE)&AJ100&\"_\"&VLOOKUP(AK100,List!$K$2:$M$447,2,FALSE)","v":"AHU03E03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM100&\" \"&\"AT%I\"&B96*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J100&\"*)\",\" \")","v":"LAHU03E03_WVB AT%I106.0 :INT ; (*空调机组NJ-3AP(KT)5-3-水阀反馈*)"},"LAHU03E03_WVB           AT%I106.0      :INT ; (*空调机组NJ-3AP(KT)5-3-水阀反馈*)",null,"AHU03E03_WVB",{"$f":"J100","v":"空调机组NJ-3AP(KT)5-3-水阀反馈"},30053]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-3AP(KT)5-4-回风温度",{"$nulls":16},"NJ-3AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-4","03E04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH101,List!$B$3:$D$445,2,FALSE)&AJ101&\"_\"&VLOOKUP(AK101,List!$K$2:$M$447,2,FALSE)","v":"AHU03E04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM101&\" \"&\"AT%I\"&B96*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J101&\"*)\",\" \")","v":"LAHU03E04_RT AT%I108.0 :INT ; (*空调机组NJ-3AP(KT)5-4-回风温度*)"},"LAHU03E04_RT            AT%I108.0      :INT ; (*空调机组NJ-3AP(KT)5-4-回风温度*)",null,"AHU03E04_RT","空调机组NJ-3AP(KT)5-4-回风温度",30054]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-3AP(KT)5-4-水阀反馈",{"$nulls":16},"NJ-3AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL102,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL102,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-4","03E04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH102,List!$B$3:$D$445,2,FALSE)&AJ102&\"_\"&VLOOKUP(AK102,List!$K$2:$M$447,2,FALSE)","v":"AHU03E04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM102&\" \"&\"AT%I\"&B96*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J102&\"*)\",\" \")","v":"LAHU03E04_WVB AT%I110.0 :INT ; (*空调机组NJ-3AP(KT)5-4-水阀反馈*)"},"LAHU03E04_WVB           AT%I110.0      :INT ; (*空调机组NJ-3AP(KT)5-4-水阀反馈*)",null,"AHU03E04_WVB","空调机组NJ-3AP(KT)5-4-水阀反馈",30055]
[null,{"$f":"B108","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B108&\"地址: \"&B105&\" *)\"","v":"(* IOM 0801U地址: 7 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH104&AA104&\"-\"&AK104","v":"空调机组NJ-3AP(KT)5-5-回风温度"},{"$nulls":16},{"$f":"IF(AI104=\"\",\"\",AI104)","v":"NJ-3AP(KT)5-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-5","03E05","回风温度",{"$f":"AH104&\"-\"&AK104","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"AHU03E05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%I\"&B105*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LAHU03E05_RT AT%I112.0 :INT ; (*空调机组NJ-3AP(KT)5-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104))),SEARCH(\":\",REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104)))))),\" \")","v":"LAHU03E05_RT            AT%I112.0      :INT ; (*空调机组NJ-3AP(KT)5-5-回风温度*)"},null,{"$f":"AM104","v":"AHU03E05_RT"},{"$f":"J104","v":"空调机组NJ-3AP(KT)5-5-回风温度"},{"$f":"30000+($B105*8+F104-1)","v":30056}]
[null,7,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-3AP(KT)5-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI105=\"\",\"\",AI105)","v":"NJ-3AP(KT)5-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-5","03E05","水阀反馈",{"$f":"AH105&\"-\"&AK105","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"AHU03E05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%I\"&B105*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LAHU03E05_WVB AT%I114.0 :INT ; (*空调机组NJ-3AP(KT)5-5-水阀反馈*)"},"LAHU03E05_WVB           AT%I114.0      :INT ; (*空调机组NJ-3AP(KT)5-5-水阀反馈*)",null,"AHU03E05_WVB",{"$f":"J105","v":"空调机组NJ-3AP(KT)5-5-水阀反馈"},{"$f":"AS104+1","v":30057}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)5-6-回风温度",{"$nulls":16},"NJ-3AP(KT)5-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-6","03E06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":"AHU03E06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%I\"&B105*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":"LAHU03E06_RT AT%I116.0 :INT ; (*空调机组NJ-3AP(KT)5-6-回风温度*)"},"LAHU03E06_RT            AT%I116.0      :INT ; (*空调机组NJ-3AP(KT)5-6-回风温度*)",null,"AHU03E06_RT","空调机组NJ-3AP(KT)5-6-回风温度",{"$f":"AS105+1","v":30058}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-3AP(KT)5-6-水阀反馈",{"$nulls":16},"NJ-3AP(KT)5-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-6","03E06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH107,List!$B$3:$D$445,2,FALSE)&AJ107&\"_\"&VLOOKUP(AK107,List!$K$2:$M$447,2,FALSE)","v":"AHU03E06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM107&\" \"&\"AT%I\"&B105*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J107&\"*)\",\" \")","v":"LAHU03E06_WVB AT%I118.0 :INT ; (*空调机组NJ-3AP(KT)5-6-水阀反馈*)"},"LAHU03E06_WVB           AT%I118.0      :INT ; (*空调机组NJ-3AP(KT)5-6-水阀反馈*)",null,"AHU03E06_WVB","空调机组NJ-3AP(KT)5-6-水阀反馈",30059]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-3AP(KT)5-7-回风温度",{"$nulls":16},"NJ-3AP(KT)5-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-7","03E07","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH108,List!$B$3:$D$445,2,FALSE)&AJ108&\"_\"&VLOOKUP(AK108,List!$K$2:$M$447,2,FALSE)","v":"AHU03E07_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM108&\" \"&\"AT%I\"&B105*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J108&\"*)\",\" \")","v":"LAHU03E07_RT AT%I120.0 :INT ; (*空调机组NJ-3AP(KT)5-7-回风温度*)"},"LAHU03E07_RT            AT%I120.0      :INT ; (*空调机组NJ-3AP(KT)5-7-回风温度*)",null,"AHU03E07_RT","空调机组NJ-3AP(KT)5-7-回风温度",30060]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-3AP(KT)5-7-水阀反馈",{"$nulls":16},"NJ-3AP(KT)5-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-7","03E07","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH109,List!$B$3:$D$445,2,FALSE)&AJ109&\"_\"&VLOOKUP(AK109,List!$K$2:$M$447,2,FALSE)","v":"AHU03E07_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM109&\" \"&\"AT%I\"&B105*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J109&\"*)\",\" \")","v":"LAHU03E07_WVB AT%I122.0 :INT ; (*空调机组NJ-3AP(KT)5-7-水阀反馈*)"},"LAHU03E07_WVB           AT%I122.0      :INT ; (*空调机组NJ-3AP(KT)5-7-水阀反馈*)",null,"AHU03E07_WVB",{"$f":"J109","v":"空调机组NJ-3AP(KT)5-7-水阀反馈"},30061]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL110,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL110,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH110,List!$B$3:$D$445,2,FALSE)&AJ110&\"_\"&VLOOKUP(AK110,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM110&\" \"&\"AT%I\"&B105*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J110&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30062]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},{"$f":"IF(AI111=\"\",\"\",AI111)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL111,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL111,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH111,List!$B$3:$D$445,2,FALSE)&AJ111&\"_\"&VLOOKUP(AK111,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM111&\" \"&\"AT%I\"&B105*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J111&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30063]
[null,{"$f":"B117","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B117&\"地址: \"&B114&\" *)\"","v":"(* IOM 0401A地址: 8 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH113&AA113&\"-\"&AK113","v":"空调机组NJ-3AP(KT)5-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI113=\"\",\"\",AI113)","v":"NJ-3AP(KT)5-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-1","03E01","水阀控制",{"$f":"AH113&\"-\"&AK113","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH113,List!$B$3:$D$445,2,FALSE)&AJ113&\"_\"&VLOOKUP(AK113,List!$K$2:$M$447,2,FALSE)","v":"AHU03E01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM113&\" \"&\"AT%Q\"&B114*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J113&\"*)\",\" \")","v":"LAHU03E01_WVC AT%Q128.0 :INT ; (*空调机组NJ-3AP(KT)5-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN113,SEARCH(\"AT%\",AN113),,REPT(\" \",25-SEARCH(\"AT%\",AN113))),SEARCH(\":\",REPLACE(AN113,SEARCH(\"AT%\",AN113),,REPT(\" \",25-SEARCH(\"AT%\",AN113)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN113,SEARCH(\"AT%\",AN113),,REPT(\" \",25-SEARCH(\"AT%\",AN113)))))),\" \")","v":"LAHU03E01_WVC           AT%Q128.0      :INT ; (*空调机组NJ-3AP(KT)5-1-水阀控制*)"},null,{"$f":"AM113","v":"AHU03E01_WVC"},{"$f":"J113","v":"空调机组NJ-3AP(KT)5-1-水阀控制"},{"$f":"40000+($B114*8+F113-1)","v":40064}]
[null,8,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH114&AA114&\"-\"&AK114","v":"空调机组NJ-3AP(KT)5-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI114=\"\",\"\",AI114)","v":"NJ-3AP(KT)5-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-2","03E02","水阀控制",{"$f":"AH114&\"-\"&AK114","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH114,List!$B$3:$D$445,2,FALSE)&AJ114&\"_\"&VLOOKUP(AK114,List!$K$2:$M$447,2,FALSE)","v":"AHU03E02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM114&\" \"&\"AT%Q\"&B114*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J114&\"*)\",\" \")","v":"LAHU03E02_WVC AT%Q130.0 :INT ; (*空调机组NJ-3AP(KT)5-2-水阀控制*)"},"LAHU03E02_WVC           AT%Q130.0      :INT ; (*空调机组NJ-3AP(KT)5-2-水阀控制*)",null,"AHU03E02_WVC",{"$f":"J114","v":"空调机组NJ-3AP(KT)5-2-水阀控制"},{"$f":"AS113+1","v":40065}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH115&AA115&\"-\"&AK115","v":"空调机组NJ-3AP(KT)5-3-水阀控制"},{"$nulls":16},"NJ-3AP(KT)5-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-3","03E03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH115,List!$B$3:$D$445,2,FALSE)&AJ115&\"_\"&VLOOKUP(AK115,List!$K$2:$M$447,2,FALSE)","v":"AHU03E03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM115&\" \"&\"AT%Q\"&B114*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J115&\"*)\",\" \")","v":"LAHU03E03_WVC AT%Q132.0 :INT ; (*空调机组NJ-3AP(KT)5-3-水阀控制*)"},"LAHU03E03_WVC           AT%Q132.0      :INT ; (*空调机组NJ-3AP(KT)5-3-水阀控制*)",null,"AHU03E03_WVC","空调机组NJ-3AP(KT)5-3-水阀控制",{"$f":"AS114+1","v":40066}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH116&AA116&\"-\"&AK116","v":"空调机组NJ-3AP(KT)5-4-水阀控制"},{"$nulls":16},"NJ-3AP(KT)5-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-4","03E04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH116,List!$B$3:$D$445,2,FALSE)&AJ116&\"_\"&VLOOKUP(AK116,List!$K$2:$M$447,2,FALSE)","v":"AHU03E04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM116&\" \"&\"AT%Q\"&B114*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J116&\"*)\",\" \")","v":"LAHU03E04_WVC AT%Q134.0 :INT ; (*空调机组NJ-3AP(KT)5-4-水阀控制*)"},"LAHU03E04_WVC           AT%Q134.0      :INT ; (*空调机组NJ-3AP(KT)5-4-水阀控制*)",null,"AHU03E04_WVC","空调机组NJ-3AP(KT)5-4-水阀控制",40067]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B126","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B126&\"地址: \"&B123&\" *)\"","v":"(* IOM 0401A地址: 9 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH122&AA122&\"-\"&AK122","v":"空调机组NJ-3AP(KT)5-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI122=\"\",\"\",AI122)","v":"NJ-3AP(KT)5-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-5","03E05","水阀控制",{"$f":"AH122&\"-\"&AK122","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH122,List!$B$3:$D$445,2,FALSE)&AJ122&\"_\"&VLOOKUP(AK122,List!$K$2:$M$447,2,FALSE)","v":"AHU03E05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM122&\" \"&\"AT%Q\"&B123*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J122&\"*)\",\" \")","v":"LAHU03E05_WVC AT%Q144.0 :INT ; (*空调机组NJ-3AP(KT)5-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN122,SEARCH(\"AT%\",AN122),,REPT(\" \",25-SEARCH(\"AT%\",AN122))),SEARCH(\":\",REPLACE(AN122,SEARCH(\"AT%\",AN122),,REPT(\" \",25-SEARCH(\"AT%\",AN122)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN122,SEARCH(\"AT%\",AN122),,REPT(\" \",25-SEARCH(\"AT%\",AN122)))))),\" \")","v":"LAHU03E05_WVC           AT%Q144.0      :INT ; (*空调机组NJ-3AP(KT)5-5-水阀控制*)"},null,{"$f":"AM122","v":"AHU03E05_WVC"},{"$f":"J122","v":"空调机组NJ-3AP(KT)5-5-水阀控制"},{"$f":"40000+($B123*8+F122-1)","v":40072}]
[null,9,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH123&AA123&\"-\"&AK123","v":"空调机组NJ-3AP(KT)5-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI123=\"\",\"\",AI123)","v":"NJ-3AP(KT)5-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-6","03E06","水阀控制",{"$f":"AH123&\"-\"&AK123","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH123,List!$B$3:$D$445,2,FALSE)&AJ123&\"_\"&VLOOKUP(AK123,List!$K$2:$M$447,2,FALSE)","v":"AHU03E06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM123&\" \"&\"AT%Q\"&B123*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J123&\"*)\",\" \")","v":"LAHU03E06_WVC AT%Q146.0 :INT ; (*空调机组NJ-3AP(KT)5-6-水阀控制*)"},"LAHU03E06_WVC           AT%Q146.0      :INT ; (*空调机组NJ-3AP(KT)5-6-水阀控制*)",null,"AHU03E06_WVC",{"$f":"J123","v":"空调机组NJ-3AP(KT)5-6-水阀控制"},{"$f":"AS122+1","v":40073}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH124&AA124&\"-\"&AK124","v":"空调机组NJ-3AP(KT)5-7-水阀控制"},{"$nulls":16},"NJ-3AP(KT)5-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)5-7","03E07","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH124,List!$B$3:$D$445,2,FALSE)&AJ124&\"_\"&VLOOKUP(AK124,List!$K$2:$M$447,2,FALSE)","v":"AHU03E07_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM124&\" \"&\"AT%Q\"&B123*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J124&\"*)\",\" \")","v":"LAHU03E07_WVC AT%Q148.0 :INT ; (*空调机组NJ-3AP(KT)5-7-水阀控制*)"},"LAHU03E07_WVC           AT%Q148.0      :INT ; (*空调机组NJ-3AP(KT)5-7-水阀控制*)",null,"AHU03E07_WVC","空调机组NJ-3AP(KT)5-7-水阀控制",{"$f":"AS123+1","v":40074}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH125&AA125&\"-\"&AK125","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH125,List!$B$3:$D$445,2,FALSE)&AJ125&\"_\"&VLOOKUP(AK125,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM125&\" \"&\"AT%Q\"&B123*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J125&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40075]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L503","index":34,"n_rows":50,"n_cols":45,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[4,1,5,1],[11,1,22,1],[28,1,31,1],[37,1,40,1],[46,1,49,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L01",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R D7",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 10 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH8&AA8&\"-\"&AK8","v":"F新风机组NJ-5AP(KT)51-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-5AP(KT)51"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)51","05C01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"F新风机组-运行状态"},{"$f":"VLOOKUP(AH8,[1]List!$D$3:$F$527,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05C01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LFAU05C01_R AT%I160.0 :BOOL; (*F新风机组NJ-5AP(KT)51-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LFAU05C01_R             AT%I160.0      :BOOL; (*F新风机组NJ-5AP(KT)51-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L01\\L01FAU05C01_R"},{"$f":"J8","v":"F新风机组NJ-5AP(KT)51-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":11280}]
[null,10,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},2,null,2,"C","F新风机组NJ-5AP(KT)51-故障状态",{"$nulls":16},"NJ-5AP(KT)51",{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)51","05C01","故障状态","F新风机组-故障状态",{"$f":"VLOOKUP(AH9,[1]List!$D$3:$F$527,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05C01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LFAU05C01_F AT%I160.1 :BOOL; (*F新风机组NJ-5AP(KT)51-故障状态*)"},"LFAU05C01_F             AT%I160.1      :BOOL; (*F新风机组NJ-5AP(KT)51-故障状态*)",null,"L01\\L01FAU05C01_F","F新风机组NJ-5AP(KT)51-故障状态",{"$f":"AS8+1","v":11281}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},3,null,3,"C","F新风机组NJ-5AP(KT)51-自动状态",{"$nulls":16},"NJ-5AP(KT)51",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)51","05C01","自动状态","F新风机组-自动状态",{"$f":"VLOOKUP(AH10,[1]List!$D$3:$F$527,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05C01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LFAU05C01_A AT%I160.2 :BOOL; (*F新风机组NJ-5AP(KT)51-自动状态*)"},"LFAU05C01_A             AT%I160.2      :BOOL; (*F新风机组NJ-5AP(KT)51-自动状态*)",null,"L01\\L01FAU05C01_A","F新风机组NJ-5AP(KT)51-自动状态",11282]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},4,null,4,"C","F新风机组NJ-5AP(KT)51-风机压差",{"$nulls":16},"NJ-5AP(KT)51",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)51","05C01","风机压差","F新风机组-风机压差",{"$f":"VLOOKUP(AH11,[1]List!$D$3:$F$527,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05C01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LFAU05C01_FPS AT%I160.3 :BOOL; (*F新风机组NJ-5AP(KT)51-风机压差*)"},"LFAU05C01_FPS           AT%I160.3      :BOOL; (*F新风机组NJ-5AP(KT)51-风机压差*)",null,"L01\\L01FAU05C01_FPS","F新风机组NJ-5AP(KT)51-风机压差",11283]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,5,"C","F新风机组NJ-5AP(KT)51-初效滤网压差",{"$nulls":16},"NJ-5AP(KT)51",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)51","05C01","初效滤网压差","F新风机组-初效滤网压差",{"$f":"VLOOKUP(AH12,[1]List!$D$3:$F$527,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05C01_IPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LFAU05C01_IPS AT%I160.4 :BOOL; (*F新风机组NJ-5AP(KT)51-初效滤网压差*)"},"LFAU05C01_IPS           AT%I160.4      :BOOL; (*F新风机组NJ-5AP(KT)51-初效滤网压差*)",null,"L01\\L01FAU05C01_IPS","F新风机组NJ-5AP(KT)51-初效滤网压差",11284]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","F新风机组NJ-5AP(KT)51-低温断路开关",{"$nulls":16},"NJ-5AP(KT)51",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)51","05C01","低温断路开关","F新风机组-低温断路开关",{"$f":"VLOOKUP(AH13,[1]List!$D$3:$F$527,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05C01_AFS"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LFAU05C01_AFS AT%I160.5 :BOOL; (*F新风机组NJ-5AP(KT)51-低温断路开关*)"},"LFAU05C01_AFS           AT%I160.5      :BOOL; (*F新风机组NJ-5AP(KT)51-低温断路开关*)",null,"L01\\L01FAU05C01_AFS","F新风机组NJ-5AP(KT)51-低温断路开关",11285]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","F新风机组NJ-5AP(KT)51-新风阀开状态",{"$nulls":16},"NJ-5AP(KT)51",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)51","05C01","新风阀开状态","F新风机组-新风阀开状态",{"$f":"VLOOKUP(AH14,[1]List!$D$3:$F$527,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05C01_FDOB"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LFAU05C01_FDOB AT%I160.6 :BOOL; (*F新风机组NJ-5AP(KT)51-新风阀开状态*)"},"LFAU05C01_FDOB          AT%I160.6      :BOOL; (*F新风机组NJ-5AP(KT)51-新风阀开状态*)",null,"L01\\L01FAU05C01_FDOB","F新风机组NJ-5AP(KT)51-新风阀开状态",11286]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","F新风机组NJ-5AP(KT)51-新风阀关状态",{"$nulls":16},"NJ-5AP(KT)51",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)51","05C01","新风阀关状态","F新风机组-新风阀关状态",{"$f":"VLOOKUP(AH15,[1]List!$D$3:$F$527,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05C01_FDSB"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LFAU05C01_FDSB AT%I160.7 :BOOL; (*F新风机组NJ-5AP(KT)51-新风阀关状态*)"},"LFAU05C01_FDSB          AT%I160.7      :BOOL; (*F新风机组NJ-5AP(KT)51-新风阀关状态*)",null,"L01\\L01FAU05C01_FDSB","F新风机组NJ-5AP(KT)51-新风阀关状态",11287]
[{"$nulls":5},9,null,9,"C","消防水箱-高液位",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"消防水箱",null,"05C01","高液位","消防水箱-高液位",{"$f":"VLOOKUP(AH16,[1]List!$D$3:$F$527,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,[1]List!$I$2:$K$529,2,FALSE)","v":"SWT05C01_HL"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LSWT05C01_HL AT%I161.0 :BOOL; (*消防水箱-高液位*)"},"LSWT05C01_HL            AT%I161.0      :BOOL; (*消防水箱-高液位*)",null,"L01\\L01SWT05C01_HL","消防水箱-高液位",11288]
[{"$nulls":5},10,null,10,"C","消防水箱-低液位",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"消防水箱",null,"05C01","低液位","消防水箱-低液位",{"$f":"VLOOKUP(AH17,[1]List!$D$3:$F$527,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,[1]List!$I$2:$K$529,2,FALSE)","v":"SWT05C01_LL"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LSWT05C01_LL AT%I161.1 :BOOL; (*消防水箱-低液位*)"},"LSWT05C01_LL            AT%I161.1      :BOOL; (*消防水箱-低液位*)",null,"L01\\L01SWT05C01_LL","消防水箱-低液位",11289]
[{"$nulls":5},11,null,11,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH18,[1]List!$D$3:$F$527,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN18,SEARCH(\"AT%\",AN18),,REPT(\" \",30-SEARCH(\"AT%\",AN18))),SEARCH(\":\",REPLACE(AN18,SEARCH(\"AT%\",AN18),,REPT(\" \",30-SEARCH(\"AT%\",AN18)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN18,SEARCH(\"AT%\",AN18),,REPT(\" \",25-SEARCH(\"AT%\",AN18)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",11290]
[{"$nulls":5},12,null,12,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH19,[1]List!$D$3:$F$527,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11291]
[{"$nulls":5},13,null,13,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH20,[1]List!$D$3:$F$527,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11292]
[{"$nulls":5},14,null,14,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH21,[1]List!$D$3:$F$527,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11293]
[{"$nulls":5},15,null,15,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH22,[1]List!$D$3:$F$527,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11294]
[".",{"$nulls":4},16,null,16,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH23,[1]List!$D$3:$F$527,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11295]
[null,{"$f":"B29","v":"IOM 0801D"},{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 0801D地址: 11 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH25&AA25&\"-\"&AK25","v":"F新风机组NJ-5AP(KT)51-启停控制"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-5AP(KT)51"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)51","05C01","启停控制",{"$f":"AH25&\"-\"&AK25","v":"F新风机组-启停控制"},{"$f":"VLOOKUP(AH25,[1]List!$D$3:$F$527,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05C01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%Q\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LFAU05C01_C AT%Q176.0 :BOOL; (*F新风机组NJ-5AP(KT)51-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LFAU05C01_C             AT%Q176.0      :BOOL; (*F新风机组NJ-5AP(KT)51-启停控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L01\\L01FAU05C01_C"},{"$f":"J25","v":"F新风机组NJ-5AP(KT)51-启停控制"},{"$f":"($B26*16*8+F25-1)","v":1408}]
[null,11,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","F新风机组NJ-5AP(KT)51-新风阀开控制",{"$nulls":16},"NJ-5AP(KT)51",{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)51","05C01","新风阀开控制","F新风机组-新风阀开控制",{"$f":"VLOOKUP(AH26,[1]List!$D$3:$F$527,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05C01_FDOC"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%Q\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LFAU05C01_FDOC AT%Q176.1 :BOOL; (*F新风机组NJ-5AP(KT)51-新风阀开控制*)"},"LFAU05C01_FDOC          AT%Q176.1      :BOOL; (*F新风机组NJ-5AP(KT)51-新风阀开控制*)",null,"L01\\L01FAU05C01_FDOC","F新风机组NJ-5AP(KT)51-新风阀开控制",{"$f":"AS25+1","v":1409}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","F新风机组NJ-5AP(KT)51-新风阀关控制",{"$nulls":16},"NJ-5AP(KT)51",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)51","05C01","新风阀关控制","F新风机组-新风阀关控制",{"$f":"VLOOKUP(AH27,[1]List!$D$3:$F$527,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05C01_FDSC"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%Q\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LFAU05C01_FDSC AT%Q176.2 :BOOL; (*F新风机组NJ-5AP(KT)51-新风阀关控制*)"},"LFAU05C01_FDSC          AT%Q176.2      :BOOL; (*F新风机组NJ-5AP(KT)51-新风阀关控制*)",null,"L01\\L01FAU05C01_FDSC","F新风机组NJ-5AP(KT)51-新风阀关控制",1410]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH28,[1]List!$D$3:$F$527,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%Q\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN28,SEARCH(\"AT%\",AN28),,REPT(\" \",30-SEARCH(\"AT%\",AN28))),SEARCH(\":\",REPLACE(AN28,SEARCH(\"AT%\",AN28),,REPT(\" \",30-SEARCH(\"AT%\",AN28)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN28,SEARCH(\"AT%\",AN28),,REPT(\" \",25-SEARCH(\"AT%\",AN28)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",1411]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH29,[1]List!$D$3:$F$527,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%Q\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1412]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH30,[1]List!$D$3:$F$527,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%Q\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1413]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH31,[1]List!$D$3:$F$527,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%Q\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1414]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH32,[1]List!$D$3:$F$527,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%Q\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1415]
[null,{"$f":"B38","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B38&\"地址: \"&B35&\" *)\"","v":"(* IOM 0801U地址: 12 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH34&AA34&\"-\"&AK34","v":"F新风机组NJ-5AP(KT)51-送风温度"},{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-5AP(KT)51"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,[2]List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,[2]List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"F新风机组","NJ-5AP(KT)51","05C01","送风温度",{"$f":"AH34&\"-\"&AK34","v":"F新风机组-送风温度"},{"$f":"VLOOKUP(AH34,[2]List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,[2]List!$K$2:$M$447,2,FALSE)","v":"FAU05C01_ST"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B35*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LFAU05C01_ST AT%I192.0 :INT ; (*F新风机组NJ-5AP(KT)51-送风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34))),SEARCH(\":\",REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34)))))),\" \")","v":"LFAU05C01_ST            AT%I192.0      :INT ; (*F新风机组NJ-5AP(KT)51-送风温度*)"},null,{"$f":"AM34","v":"FAU05C01_ST"},{"$f":"J34","v":"F新风机组NJ-5AP(KT)51-送风温度"},{"$f":"30000+($B35*8+F34-1)","v":30096}]
[null,12,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),4,1))","v":0},2,null,2,"0V","F新风机组NJ-5AP(KT)51-水阀反馈",{"$nulls":16},"NJ-5AP(KT)51",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[2]List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[2]List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"F新风机组","NJ-5AP(KT)51","05C01","水阀反馈","F新风机组-水阀反馈",{"$f":"VLOOKUP(AH35,[2]List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,[2]List!$K$2:$M$447,2,FALSE)","v":"FAU05C01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B35*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LFAU05C01_WVB AT%I194.0 :INT ; (*F新风机组NJ-5AP(KT)51-水阀反馈*)"},"LFAU05C01_WVB           AT%I194.0      :INT ; (*F新风机组NJ-5AP(KT)51-水阀反馈*)",null,"FAU05C01_WVB","F新风机组NJ-5AP(KT)51-水阀反馈",{"$f":"AS34+1","v":30097}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),3,1))","v":1},3,null,3,"0V","F新风机组NJ-5AP(KT)51-变频器频率反馈",{"$nulls":16},"NJ-5AP(KT)51",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[2]List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[2]List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",null,null,"F新风机组","NJ-5AP(KT)51","05C01","变频器频率反馈","F新风机组-变频器频率反馈",{"$f":"VLOOKUP(AH36,[2]List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,[2]List!$K$2:$M$447,2,FALSE)","v":"FAU05C01_VFB"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B35*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LFAU05C01_VFB AT%I196.0 :INT ; (*F新风机组NJ-5AP(KT)51-变频器频率反馈*)"},"LFAU05C01_VFB           AT%I196.0      :INT ; (*F新风机组NJ-5AP(KT)51-变频器频率反馈*)",null,"FAU05C01_VFB","F新风机组NJ-5AP(KT)51-变频器频率反馈",30098]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),2,1))","v":1},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[2]List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[2]List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH37,[2]List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,[2]List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B35*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30099]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),1,1))","v":0},5,null,5,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[2]List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[2]List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH38,[2]List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,[2]List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B35*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30100]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,[2]List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,[2]List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH39,[2]List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,[2]List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B35*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30101]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,[2]List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,[2]List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH40,[2]List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,[2]List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B35*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30102]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,[2]List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,[2]List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"不通过",{"$nulls":6},"-",{"$f":"VLOOKUP(AH41,[2]List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,[2]List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%I\"&B35*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30103]
[null,{"$f":"B47","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 0401A地址: 13 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH43&AA43&\"-\"&AK43","v":"F新风机组NJ-5AP(KT)51-水阀控制"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-5AP(KT)51"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)51","05C01","水阀控制",{"$f":"AH43&\"-\"&AK43","v":"F新风机组-水阀控制"},{"$f":"VLOOKUP(AH43,[1]List!$D$3:$F$527,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05C01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%Q\"&B44*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LFAU05C01_WVC AT%Q208.0 :INT; (*F新风机组NJ-5AP(KT)51-水阀控制*)"},"LFAU05C01_WVC           AT%Q208.0      :INT; (*F新风机组NJ-5AP(KT)51-水阀控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM43","v":"L01\\L01FAU05C01_WVC"},{"$f":"J43","v":"F新风机组NJ-5AP(KT)51-水阀控制"},{"$f":"40000+($B44*8+F43-1)","v":40104}]
[null,13,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":0},2,null,3,4,"F新风机组NJ-5AP(KT)51-变频器频率控制",{"$nulls":16},"NJ-5AP(KT)51",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)51","05C01","变频器频率控制","F新风机组-变频器频率控制",{"$f":"VLOOKUP(AH44,[1]List!$D$3:$F$527,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05C01_VFC"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%Q\"&B44*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LFAU05C01_VFC AT%Q210.0 :INT; (*F新风机组NJ-5AP(KT)51-变频器频率控制*)"},"LFAU05C01_VFC           AT%Q210.0      :INT; (*F新风机组NJ-5AP(KT)51-变频器频率控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM44","v":"L01\\L01FAU05C01_VFC"},"F新风机组NJ-5AP(KT)51-变频器频率控制",{"$f":"AS43+1","v":40105}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":1},3,null,5,6,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH45,[1]List!$D$3:$F$527,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%Q\"&B44*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM45","v":{"$error":"#N/A"}},"-",40106]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":1},4,null,7,8,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH46,[1]List!$D$3:$F$527,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%Q\"&B44*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN46,SEARCH(\"AT%\",AN46),,REPT(\" \",30-SEARCH(\"AT%\",AN46))),SEARCH(\":\",REPLACE(AN46,SEARCH(\"AT%\",AN46),,REPT(\" \",30-SEARCH(\"AT%\",AN46)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN46,SEARCH(\"AT%\",AN46),,REPT(\" \",25-SEARCH(\"AT%\",AN46)))))),\" \")","v":" "},null,{"$f":"$B$2&\"\\\"&$B$2&AM46","v":{"$error":"#N/A"}},"-",40107]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L504","index":35,"n_rows":42,"n_cols":45,"rows_kept":42,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[41,5,41,6],[41,9,41,25],[4,1,5,1],[11,1,14,1],[20,1,23,1],[29,1,32,1],[38,1,41,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L01",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.0801R D7",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 0801R地址: 14 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH8&AA8&\"-\"&AK8","v":"F新风机组NJ-5AP(KT)52-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-5AP(KT)52"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)52","05D01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"F新风机组-运行状态"},{"$f":"VLOOKUP(AH8,[1]List!$D$3:$F$527,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05D01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LFAU05D01_R AT%I224.0 :BOOL; (*F新风机组NJ-5AP(KT)52-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LFAU05D01_R             AT%I224.0      :BOOL; (*F新风机组NJ-5AP(KT)52-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L01\\L01FAU05D01_R"},{"$f":"J8","v":"F新风机组NJ-5AP(KT)52-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":11792}]
[null,14,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},2,null,2,"C","F新风机组NJ-5AP(KT)52-故障状态",{"$nulls":16},"NJ-5AP(KT)52",{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)52","05D01","故障状态","F新风机组-故障状态",{"$f":"VLOOKUP(AH9,[1]List!$D$3:$F$527,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05D01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LFAU05D01_F AT%I224.1 :BOOL; (*F新风机组NJ-5AP(KT)52-故障状态*)"},"LFAU05D01_F             AT%I224.1      :BOOL; (*F新风机组NJ-5AP(KT)52-故障状态*)",null,"L01\\L01FAU05D01_F","F新风机组NJ-5AP(KT)52-故障状态",{"$f":"AS8+1","v":11793}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},3,null,3,"C","F新风机组NJ-5AP(KT)52-自动状态",{"$nulls":16},"NJ-5AP(KT)52",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)52","05D01","自动状态","F新风机组-自动状态",{"$f":"VLOOKUP(AH10,[1]List!$D$3:$F$527,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05D01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LFAU05D01_A AT%I224.2 :BOOL; (*F新风机组NJ-5AP(KT)52-自动状态*)"},"LFAU05D01_A             AT%I224.2      :BOOL; (*F新风机组NJ-5AP(KT)52-自动状态*)",null,"L01\\L01FAU05D01_A","F新风机组NJ-5AP(KT)52-自动状态",11794]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},4,null,4,"C","F新风机组NJ-5AP(KT)52-风机压差",{"$nulls":16},"NJ-5AP(KT)52",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)52","05D01","风机压差","F新风机组-风机压差",{"$f":"VLOOKUP(AH11,[1]List!$D$3:$F$527,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05D01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LFAU05D01_FPS AT%I224.3 :BOOL; (*F新风机组NJ-5AP(KT)52-风机压差*)"},"LFAU05D01_FPS           AT%I224.3      :BOOL; (*F新风机组NJ-5AP(KT)52-风机压差*)",null,"L01\\L01FAU05D01_FPS","F新风机组NJ-5AP(KT)52-风机压差",11795]
[null,"IOM 0801R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,5,"C","F新风机组NJ-5AP(KT)52-初效滤网压差",{"$nulls":16},"NJ-5AP(KT)52",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)52","05D01","初效滤网压差","F新风机组-初效滤网压差",{"$f":"VLOOKUP(AH12,[1]List!$D$3:$F$527,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05D01_IPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LFAU05D01_IPS AT%I224.4 :BOOL; (*F新风机组NJ-5AP(KT)52-初效滤网压差*)"},"LFAU05D01_IPS           AT%I224.4      :BOOL; (*F新风机组NJ-5AP(KT)52-初效滤网压差*)",null,"L01\\L01FAU05D01_IPS","F新风机组NJ-5AP(KT)52-初效滤网压差",11796]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","F新风机组NJ-5AP(KT)52-低温断路开关",{"$nulls":16},"NJ-5AP(KT)52",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)52","05D01","低温断路开关","F新风机组-低温断路开关",{"$f":"VLOOKUP(AH13,[1]List!$D$3:$F$527,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05D01_AFS"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LFAU05D01_AFS AT%I224.5 :BOOL; (*F新风机组NJ-5AP(KT)52-低温断路开关*)"},"LFAU05D01_AFS           AT%I224.5      :BOOL; (*F新风机组NJ-5AP(KT)52-低温断路开关*)",null,"L01\\L01FAU05D01_AFS","F新风机组NJ-5AP(KT)52-低温断路开关",11797]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","F新风机组NJ-5AP(KT)52-新风阀开状态",{"$nulls":16},"NJ-5AP(KT)52",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)52","05D01","新风阀开状态","F新风机组-新风阀开状态",{"$f":"VLOOKUP(AH14,[1]List!$D$3:$F$527,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05D01_FDOB"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LFAU05D01_FDOB AT%I224.6 :BOOL; (*F新风机组NJ-5AP(KT)52-新风阀开状态*)"},"LFAU05D01_FDOB          AT%I224.6      :BOOL; (*F新风机组NJ-5AP(KT)52-新风阀开状态*)",null,"L01\\L01FAU05D01_FDOB","F新风机组NJ-5AP(KT)52-新风阀开状态",11798]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","F新风机组NJ-5AP(KT)52-新风阀关状态",{"$nulls":16},"NJ-5AP(KT)52",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)52","05D01","新风阀关状态","F新风机组-新风阀关状态",{"$f":"VLOOKUP(AH15,[1]List!$D$3:$F$527,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05D01_FDSB"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LFAU05D01_FDSB AT%I224.7 :BOOL; (*F新风机组NJ-5AP(KT)52-新风阀关状态*)"},"LFAU05D01_FDSB          AT%I224.7      :BOOL; (*F新风机组NJ-5AP(KT)52-新风阀关状态*)",null,"L01\\L01FAU05D01_FDSB","F新风机组NJ-5AP(KT)52-新风阀关状态",11799]
[null,{"$f":"B21","v":"IOM 0801D"},{"$nulls":38},{"$f":"\"(* \"&B21&\"地址: \"&B18&\" *)\"","v":"(* IOM 0801D地址: 15 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH17&AA17&\"-\"&AK17","v":"F新风机组NJ-5AP(KT)52-启停控制"},{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-5AP(KT)52"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)52","05D01","启停控制",{"$f":"AH17&\"-\"&AK17","v":"F新风机组-启停控制"},{"$f":"VLOOKUP(AH17,[1]List!$D$3:$F$527,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05D01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%Q\"&B18*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LFAU05D01_C AT%Q240.0 :BOOL; (*F新风机组NJ-5AP(KT)52-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",25-SEARCH(\"AT%\",AN17))),SEARCH(\":\",REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",25-SEARCH(\"AT%\",AN17)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",25-SEARCH(\"AT%\",AN17)))))),\" \")","v":"LFAU05D01_C             AT%Q240.0      :BOOL; (*F新风机组NJ-5AP(KT)52-启停控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM17","v":"L01\\L01FAU05D01_C"},{"$f":"J17","v":"F新风机组NJ-5AP(KT)52-启停控制"},{"$f":"($B18*16*8+F17-1)","v":1920}]
[null,15,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","F新风机组NJ-5AP(KT)52-新风阀开控制",{"$nulls":16},"NJ-5AP(KT)52",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)52","05D01","新风阀开控制","F新风机组-新风阀开控制",{"$f":"VLOOKUP(AH18,[1]List!$D$3:$F$527,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05D01_FDOC"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%Q\"&B18*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LFAU05D01_FDOC AT%Q240.1 :BOOL; (*F新风机组NJ-5AP(KT)52-新风阀开控制*)"},"LFAU05D01_FDOC          AT%Q240.1      :BOOL; (*F新风机组NJ-5AP(KT)52-新风阀开控制*)",null,"L01\\L01FAU05D01_FDOC","F新风机组NJ-5AP(KT)52-新风阀开控制",{"$f":"AS17+1","v":1921}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","F新风机组NJ-5AP(KT)52-新风阀关控制",{"$nulls":16},"NJ-5AP(KT)52",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)52","05D01","新风阀关控制","F新风机组-新风阀关控制",{"$f":"VLOOKUP(AH19,[1]List!$D$3:$F$527,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05D01_FDSC"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%Q\"&B18*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LFAU05D01_FDSC AT%Q240.2 :BOOL; (*F新风机组NJ-5AP(KT)52-新风阀关控制*)"},"LFAU05D01_FDSC          AT%Q240.2      :BOOL; (*F新风机组NJ-5AP(KT)52-新风阀关控制*)",null,"L01\\L01FAU05D01_FDSC","F新风机组NJ-5AP(KT)52-新风阀关控制",1922]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH20,[1]List!$D$3:$F$527,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%Q\"&B18*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN20,SEARCH(\"AT%\",AN20),,REPT(\" \",30-SEARCH(\"AT%\",AN20))),SEARCH(\":\",REPLACE(AN20,SEARCH(\"AT%\",AN20),,REPT(\" \",30-SEARCH(\"AT%\",AN20)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN20,SEARCH(\"AT%\",AN20),,REPT(\" \",25-SEARCH(\"AT%\",AN20)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",1923]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH21,[1]List!$D$3:$F$527,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%Q\"&B18*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1924]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH22,[1]List!$D$3:$F$527,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%Q\"&B18*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1925]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH23,[1]List!$D$3:$F$527,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%Q\"&B18*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1926]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH24,[1]List!$D$3:$F$527,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%Q\"&B18*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1927]
[null,{"$f":"B30","v":"IOM 0401U E5"},{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 0401U E5地址: 16 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH26&AA26&\"-\"&AK26","v":"F新风机组NJ-5AP(KT)52-送风温度"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-5AP(KT)52"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)52","05D01","送风温度",{"$f":"AH26&\"-\"&AK26","v":"F新风机组-送风温度"},{"$f":"VLOOKUP(AH26,[1]List!$D$3:$F$527,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05D01_ST"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LFAU05D01_ST AT%I256.0 :INT; (*F新风机组NJ-5AP(KT)52-送风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LFAU05D01_ST            AT%I256.0      :INT; (*F新风机组NJ-5AP(KT)52-送风温度*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L01\\L01FAU05D01_ST"},{"$f":"J26","v":"F新风机组NJ-5AP(KT)52-送风温度"},{"$f":"30000+($B27*8+F26-1)","v":30128}]
[null,16,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,2,"0V","F新风机组NJ-5AP(KT)52-水阀反馈",{"$nulls":16},"NJ-5AP(KT)52",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)52","05D01","水阀反馈","F新风机组-水阀反馈",{"$f":"VLOOKUP(AH27,[1]List!$D$3:$F$527,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05D01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LFAU05D01_WVB AT%I258.0 :INT; (*F新风机组NJ-5AP(KT)52-水阀反馈*)"},"LFAU05D01_WVB           AT%I258.0      :INT; (*F新风机组NJ-5AP(KT)52-水阀反馈*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM27","v":"L01\\L01FAU05D01_WVB"},"F新风机组NJ-5AP(KT)52-水阀反馈",{"$f":"AS26+1","v":30129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,3,"0V","F新风机组NJ-5AP(KT)52-变频器频率反馈",{"$nulls":16},"NJ-5AP(KT)52",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)52","05D01","变频器频率反馈","F新风机组-变频器频率反馈",{"$f":"VLOOKUP(AH28,[1]List!$D$3:$F$527,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05D01_VFB"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LFAU05D01_VFB AT%I260.0 :INT; (*F新风机组NJ-5AP(KT)52-变频器频率反馈*)"},"LFAU05D01_VFB           AT%I260.0      :INT; (*F新风机组NJ-5AP(KT)52-变频器频率反馈*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM28","v":"L01\\L01FAU05D01_VFB"},"F新风机组NJ-5AP(KT)52-变频器频率反馈",30130]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH29,[1]List!$D$3:$F$527,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM29","v":{"$error":"#N/A"}},"-",30131]
[null,"IOM 0401U E5",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":1}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B39","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B39&\"地址: \"&B36&\" *)\"","v":"(* IOM 0401A地址: 17 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH35&AA35&\"-\"&AK35","v":"F新风机组NJ-5AP(KT)52-水阀控制"},{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-5AP(KT)52"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)52","05D01","水阀控制",{"$f":"AH35&\"-\"&AK35","v":"F新风机组-水阀控制"},{"$f":"VLOOKUP(AH35,[1]List!$D$3:$F$527,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05D01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%Q\"&B36*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LFAU05D01_WVC AT%Q272.0 :INT; (*F新风机组NJ-5AP(KT)52-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35))),SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35)))))),\" \")","v":"LFAU05D01_WVC           AT%Q272.0      :INT; (*F新风机组NJ-5AP(KT)52-水阀控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM35","v":"L01\\L01FAU05D01_WVC"},{"$f":"J35","v":"F新风机组NJ-5AP(KT)52-水阀控制"},{"$f":"40000+($B36*8+F35-1)","v":40136}]
[null,17,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":0},2,null,3,4,"F新风机组NJ-5AP(KT)52-变频器频率控制",{"$nulls":16},"NJ-5AP(KT)52",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)52","05D01","变频器频率控制","F新风机组-变频器频率控制",{"$f":"VLOOKUP(AH36,[1]List!$D$3:$F$527,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05D01_VFC"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%Q\"&B36*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LFAU05D01_VFC AT%Q274.0 :INT; (*F新风机组NJ-5AP(KT)52-变频器频率控制*)"},"LFAU05D01_VFC           AT%Q274.0      :INT; (*F新风机组NJ-5AP(KT)52-变频器频率控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM36","v":"L01\\L01FAU05D01_VFC"},"F新风机组NJ-5AP(KT)52-变频器频率控制",{"$f":"AS35+1","v":40137}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":0},3,null,5,6,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH37,[1]List!$D$3:$F$527,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%Q\"&B36*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM37","v":{"$error":"#N/A"}},"-",40138]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":0},4,null,7,8,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH38,[1]List!$D$3:$F$527,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%Q\"&B36*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN38,SEARCH(\"AT%\",AN38),,REPT(\" \",30-SEARCH(\"AT%\",AN38))),SEARCH(\":\",REPLACE(AN38,SEARCH(\"AT%\",AN38),,REPT(\" \",30-SEARCH(\"AT%\",AN38)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN38,SEARCH(\"AT%\",AN38),,REPT(\" \",25-SEARCH(\"AT%\",AN38)))))),\" \")","v":" "},null,{"$f":"$B$2&\"\\\"&$B$2&AM38","v":{"$error":"#N/A"}},"-",40139]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L306","index":36,"n_rows":129,"n_cols":45,"rows_kept":129,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[6,1,6,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[75,5,75,6],[75,9,75,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[92,5,92,6],[92,9,92,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[101,5,101,6],[101,9,101,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[109,5,109,6],[109,9,109,25],[110,5,110,6],[110,9,110,25],[112,5,112,6],[112,9,112,25],[113,5,113,6],[113,9,113,25],[114,5,114,6],[114,9,114,25],[115,5,115,6],[115,9,115,25],[116,5,116,6],[116,9,116,25],[117,5,117,6],[117,9,117,25],[118,5,118,6],[118,9,118,25],[119,5,119,6],[119,9,119,25],[121,5,121,6],[121,9,121,25],[122,5,122,6],[122,9,122,25],[123,5,123,6],[123,9,123,25],[124,5,124,6],[124,9,124,25],[125,5,125,6],[125,9,125,25],[126,5,126,6],[126,9,126,25],[127,5,127,6],[127,9,127,25],[128,5,128,6],[128,9,128,25],[4,1,5,1],[12,1,23,1],[29,1,40,1],[46,1,57,1],[63,1,66,1],[72,1,83,1],[89,1,92,1],[98,1,101,1],[107,1,110,1],[116,1,119,1],[125,1,128,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[16,2,23,4],[33,2,40,4],[50,2,57,4],[76,2,83,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L24",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"EXC-1000"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B13&\"地址: \"&B10&\" *)\"","v":"(* IOM 1601R地址: 0 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH9&AA9&\"-\"&AK9","v":"空调机组NJ-3AP(KT)6-1-运行状态"},{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-3AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-1","03F01","运行状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU03F01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B10*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU03F01_R AT%I0.0 :BOOL; (*空调机组NJ-3AP(KT)6-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9))),SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))))),\" \")","v":"LAHU03F01_R             AT%I0.0        :BOOL; (*空调机组NJ-3AP(KT)6-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM9","v":"L24\\L24AHU03F01_R"},{"$f":"J9","v":"空调机组NJ-3AP(KT)6-1-运行状态"},{"$f":"10000+($B10*16*8+F9-1)","v":10000}]
[null,0,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-3AP(KT)6-1-故障状态",{"$nulls":16},{"$f":"IF(AI10=\"\",\"\",AI10)","v":"NJ-3AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-1","03F01","故障状态",{"$f":"AH10&\"-\"&AK10","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU03F01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B10*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU03F01_F AT%I0.1 :BOOL; (*空调机组NJ-3AP(KT)6-1-故障状态*)"},"LAHU03F01_F             AT%I0.1        :BOOL; (*空调机组NJ-3AP(KT)6-1-故障状态*)",null,"L24\\L24AHU03F01_F",{"$f":"J10","v":"空调机组NJ-3AP(KT)6-1-故障状态"},{"$f":"AS9+1","v":10001}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)6-1-自动状态",{"$nulls":16},"NJ-3AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-1","03F01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU03F01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B10*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU03F01_A AT%I0.2 :BOOL; (*空调机组NJ-3AP(KT)6-1-自动状态*)"},"LAHU03F01_A             AT%I0.2        :BOOL; (*空调机组NJ-3AP(KT)6-1-自动状态*)",null,"L24\\L24AHU03F01_A","空调机组NJ-3AP(KT)6-1-自动状态",{"$f":"AS10+1","v":10002}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)6-1-风机压差",{"$nulls":16},"NJ-3AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-1","03F01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU03F01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B10*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU03F01_FPS AT%I0.3 :BOOL; (*空调机组NJ-3AP(KT)6-1-风机压差*)"},"LAHU03F01_FPS           AT%I0.3        :BOOL; (*空调机组NJ-3AP(KT)6-1-风机压差*)",null,"L24\\L24AHU03F01_FPS","空调机组NJ-3AP(KT)6-1-风机压差",10003]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)6-2-运行状态",{"$nulls":16},"NJ-3AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-2","03F02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU03F02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B10*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU03F02_R AT%I0.4 :BOOL; (*空调机组NJ-3AP(KT)6-2-运行状态*)"},"LAHU03F02_R             AT%I0.4        :BOOL; (*空调机组NJ-3AP(KT)6-2-运行状态*)",null,"L24\\L24AHU03F02_R","空调机组NJ-3AP(KT)6-2-运行状态",10004]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)6-2-故障状态",{"$nulls":16},"NJ-3AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-2","03F02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU03F02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B10*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU03F02_F AT%I0.5 :BOOL; (*空调机组NJ-3AP(KT)6-2-故障状态*)"},"LAHU03F02_F             AT%I0.5        :BOOL; (*空调机组NJ-3AP(KT)6-2-故障状态*)",null,"L24\\L24AHU03F02_F","空调机组NJ-3AP(KT)6-2-故障状态",10005]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)6-2-自动状态",{"$nulls":16},"NJ-3AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-2","03F02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU03F02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B10*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU03F02_A AT%I0.6 :BOOL; (*空调机组NJ-3AP(KT)6-2-自动状态*)"},"LAHU03F02_A             AT%I0.6        :BOOL; (*空调机组NJ-3AP(KT)6-2-自动状态*)",null,"L24\\L24AHU03F02_A","空调机组NJ-3AP(KT)6-2-自动状态",10006]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)6-2-风机压差",{"$nulls":16},"NJ-3AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-2","03F02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU03F02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B10*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU03F02_FPS AT%I0.7 :BOOL; (*空调机组NJ-3AP(KT)6-2-风机压差*)"},"LAHU03F02_FPS           AT%I0.7        :BOOL; (*空调机组NJ-3AP(KT)6-2-风机压差*)",null,"L24\\L24AHU03F02_FPS","空调机组NJ-3AP(KT)6-2-风机压差",10007]
[{"$nulls":5},9,null,17,18,"空调机组NJ-3AP(KT)6-3-运行状态",{"$nulls":16},"NJ-3AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-3","03F03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU03F03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B10*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU03F03_R AT%I1.0 :BOOL; (*空调机组NJ-3AP(KT)6-3-运行状态*)"},"LAHU03F03_R             AT%I1.0        :BOOL; (*空调机组NJ-3AP(KT)6-3-运行状态*)",null,"L24\\L24AHU03F03_R","空调机组NJ-3AP(KT)6-3-运行状态",10008]
[{"$nulls":5},10,null,19,20,"空调机组NJ-3AP(KT)6-3-故障状态",{"$nulls":16},{"$f":"IF(AI18=\"\",\"\",AI18)","v":"NJ-3AP(KT)6-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-3","03F03","故障状态",{"$f":"AH18&\"-\"&AK18","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU03F03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B10*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU03F03_F AT%I1.1 :BOOL; (*空调机组NJ-3AP(KT)6-3-故障状态*)"},"LAHU03F03_F             AT%I1.1        :BOOL; (*空调机组NJ-3AP(KT)6-3-故障状态*)",null,"L24\\L24AHU03F03_F","空调机组NJ-3AP(KT)6-3-故障状态",10009]
[{"$nulls":5},11,null,21,22,"空调机组NJ-3AP(KT)6-3-自动状态",{"$nulls":16},"NJ-3AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-3","03F03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU03F03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B10*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU03F03_A AT%I1.2 :BOOL; (*空调机组NJ-3AP(KT)6-3-自动状态*)"},"LAHU03F03_A             AT%I1.2        :BOOL; (*空调机组NJ-3AP(KT)6-3-自动状态*)",null,"L24\\L24AHU03F03_A","空调机组NJ-3AP(KT)6-3-自动状态",10010]
[{"$nulls":5},12,null,23,24,"空调机组NJ-3AP(KT)6-3-风机压差",{"$nulls":16},"NJ-3AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-3","03F03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU03F03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B10*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU03F03_FPS AT%I1.3 :BOOL; (*空调机组NJ-3AP(KT)6-3-风机压差*)"},"LAHU03F03_FPS           AT%I1.3        :BOOL; (*空调机组NJ-3AP(KT)6-3-风机压差*)",null,"L24\\L24AHU03F03_FPS","空调机组NJ-3AP(KT)6-3-风机压差",10011]
[{"$nulls":5},13,null,25,26,"空调机组NJ-3AP(KT)6-4-运行状态",{"$nulls":16},"NJ-3AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-4","03F04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU03F04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B10*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU03F04_R AT%I1.4 :BOOL; (*空调机组NJ-3AP(KT)6-4-运行状态*)"},"LAHU03F04_R             AT%I1.4        :BOOL; (*空调机组NJ-3AP(KT)6-4-运行状态*)",null,"L24\\L24AHU03F04_R","空调机组NJ-3AP(KT)6-4-运行状态",10012]
[{"$nulls":5},14,null,27,28,"空调机组NJ-3AP(KT)6-4-故障状态",{"$nulls":16},"NJ-3AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-4","03F04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU03F04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B10*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU03F04_F AT%I1.5 :BOOL; (*空调机组NJ-3AP(KT)6-4-故障状态*)"},"LAHU03F04_F             AT%I1.5        :BOOL; (*空调机组NJ-3AP(KT)6-4-故障状态*)",null,"L24\\L24AHU03F04_F","空调机组NJ-3AP(KT)6-4-故障状态",10013]
[{"$nulls":5},15,null,29,30,"空调机组NJ-3AP(KT)6-4-自动状态",{"$nulls":16},"NJ-3AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-4","03F04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU03F04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B10*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU03F04_A AT%I1.6 :BOOL; (*空调机组NJ-3AP(KT)6-4-自动状态*)"},"LAHU03F04_A             AT%I1.6        :BOOL; (*空调机组NJ-3AP(KT)6-4-自动状态*)",null,"L24\\L24AHU03F04_A","空调机组NJ-3AP(KT)6-4-自动状态",10014]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-3AP(KT)6-4-风机压差",{"$nulls":16},"NJ-3AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-4","03F04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH24,List!$B$3:$D$445,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,List!$K$2:$M$447,2,FALSE)","v":"AHU03F04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%I\"&B10*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":"LAHU03F04_FPS AT%I1.7 :BOOL; (*空调机组NJ-3AP(KT)6-4-风机压差*)"},"LAHU03F04_FPS           AT%I1.7        :BOOL; (*空调机组NJ-3AP(KT)6-4-风机压差*)",null,"L24\\L24AHU03F04_FPS","空调机组NJ-3AP(KT)6-4-风机压差",10015]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 1601R地址: 1 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH26&AA26&\"-\"&AK26","v":"空调机组NJ-3AP(KT)6-5-运行状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-3AP(KT)6-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-5","03F05","运行状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU03F05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU03F05_R AT%I16.0 :BOOL; (*空调机组NJ-3AP(KT)6-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LAHU03F05_R             AT%I16.0       :BOOL; (*空调机组NJ-3AP(KT)6-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L24\\L24AHU03F05_R"},{"$f":"J26","v":"空调机组NJ-3AP(KT)6-5-运行状态"},{"$f":"10000+($B27*16*8+F26-1)","v":10128}]
[null,1,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-3AP(KT)6-5-故障状态",{"$nulls":16},{"$f":"IF(AI27=\"\",\"\",AI27)","v":"NJ-3AP(KT)6-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-5","03F05","故障状态",{"$f":"AH27&\"-\"&AK27","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU03F05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU03F05_F AT%I16.1 :BOOL; (*空调机组NJ-3AP(KT)6-5-故障状态*)"},"LAHU03F05_F             AT%I16.1       :BOOL; (*空调机组NJ-3AP(KT)6-5-故障状态*)",null,"L24\\L24AHU03F05_F",{"$f":"J27","v":"空调机组NJ-3AP(KT)6-5-故障状态"},{"$f":"AS26+1","v":10129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)6-5-自动状态",{"$nulls":16},"NJ-3AP(KT)6-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-5","03F05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU03F05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU03F05_A AT%I16.2 :BOOL; (*空调机组NJ-3AP(KT)6-5-自动状态*)"},"LAHU03F05_A             AT%I16.2       :BOOL; (*空调机组NJ-3AP(KT)6-5-自动状态*)",null,"L24\\L24AHU03F05_A","空调机组NJ-3AP(KT)6-5-自动状态",{"$f":"AS27+1","v":10130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)6-5-风机压差",{"$nulls":16},"NJ-3AP(KT)6-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-5","03F05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU03F05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU03F05_FPS AT%I16.3 :BOOL; (*空调机组NJ-3AP(KT)6-5-风机压差*)"},"LAHU03F05_FPS           AT%I16.3       :BOOL; (*空调机组NJ-3AP(KT)6-5-风机压差*)",null,"L24\\L24AHU03F05_FPS","空调机组NJ-3AP(KT)6-5-风机压差",10131]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)6-6-运行状态",{"$nulls":16},"NJ-3AP(KT)6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-6","03F06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU03F06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B27*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU03F06_R AT%I16.4 :BOOL; (*空调机组NJ-3AP(KT)6-6-运行状态*)"},"LAHU03F06_R             AT%I16.4       :BOOL; (*空调机组NJ-3AP(KT)6-6-运行状态*)",null,"L24\\L24AHU03F06_R","空调机组NJ-3AP(KT)6-6-运行状态",10132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)6-6-故障状态",{"$nulls":16},"NJ-3AP(KT)6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-6","03F06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU03F06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B27*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU03F06_F AT%I16.5 :BOOL; (*空调机组NJ-3AP(KT)6-6-故障状态*)"},"LAHU03F06_F             AT%I16.5       :BOOL; (*空调机组NJ-3AP(KT)6-6-故障状态*)",null,"L24\\L24AHU03F06_F","空调机组NJ-3AP(KT)6-6-故障状态",10133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)6-6-自动状态",{"$nulls":16},"NJ-3AP(KT)6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-6","03F06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU03F06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B27*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU03F06_A AT%I16.6 :BOOL; (*空调机组NJ-3AP(KT)6-6-自动状态*)"},"LAHU03F06_A             AT%I16.6       :BOOL; (*空调机组NJ-3AP(KT)6-6-自动状态*)",null,"L24\\L24AHU03F06_A","空调机组NJ-3AP(KT)6-6-自动状态",10134]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)6-6-风机压差",{"$nulls":16},"NJ-3AP(KT)6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-6","03F06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU03F06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B27*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU03F06_FPS AT%I16.7 :BOOL; (*空调机组NJ-3AP(KT)6-6-风机压差*)"},"LAHU03F06_FPS           AT%I16.7       :BOOL; (*空调机组NJ-3AP(KT)6-6-风机压差*)",null,"L24\\L24AHU03F06_FPS","空调机组NJ-3AP(KT)6-6-风机压差",10135]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-3AL6-1-运行状态",{"$nulls":16},"NJ-3AL6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-1","03F01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"LCB03F01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B27*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LLCB03F01_R AT%I17.0 :BOOL; (*照明控制箱NJ-3AL6-1-运行状态*)"},"LLCB03F01_R             AT%I17.0       :BOOL; (*照明控制箱NJ-3AL6-1-运行状态*)",null,"L24\\L24LCB03F01_R","照明控制箱NJ-3AL6-1-运行状态",10136]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-3AL6-1-自动状态",{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-3AL6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-1","03F01","自动状态",{"$f":"AH35&\"-\"&AK35","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"LCB03F01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B27*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LLCB03F01_A AT%I17.1 :BOOL; (*照明控制箱NJ-3AL6-1-自动状态*)"},"LLCB03F01_A             AT%I17.1       :BOOL; (*照明控制箱NJ-3AL6-1-自动状态*)",null,"L24\\L24LCB03F01_A",{"$f":"J35","v":"照明控制箱NJ-3AL6-1-自动状态"},10137]
[{"$nulls":5},11,null,21,22,"照明控制箱NJ-3AL6-2-运行状态",{"$nulls":16},"NJ-3AL6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-2","03F02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"LCB03F02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B27*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LLCB03F02_R AT%I17.2 :BOOL; (*照明控制箱NJ-3AL6-2-运行状态*)"},"LLCB03F02_R             AT%I17.2       :BOOL; (*照明控制箱NJ-3AL6-2-运行状态*)",null,"L24\\L24LCB03F02_R","照明控制箱NJ-3AL6-2-运行状态",10138]
[{"$nulls":5},12,null,23,24,"照明控制箱NJ-3AL6-2-自动状态",{"$nulls":16},"NJ-3AL6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-2","03F02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"LCB03F02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B27*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LLCB03F02_A AT%I17.3 :BOOL; (*照明控制箱NJ-3AL6-2-自动状态*)"},"LLCB03F02_A             AT%I17.3       :BOOL; (*照明控制箱NJ-3AL6-2-自动状态*)",null,"L24\\L24LCB03F02_A","照明控制箱NJ-3AL6-2-自动状态",10139]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-3AL6-3-运行状态",{"$nulls":16},"NJ-3AL6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-3","03F03","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB03F03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B27*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB03F03_R AT%I17.4 :BOOL; (*照明控制箱NJ-3AL6-3-运行状态*)"},"LLCB03F03_R             AT%I17.4       :BOOL; (*照明控制箱NJ-3AL6-3-运行状态*)",null,"L24\\L24LCB03F03_R","照明控制箱NJ-3AL6-3-运行状态",10140]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-3AL6-3-自动状态",{"$nulls":16},"NJ-3AL6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-3","03F03","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB03F03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B27*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB03F03_A AT%I17.5 :BOOL; (*照明控制箱NJ-3AL6-3-自动状态*)"},"LLCB03F03_A             AT%I17.5       :BOOL; (*照明控制箱NJ-3AL6-3-自动状态*)",null,"L24\\L24LCB03F03_A","照明控制箱NJ-3AL6-3-自动状态",10141]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-3AL6-4-运行状态",{"$nulls":16},"NJ-3AL6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-4","03F04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"LCB03F04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B27*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LLCB03F04_R AT%I17.6 :BOOL; (*照明控制箱NJ-3AL6-4-运行状态*)"},"LLCB03F04_R             AT%I17.6       :BOOL; (*照明控制箱NJ-3AL6-4-运行状态*)",null,"L24\\L24LCB03F04_R","照明控制箱NJ-3AL6-4-运行状态",10142]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-3AL6-4-自动状态",{"$nulls":16},"NJ-3AL6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-4","03F04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":"LCB03F04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%I\"&B27*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":"LLCB03F04_A AT%I17.7 :BOOL; (*照明控制箱NJ-3AL6-4-自动状态*)"},"LLCB03F04_A             AT%I17.7       :BOOL; (*照明控制箱NJ-3AL6-4-自动状态*)",null,"L24\\L24LCB03F04_A","照明控制箱NJ-3AL6-4-自动状态",10143]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 1601R地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH43&AA43&\"-\"&AK43","v":"照明控制箱NJ-3AL6-5-运行状态"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-3AL6-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-5","03F05","运行状态",{"$f":"AH43&\"-\"&AK43","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"LCB03F05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B44*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LLCB03F05_R AT%I32.0 :BOOL; (*照明控制箱NJ-3AL6-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LLCB03F05_R             AT%I32.0       :BOOL; (*照明控制箱NJ-3AL6-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM43","v":"L24\\L24LCB03F05_R"},{"$f":"J43","v":"照明控制箱NJ-3AL6-5-运行状态"},{"$f":"10000+($B44*16*8+F43-1)","v":10256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},2,null,3,4,"照明控制箱NJ-3AL6-5-自动状态",{"$nulls":16},{"$f":"IF(AI44=\"\",\"\",AI44)","v":"NJ-3AL6-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-5","03F05","自动状态",{"$f":"AH44&\"-\"&AK44","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"LCB03F05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B44*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LLCB03F05_A AT%I32.1 :BOOL; (*照明控制箱NJ-3AL6-5-自动状态*)"},"LLCB03F05_A             AT%I32.1       :BOOL; (*照明控制箱NJ-3AL6-5-自动状态*)",null,"L24\\L24LCB03F05_A",{"$f":"J44","v":"照明控制箱NJ-3AL6-5-自动状态"},{"$f":"AS43+1","v":10257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,5,6,"照明控制箱NJ-3AL6-6-运行状态",{"$nulls":16},"NJ-3AL6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-6","03F06","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"LCB03F06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B44*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LLCB03F06_R AT%I32.2 :BOOL; (*照明控制箱NJ-3AL6-6-运行状态*)"},"LLCB03F06_R             AT%I32.2       :BOOL; (*照明控制箱NJ-3AL6-6-运行状态*)",null,"L24\\L24LCB03F06_R","照明控制箱NJ-3AL6-6-运行状态",{"$f":"AS44+1","v":10258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},4,null,7,8,"照明控制箱NJ-3AL6-6-自动状态",{"$nulls":16},"NJ-3AL6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-6","03F06","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"LCB03F06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B44*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LLCB03F06_A AT%I32.3 :BOOL; (*照明控制箱NJ-3AL6-6-自动状态*)"},"LLCB03F06_A             AT%I32.3       :BOOL; (*照明控制箱NJ-3AL6-6-自动状态*)",null,"L24\\L24LCB03F06_A","照明控制箱NJ-3AL6-6-自动状态",10259]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-3AL6-7-运行状态",{"$nulls":16},"NJ-3AL6-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-7","03F07","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"LCB03F07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B44*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LLCB03F07_R AT%I32.4 :BOOL; (*照明控制箱NJ-3AL6-7-运行状态*)"},"LLCB03F07_R             AT%I32.4       :BOOL; (*照明控制箱NJ-3AL6-7-运行状态*)",null,"L24\\L24LCB03F07_R","照明控制箱NJ-3AL6-7-运行状态",10260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-3AL6-7-自动状态",{"$nulls":16},"NJ-3AL6-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-7","03F07","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"LCB03F07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B44*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LLCB03F07_A AT%I32.5 :BOOL; (*照明控制箱NJ-3AL6-7-自动状态*)"},"LLCB03F07_A             AT%I32.5       :BOOL; (*照明控制箱NJ-3AL6-7-自动状态*)",null,"L24\\L24LCB03F07_A","照明控制箱NJ-3AL6-7-自动状态",10261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"照明控制箱NJ-3AL(GG)6-1-运行状态",{"$nulls":16},"NJ-3AL(GG)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)6-1","03F08","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"LCB03F08_R"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B44*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LLCB03F08_R AT%I32.6 :BOOL; (*照明控制箱NJ-3AL(GG)6-1-运行状态*)"},"LLCB03F08_R             AT%I32.6       :BOOL; (*照明控制箱NJ-3AL(GG)6-1-运行状态*)",null,"L24\\L24LCB03F08_R","照明控制箱NJ-3AL(GG)6-1-运行状态",10262]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"照明控制箱NJ-3AL(GG)6-1-自动状态",{"$nulls":16},"NJ-3AL(GG)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)6-1","03F08","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"LCB03F08_A"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B44*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LLCB03F08_A AT%I32.7 :BOOL; (*照明控制箱NJ-3AL(GG)6-1-自动状态*)"},"LLCB03F08_A             AT%I32.7       :BOOL; (*照明控制箱NJ-3AL(GG)6-1-自动状态*)",null,"L24\\L24LCB03F08_A","照明控制箱NJ-3AL(GG)6-1-自动状态",10263]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-3AL(GG)6-2-运行状态",{"$nulls":16},"NJ-3AL(GG)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)6-2","03F09","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"LCB03F09_R"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B44*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LLCB03F09_R AT%I33.0 :BOOL; (*照明控制箱NJ-3AL(GG)6-2-运行状态*)"},"LLCB03F09_R             AT%I33.0       :BOOL; (*照明控制箱NJ-3AL(GG)6-2-运行状态*)",null,"L24\\L24LCB03F09_R","照明控制箱NJ-3AL(GG)6-2-运行状态",10264]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-3AL(GG)6-2-自动状态",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-3AL(GG)6-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)6-2","03F09","自动状态",{"$f":"AH52&\"-\"&AK52","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"LCB03F09_A"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%I\"&B44*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LLCB03F09_A AT%I33.1 :BOOL; (*照明控制箱NJ-3AL(GG)6-2-自动状态*)"},"LLCB03F09_A             AT%I33.1       :BOOL; (*照明控制箱NJ-3AL(GG)6-2-自动状态*)",null,"L24\\L24LCB03F09_A",{"$f":"J52","v":"照明控制箱NJ-3AL(GG)6-2-自动状态"},10265]
[{"$nulls":5},11,null,21,22,"照明控制箱NJ-3AL(GG)6-3-运行状态",{"$nulls":16},"NJ-3AL(GG)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)6-3","03F10","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"LCB03F10_R"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%I\"&B44*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LLCB03F10_R AT%I33.2 :BOOL; (*照明控制箱NJ-3AL(GG)6-3-运行状态*)"},"LLCB03F10_R             AT%I33.2       :BOOL; (*照明控制箱NJ-3AL(GG)6-3-运行状态*)",null,"L24\\L24LCB03F10_R","照明控制箱NJ-3AL(GG)6-3-运行状态",10266]
[{"$nulls":5},12,null,23,24,"照明控制箱NJ-3AL(GG)6-3-自动状态",{"$nulls":16},"NJ-3AL(GG)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)6-3","03F10","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"LCB03F10_A"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%I\"&B44*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LLCB03F10_A AT%I33.3 :BOOL; (*照明控制箱NJ-3AL(GG)6-3-自动状态*)"},"LLCB03F10_A             AT%I33.3       :BOOL; (*照明控制箱NJ-3AL(GG)6-3-自动状态*)",null,"L24\\L24LCB03F10_A","照明控制箱NJ-3AL(GG)6-3-自动状态",10267]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-3AL(GG)6-4-运行状态",{"$nulls":16},"NJ-3AL(GG)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)6-4","03F11","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"LCB03F11_R"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%I\"&B44*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LLCB03F11_R AT%I33.4 :BOOL; (*照明控制箱NJ-3AL(GG)6-4-运行状态*)"},"LLCB03F11_R             AT%I33.4       :BOOL; (*照明控制箱NJ-3AL(GG)6-4-运行状态*)",null,"L24\\L24LCB03F11_R","照明控制箱NJ-3AL(GG)6-4-运行状态",10268]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-3AL(GG)6-4-自动状态",{"$nulls":16},"NJ-3AL(GG)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)6-4","03F11","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"LCB03F11_A"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%I\"&B44*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LLCB03F11_A AT%I33.5 :BOOL; (*照明控制箱NJ-3AL(GG)6-4-自动状态*)"},"LLCB03F11_A             AT%I33.5       :BOOL; (*照明控制箱NJ-3AL(GG)6-4-自动状态*)",null,"L24\\L24LCB03F11_A","照明控制箱NJ-3AL(GG)6-4-自动状态",10269]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-3AL(GG)6-5-运行状态",{"$nulls":16},"NJ-3AL(GG)6-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)6-5","03F12","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"LCB03F12_R"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%I\"&B44*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LLCB03F12_R AT%I33.6 :BOOL; (*照明控制箱NJ-3AL(GG)6-5-运行状态*)"},"LLCB03F12_R             AT%I33.6       :BOOL; (*照明控制箱NJ-3AL(GG)6-5-运行状态*)",null,"L24\\L24LCB03F12_R","照明控制箱NJ-3AL(GG)6-5-运行状态",10270]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-3AL(GG)6-5-自动状态",{"$nulls":16},"NJ-3AL(GG)6-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)6-5","03F12","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":"LCB03F12_A"},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%I\"&B44*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":"LLCB03F12_A AT%I33.7 :BOOL; (*照明控制箱NJ-3AL(GG)6-5-自动状态*)"},"LLCB03F12_A             AT%I33.7       :BOOL; (*照明控制箱NJ-3AL(GG)6-5-自动状态*)",null,"L24\\L24LCB03F12_A","照明控制箱NJ-3AL(GG)6-5-自动状态",10271]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B64&\"地址: \"&B61&\" *)\"","v":"(* IOM 0801R 地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},1,null,1,"C",{"$f":"AH60&AA60&\"-\"&AK60","v":"风机盘管NJ-3AL(GG)6-1-运行状态"},{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-3AL(GG)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-3AL(GG)6-1","03F01","运行状态",{"$f":"AH60&\"-\"&AK60","v":"风机盘管-运行状态"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"FCU03F01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%I\"&B61*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LFCU03F01_R AT%I48.0 :BOOL; (*风机盘管NJ-3AL(GG)6-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60))),SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))))),\" \")","v":"LFCU03F01_R             AT%I48.0       :BOOL; (*风机盘管NJ-3AL(GG)6-1-运行状态*)"},null,{"$f":"AM60","v":"FCU03F01_R"},{"$f":"J60","v":"风机盘管NJ-3AL(GG)6-1-运行状态"},{"$f":"10000+($B61*16*8+F60-1)","v":10384}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},2,null,2,"C",{"$f":"AH61&AA61&\"-\"&AK61","v":"风机盘管NJ-3AL(GG)6-1-自动状态"},{"$nulls":16},{"$f":"IF(AI61=\"\",\"\",AI61)","v":"NJ-3AL(GG)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-3AL(GG)6-1","03F01","自动状态",{"$f":"AH61&\"-\"&AK61","v":"风机盘管-自动状态"},{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"FCU03F01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%I\"&B61*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LFCU03F01_A AT%I48.1 :BOOL; (*风机盘管NJ-3AL(GG)6-1-自动状态*)"},"LFCU03F01_A             AT%I48.1       :BOOL; (*风机盘管NJ-3AL(GG)6-1-自动状态*)",null,{"$f":"AM61","v":"FCU03F01_A"},{"$f":"J61","v":"风机盘管NJ-3AL(GG)6-1-自动状态"},{"$f":"AS60+1","v":10385}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},3,null,3,"C",{"$f":"AH62&AA62&\"-\"&AK62","v":"风机盘管NJ-3AL(GG)6-1-电磁阀开启状态"},{"$nulls":16},"NJ-3AL(GG)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-3AL(GG)6-1","03F01","电磁阀开启状态","风机盘管-电磁阀开启状态",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"FCU03F01_EVR"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B61*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LFCU03F01_EVR AT%I48.2 :BOOL; (*风机盘管NJ-3AL(GG)6-1-电磁阀开启状态*)"},"LFCU03F01_EVR           AT%I48.2       :BOOL; (*风机盘管NJ-3AL(GG)6-1-电磁阀开启状态*)",null,"FCU03F01_EVR","风机盘管NJ-3AL(GG)6-1-电磁阀开启状态",{"$f":"AS61+1","v":10386}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},4,null,4,"C",{"$f":"AH63&AA63&\"-\"&AK63","v":"风机盘管NJ-3AL(GG)6-1-电磁阀自动状态"},{"$nulls":16},"NJ-3AL(GG)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-3AL(GG)6-1","03F01","电磁阀自动状态","风机盘管-电磁阀自动状态",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"FCU03F01_EVA"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B61*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LFCU03F01_EVA AT%I48.3 :BOOL; (*风机盘管NJ-3AL(GG)6-1-电磁阀自动状态*)"},"LFCU03F01_EVA           AT%I48.3       :BOOL; (*风机盘管NJ-3AL(GG)6-1-电磁阀自动状态*)",null,"FCU03F01_EVA","风机盘管NJ-3AL(GG)6-1-电磁阀自动状态",10387]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},5,null,5,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B61*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10388]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B61*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10389]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B61*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10390]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%I\"&B61*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10391]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B73&\"地址: \"&B70&\" *)\"","v":"(* IOM 1601D地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH69&AA69&\"-\"&AK69","v":"空调机组NJ-3AP(KT)6-1-启停控制"},{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-3AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-1","03F01","启停控制",{"$f":"AH69&\"-\"&AK69","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU03F01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%Q\"&B70*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU03F01_C AT%Q64.0 :BOOL; (*空调机组NJ-3AP(KT)6-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69))),SEARCH(\":\",REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69)))))),\" \")","v":"LAHU03F01_C             AT%Q64.0       :BOOL; (*空调机组NJ-3AP(KT)6-1-启停控制*)"},null,{"$f":"AM69","v":"AHU03F01_C"},{"$f":"J69","v":"空调机组NJ-3AP(KT)6-1-启停控制"},{"$f":"($B70*16*8+F69-1)","v":512}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","空调机组NJ-3AP(KT)6-2-启停控制",{"$nulls":16},{"$f":"IF(AI70=\"\",\"\",AI70)","v":"NJ-3AP(KT)6-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-2","03F02","启停控制",{"$f":"AH70&\"-\"&AK70","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"AHU03F02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%Q\"&B70*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LAHU03F02_C AT%Q64.1 :BOOL; (*空调机组NJ-3AP(KT)6-2-启停控制*)"},"LAHU03F02_C             AT%Q64.1       :BOOL; (*空调机组NJ-3AP(KT)6-2-启停控制*)",null,"AHU03F02_C",{"$f":"J70","v":"空调机组NJ-3AP(KT)6-2-启停控制"},{"$f":"AS69+1","v":513}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-3AP(KT)6-3-启停控制",{"$nulls":16},"NJ-3AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-3","03F03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"AHU03F03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%Q\"&B70*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LAHU03F03_C AT%Q64.2 :BOOL; (*空调机组NJ-3AP(KT)6-3-启停控制*)"},"LAHU03F03_C             AT%Q64.2       :BOOL; (*空调机组NJ-3AP(KT)6-3-启停控制*)",null,"AHU03F03_C","空调机组NJ-3AP(KT)6-3-启停控制",{"$f":"AS70+1","v":514}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","空调机组NJ-3AP(KT)6-4-启停控制",{"$nulls":16},"NJ-3AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-4","03F04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"AHU03F04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%Q\"&B70*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LAHU03F04_C AT%Q64.3 :BOOL; (*空调机组NJ-3AP(KT)6-4-启停控制*)"},"LAHU03F04_C             AT%Q64.3       :BOOL; (*空调机组NJ-3AP(KT)6-4-启停控制*)",null,"AHU03F04_C","空调机组NJ-3AP(KT)6-4-启停控制",515]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-3AP(KT)6-5-启停控制",{"$nulls":16},"NJ-3AP(KT)6-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-5","03F05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"AHU03F05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%Q\"&B70*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LAHU03F05_C AT%Q64.4 :BOOL; (*空调机组NJ-3AP(KT)6-5-启停控制*)"},"LAHU03F05_C             AT%Q64.4       :BOOL; (*空调机组NJ-3AP(KT)6-5-启停控制*)",null,"AHU03F05_C","空调机组NJ-3AP(KT)6-5-启停控制",516]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-3AP(KT)6-6-启停控制",{"$nulls":16},"NJ-3AP(KT)6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-6","03F06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":"AHU03F06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%Q\"&B70*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":"LAHU03F06_C AT%Q64.5 :BOOL; (*空调机组NJ-3AP(KT)6-6-启停控制*)"},"LAHU03F06_C             AT%Q64.5       :BOOL; (*空调机组NJ-3AP(KT)6-6-启停控制*)",null,"AHU03F06_C","空调机组NJ-3AP(KT)6-6-启停控制",517]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","照明控制箱NJ-3AL6-1-启停控制",{"$nulls":16},"NJ-3AL6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-1","03F01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":"LCB03F01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%Q\"&B70*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":"LLCB03F01_C AT%Q64.6 :BOOL; (*照明控制箱NJ-3AL6-1-启停控制*)"},"LLCB03F01_C             AT%Q64.6       :BOOL; (*照明控制箱NJ-3AL6-1-启停控制*)",null,"LCB03F01_C","照明控制箱NJ-3AL6-1-启停控制",518]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-3AL6-2-启停控制",{"$nulls":16},"NJ-3AL6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-2","03F02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH76,List!$B$3:$D$445,2,FALSE)&AJ76&\"_\"&VLOOKUP(AK76,List!$K$2:$M$447,2,FALSE)","v":"LCB03F02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM76&\" \"&\"AT%Q\"&B70*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J76&\"*)\",\" \")","v":"LLCB03F02_C AT%Q64.7 :BOOL; (*照明控制箱NJ-3AL6-2-启停控制*)"},"LLCB03F02_C             AT%Q64.7       :BOOL; (*照明控制箱NJ-3AL6-2-启停控制*)",null,"LCB03F02_C","照明控制箱NJ-3AL6-2-启停控制",519]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-3AL6-3-启停控制",{"$nulls":16},"NJ-3AL6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-3","03F03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"LCB03F03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%Q\"&B70*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LLCB03F03_C AT%Q65.0 :BOOL; (*照明控制箱NJ-3AL6-3-启停控制*)"},"LLCB03F03_C             AT%Q65.0       :BOOL; (*照明控制箱NJ-3AL6-3-启停控制*)",null,"LCB03F03_C","照明控制箱NJ-3AL6-3-启停控制",520]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-3AL6-4-启停控制",{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-3AL6-4"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-4","03F04","启停控制",{"$f":"AH78&\"-\"&AK78","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"LCB03F04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B70*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LLCB03F04_C AT%Q65.1 :BOOL; (*照明控制箱NJ-3AL6-4-启停控制*)"},"LLCB03F04_C             AT%Q65.1       :BOOL; (*照明控制箱NJ-3AL6-4-启停控制*)",null,"LCB03F04_C",{"$f":"J78","v":"照明控制箱NJ-3AL6-4-启停控制"},521]
[{"$nulls":5},11,null,"11+","11-","照明控制箱NJ-3AL6-5-启停控制",{"$nulls":16},"NJ-3AL6-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-5","03F05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"LCB03F05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B70*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LLCB03F05_C AT%Q65.2 :BOOL; (*照明控制箱NJ-3AL6-5-启停控制*)"},"LLCB03F05_C             AT%Q65.2       :BOOL; (*照明控制箱NJ-3AL6-5-启停控制*)",null,"LCB03F05_C","照明控制箱NJ-3AL6-5-启停控制",522]
[{"$nulls":5},12,null,"12+","12-","照明控制箱NJ-3AL6-6-启停控制",{"$nulls":16},"NJ-3AL6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-6","03F06","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"LCB03F06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B70*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LLCB03F06_C AT%Q65.3 :BOOL; (*照明控制箱NJ-3AL6-6-启停控制*)"},"LLCB03F06_C             AT%Q65.3       :BOOL; (*照明控制箱NJ-3AL6-6-启停控制*)",null,"LCB03F06_C","照明控制箱NJ-3AL6-6-启停控制",523]
[{"$nulls":5},13,null,"13+","13-","照明控制箱NJ-3AL6-7-启停控制",{"$nulls":16},"NJ-3AL6-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL6-7","03F07","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"LCB03F07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%Q\"&B70*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LLCB03F07_C AT%Q65.4 :BOOL; (*照明控制箱NJ-3AL6-7-启停控制*)"},"LLCB03F07_C             AT%Q65.4       :BOOL; (*照明控制箱NJ-3AL6-7-启停控制*)",null,"LCB03F07_C","照明控制箱NJ-3AL6-7-启停控制",524]
[{"$nulls":5},14,null,"14+","14-","照明控制箱NJ-3AL(GG)6-1-启停控制",{"$nulls":16},"NJ-3AL(GG)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)6-1","03F08","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":"LCB03F08_C"},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%Q\"&B70*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":"LLCB03F08_C AT%Q65.5 :BOOL; (*照明控制箱NJ-3AL(GG)6-1-启停控制*)"},"LLCB03F08_C             AT%Q65.5       :BOOL; (*照明控制箱NJ-3AL(GG)6-1-启停控制*)",null,"LCB03F08_C","照明控制箱NJ-3AL(GG)6-1-启停控制",525]
[{"$nulls":5},15,null,"15+","15-","照明控制箱NJ-3AL(GG)6-2-启停控制",{"$nulls":16},"NJ-3AL(GG)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)6-2","03F09","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":"LCB03F09_C"},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%Q\"&B70*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":"LLCB03F09_C AT%Q65.6 :BOOL; (*照明控制箱NJ-3AL(GG)6-2-启停控制*)"},"LLCB03F09_C             AT%Q65.6       :BOOL; (*照明控制箱NJ-3AL(GG)6-2-启停控制*)",null,"LCB03F09_C","照明控制箱NJ-3AL(GG)6-2-启停控制",526]
[".",{"$nulls":4},16,null,"16+","16-","照明控制箱NJ-3AL(GG)6-3-启停控制",{"$nulls":16},"NJ-3AL(GG)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)6-3","03F10","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH84,List!$B$3:$D$445,2,FALSE)&AJ84&\"_\"&VLOOKUP(AK84,List!$K$2:$M$447,2,FALSE)","v":"LCB03F10_C"},{"$f":"_xlfn.IFNA(\"L\"&AM84&\" \"&\"AT%Q\"&B70*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J84&\"*)\",\" \")","v":"LLCB03F10_C AT%Q65.7 :BOOL; (*照明控制箱NJ-3AL(GG)6-3-启停控制*)"},"LLCB03F10_C             AT%Q65.7       :BOOL; (*照明控制箱NJ-3AL(GG)6-3-启停控制*)",null,"LCB03F10_C","照明控制箱NJ-3AL(GG)6-3-启停控制",527]
[null,"IOM 0801D",{"$nulls":38},{"$f":"\"(* \"&B90&\"地址: \"&B87&\" *)\"","v":"(* IOM 0801D地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH86&AA86&\"-\"&AK86","v":"照明控制箱NJ-3AL(GG)6-4-启停控制"},{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-3AL(GG)6-4"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)6-4","03F11","启停控制",{"$f":"AH86&\"-\"&AK86","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"LCB03F11_C"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%Q\"&B87*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LLCB03F11_C AT%Q80.0 :BOOL; (*照明控制箱NJ-3AL(GG)6-4-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86))),SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))))),\" \")","v":"LLCB03F11_C             AT%Q80.0       :BOOL; (*照明控制箱NJ-3AL(GG)6-4-启停控制*)"},null,{"$f":"AM86","v":"LCB03F11_C"},{"$f":"J86","v":"照明控制箱NJ-3AL(GG)6-4-启停控制"},{"$f":"($B87*16*8+F86-1)","v":640}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","照明控制箱NJ-3AL(GG)6-5-启停控制",{"$nulls":16},{"$f":"IF(AI87=\"\",\"\",AI87)","v":"NJ-3AL(GG)6-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL(GG)6-5","03F12","启停控制",{"$f":"AH87&\"-\"&AK87","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"LCB03F12_C"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%Q\"&B87*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LLCB03F12_C AT%Q80.1 :BOOL; (*照明控制箱NJ-3AL(GG)6-5-启停控制*)"},"LLCB03F12_C             AT%Q80.1       :BOOL; (*照明控制箱NJ-3AL(GG)6-5-启停控制*)",null,"LCB03F12_C",{"$f":"J87","v":"照明控制箱NJ-3AL(GG)6-5-启停控制"},{"$f":"AS86+1","v":641}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","风机盘管NJ-3AL(GG)6-1-启停控制",{"$nulls":16},"NJ-3AL(GG)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-3AL(GG)6-1","03F01","启停控制","风机盘管-启停控制",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"FCU03F01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%Q\"&B87*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LFCU03F01_C AT%Q80.2 :BOOL; (*风机盘管NJ-3AL(GG)6-1-启停控制*)"},"LFCU03F01_C             AT%Q80.2       :BOOL; (*风机盘管NJ-3AL(GG)6-1-启停控制*)",null,"FCU03F01_C","风机盘管NJ-3AL(GG)6-1-启停控制",{"$f":"AS87+1","v":642}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","风机盘管NJ-3AL(GG)6-1-电磁阀开关控制",{"$nulls":16},"NJ-3AL(GG)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-3AL(GG)6-1","03F01","电磁阀开关控制","风机盘管-电磁阀开关控制",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"FCU03F01_EVC"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%Q\"&B87*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LFCU03F01_EVC AT%Q80.3 :BOOL; (*风机盘管NJ-3AL(GG)6-1-电磁阀开关控制*)"},"LFCU03F01_EVC           AT%Q80.3       :BOOL; (*风机盘管NJ-3AL(GG)6-1-电磁阀开关控制*)",null,"FCU03F01_EVC","风机盘管NJ-3AL(GG)6-1-电磁阀开关控制",643]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%Q\"&B87*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",644]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH91,List!$B$3:$D$445,2,FALSE)&AJ91&\"_\"&VLOOKUP(AK91,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM91&\" \"&\"AT%Q\"&B87*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J91&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",645]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH92,List!$B$3:$D$445,2,FALSE)&AJ92&\"_\"&VLOOKUP(AK92,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM92&\" \"&\"AT%Q\"&B87*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J92&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",646]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL93,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL93,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH93,List!$B$3:$D$445,2,FALSE)&AJ93&\"_\"&VLOOKUP(AK93,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM93&\" \"&\"AT%Q\"&B87*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J93&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",647]
[null,{"$f":"B99","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B99&\"地址: \"&B96&\" *)\"","v":"(* IOM 0801U地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH95&AA95&\"-\"&AK95","v":"空调机组NJ-3AP(KT)6-1-回风温度"},{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-3AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-1","03F01","回风温度",{"$f":"AH95&\"-\"&AK95","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"AHU03F01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%I\"&B96*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LAHU03F01_RT AT%I96.0 :INT ; (*空调机组NJ-3AP(KT)6-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95))),SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))))),\" \")","v":"LAHU03F01_RT            AT%I96.0       :INT ; (*空调机组NJ-3AP(KT)6-1-回风温度*)"},null,{"$f":"AM95","v":"AHU03F01_RT"},{"$f":"J95","v":"空调机组NJ-3AP(KT)6-1-回风温度"},{"$f":"30000+($B96*8+F95-1)","v":30048}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-3AP(KT)6-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI96=\"\",\"\",AI96)","v":"NJ-3AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-1","03F01","水阀反馈",{"$f":"AH96&\"-\"&AK96","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"AHU03F01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%I\"&B96*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LAHU03F01_WVB AT%I98.0 :INT ; (*空调机组NJ-3AP(KT)6-1-水阀反馈*)"},"LAHU03F01_WVB           AT%I98.0       :INT ; (*空调机组NJ-3AP(KT)6-1-水阀反馈*)",null,"AHU03F01_WVB",{"$f":"J96","v":"空调机组NJ-3AP(KT)6-1-水阀反馈"},{"$f":"AS95+1","v":30049}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)6-2-回风温度",{"$nulls":16},"NJ-3AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-2","03F02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":"AHU03F02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%I\"&B96*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":"LAHU03F02_RT AT%I100.0 :INT ; (*空调机组NJ-3AP(KT)6-2-回风温度*)"},"LAHU03F02_RT            AT%I100.0      :INT ; (*空调机组NJ-3AP(KT)6-2-回风温度*)",null,"AHU03F02_RT","空调机组NJ-3AP(KT)6-2-回风温度",{"$f":"AS96+1","v":30050}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-3AP(KT)6-2-水阀反馈",{"$nulls":16},"NJ-3AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-2","03F02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":"AHU03F02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%I\"&B96*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":"LAHU03F02_WVB AT%I102.0 :INT ; (*空调机组NJ-3AP(KT)6-2-水阀反馈*)"},"LAHU03F02_WVB           AT%I102.0      :INT ; (*空调机组NJ-3AP(KT)6-2-水阀反馈*)",null,"AHU03F02_WVB","空调机组NJ-3AP(KT)6-2-水阀反馈",30051]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-3AP(KT)6-3-回风温度",{"$nulls":16},"NJ-3AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-3","03F03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH99,List!$B$3:$D$445,2,FALSE)&AJ99&\"_\"&VLOOKUP(AK99,List!$K$2:$M$447,2,FALSE)","v":"AHU03F03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM99&\" \"&\"AT%I\"&B96*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J99&\"*)\",\" \")","v":"LAHU03F03_RT AT%I104.0 :INT ; (*空调机组NJ-3AP(KT)6-3-回风温度*)"},"LAHU03F03_RT            AT%I104.0      :INT ; (*空调机组NJ-3AP(KT)6-3-回风温度*)",null,"AHU03F03_RT","空调机组NJ-3AP(KT)6-3-回风温度",30052]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-3AP(KT)6-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI100=\"\",\"\",AI100)","v":"NJ-3AP(KT)6-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-3","03F03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH100,List!$B$3:$D$445,2,FALSE)&AJ100&\"_\"&VLOOKUP(AK100,List!$K$2:$M$447,2,FALSE)","v":"AHU03F03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM100&\" \"&\"AT%I\"&B96*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J100&\"*)\",\" \")","v":"LAHU03F03_WVB AT%I106.0 :INT ; (*空调机组NJ-3AP(KT)6-3-水阀反馈*)"},"LAHU03F03_WVB           AT%I106.0      :INT ; (*空调机组NJ-3AP(KT)6-3-水阀反馈*)",null,"AHU03F03_WVB",{"$f":"J100","v":"空调机组NJ-3AP(KT)6-3-水阀反馈"},30053]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-3AP(KT)6-4-回风温度",{"$nulls":16},"NJ-3AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-4","03F04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH101,List!$B$3:$D$445,2,FALSE)&AJ101&\"_\"&VLOOKUP(AK101,List!$K$2:$M$447,2,FALSE)","v":"AHU03F04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM101&\" \"&\"AT%I\"&B96*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J101&\"*)\",\" \")","v":"LAHU03F04_RT AT%I108.0 :INT ; (*空调机组NJ-3AP(KT)6-4-回风温度*)"},"LAHU03F04_RT            AT%I108.0      :INT ; (*空调机组NJ-3AP(KT)6-4-回风温度*)",null,"AHU03F04_RT","空调机组NJ-3AP(KT)6-4-回风温度",30054]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-3AP(KT)6-4-水阀反馈",{"$nulls":16},"NJ-3AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL102,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL102,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-4","03F04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH102,List!$B$3:$D$445,2,FALSE)&AJ102&\"_\"&VLOOKUP(AK102,List!$K$2:$M$447,2,FALSE)","v":"AHU03F04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM102&\" \"&\"AT%I\"&B96*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J102&\"*)\",\" \")","v":"LAHU03F04_WVB AT%I110.0 :INT ; (*空调机组NJ-3AP(KT)6-4-水阀反馈*)"},"LAHU03F04_WVB           AT%I110.0      :INT ; (*空调机组NJ-3AP(KT)6-4-水阀反馈*)",null,"AHU03F04_WVB","空调机组NJ-3AP(KT)6-4-水阀反馈",30055]
[null,{"$f":"B108","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B108&\"地址: \"&B105&\" *)\"","v":"(* IOM 0801U地址: 7 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH104&AA104&\"-\"&AK104","v":"空调机组NJ-3AP(KT)6-5-回风温度"},{"$nulls":16},{"$f":"IF(AI104=\"\",\"\",AI104)","v":"NJ-3AP(KT)6-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-5","03F05","回风温度",{"$f":"AH104&\"-\"&AK104","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"AHU03F05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%I\"&B105*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LAHU03F05_RT AT%I112.0 :INT ; (*空调机组NJ-3AP(KT)6-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104))),SEARCH(\":\",REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104)))))),\" \")","v":"LAHU03F05_RT            AT%I112.0      :INT ; (*空调机组NJ-3AP(KT)6-5-回风温度*)"},null,{"$f":"AM104","v":"AHU03F05_RT"},{"$f":"J104","v":"空调机组NJ-3AP(KT)6-5-回风温度"},{"$f":"30000+($B105*8+F104-1)","v":30056}]
[null,7,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-3AP(KT)6-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI105=\"\",\"\",AI105)","v":"NJ-3AP(KT)6-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-5","03F05","水阀反馈",{"$f":"AH105&\"-\"&AK105","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"AHU03F05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%I\"&B105*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LAHU03F05_WVB AT%I114.0 :INT ; (*空调机组NJ-3AP(KT)6-5-水阀反馈*)"},"LAHU03F05_WVB           AT%I114.0      :INT ; (*空调机组NJ-3AP(KT)6-5-水阀反馈*)",null,"AHU03F05_WVB",{"$f":"J105","v":"空调机组NJ-3AP(KT)6-5-水阀反馈"},{"$f":"AS104+1","v":30057}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)6-6-回风温度",{"$nulls":16},"NJ-3AP(KT)6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-6","03F06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":"AHU03F06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%I\"&B105*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":"LAHU03F06_RT AT%I116.0 :INT ; (*空调机组NJ-3AP(KT)6-6-回风温度*)"},"LAHU03F06_RT            AT%I116.0      :INT ; (*空调机组NJ-3AP(KT)6-6-回风温度*)",null,"AHU03F06_RT","空调机组NJ-3AP(KT)6-6-回风温度",{"$f":"AS105+1","v":30058}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-3AP(KT)6-6-水阀反馈",{"$nulls":16},"NJ-3AP(KT)6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-6","03F06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH107,List!$B$3:$D$445,2,FALSE)&AJ107&\"_\"&VLOOKUP(AK107,List!$K$2:$M$447,2,FALSE)","v":"AHU03F06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM107&\" \"&\"AT%I\"&B105*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J107&\"*)\",\" \")","v":"LAHU03F06_WVB AT%I118.0 :INT ; (*空调机组NJ-3AP(KT)6-6-水阀反馈*)"},"LAHU03F06_WVB           AT%I118.0      :INT ; (*空调机组NJ-3AP(KT)6-6-水阀反馈*)",null,"AHU03F06_WVB","空调机组NJ-3AP(KT)6-6-水阀反馈",30059]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),1,1))","v":0},5,null,5,"0V","风机盘管NJ-3AL(GG)6-1-温度状态",{"$nulls":16},"NJ-3AL(GG)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-3AL(GG)6-1","03F01","温度状态","风机盘管-温度状态",{"$f":"VLOOKUP(AH108,List!$B$3:$D$445,2,FALSE)&AJ108&\"_\"&VLOOKUP(AK108,List!$K$2:$M$447,2,FALSE)","v":"FCU03F01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM108&\" \"&\"AT%I\"&B105*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J108&\"*)\",\" \")","v":"LFCU03F01_T AT%I120.0 :INT ; (*风机盘管NJ-3AL(GG)6-1-温度状态*)"},"LFCU03F01_T             AT%I120.0      :INT ; (*风机盘管NJ-3AL(GG)6-1-温度状态*)",null,"FCU03F01_T","风机盘管NJ-3AL(GG)6-1-温度状态",30060]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH109,List!$B$3:$D$445,2,FALSE)&AJ109&\"_\"&VLOOKUP(AK109,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM109&\" \"&\"AT%I\"&B105*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J109&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J109","v":"-"},30061]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL110,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL110,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH110,List!$B$3:$D$445,2,FALSE)&AJ110&\"_\"&VLOOKUP(AK110,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM110&\" \"&\"AT%I\"&B105*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J110&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30062]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},{"$f":"IF(AI111=\"\",\"\",AI111)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL111,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL111,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH111,List!$B$3:$D$445,2,FALSE)&AJ111&\"_\"&VLOOKUP(AK111,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM111&\" \"&\"AT%I\"&B105*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J111&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30063]
[null,{"$f":"B117","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B117&\"地址: \"&B114&\" *)\"","v":"(* IOM 0401A地址: 8 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH113&AA113&\"-\"&AK113","v":"空调机组NJ-3AP(KT)6-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI113=\"\",\"\",AI113)","v":"NJ-3AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-1","03F01","水阀控制",{"$f":"AH113&\"-\"&AK113","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH113,List!$B$3:$D$445,2,FALSE)&AJ113&\"_\"&VLOOKUP(AK113,List!$K$2:$M$447,2,FALSE)","v":"AHU03F01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM113&\" \"&\"AT%Q\"&B114*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J113&\"*)\",\" \")","v":"LAHU03F01_WVC AT%Q128.0 :INT ; (*空调机组NJ-3AP(KT)6-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN113,SEARCH(\"AT%\",AN113),,REPT(\" \",25-SEARCH(\"AT%\",AN113))),SEARCH(\":\",REPLACE(AN113,SEARCH(\"AT%\",AN113),,REPT(\" \",25-SEARCH(\"AT%\",AN113)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN113,SEARCH(\"AT%\",AN113),,REPT(\" \",25-SEARCH(\"AT%\",AN113)))))),\" \")","v":"LAHU03F01_WVC           AT%Q128.0      :INT ; (*空调机组NJ-3AP(KT)6-1-水阀控制*)"},null,{"$f":"AM113","v":"AHU03F01_WVC"},{"$f":"J113","v":"空调机组NJ-3AP(KT)6-1-水阀控制"},{"$f":"40000+($B114*8+F113-1)","v":40064}]
[null,8,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH114&AA114&\"-\"&AK114","v":"空调机组NJ-3AP(KT)6-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI114=\"\",\"\",AI114)","v":"NJ-3AP(KT)6-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-2","03F02","水阀控制",{"$f":"AH114&\"-\"&AK114","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH114,List!$B$3:$D$445,2,FALSE)&AJ114&\"_\"&VLOOKUP(AK114,List!$K$2:$M$447,2,FALSE)","v":"AHU03F02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM114&\" \"&\"AT%Q\"&B114*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J114&\"*)\",\" \")","v":"LAHU03F02_WVC AT%Q130.0 :INT ; (*空调机组NJ-3AP(KT)6-2-水阀控制*)"},"LAHU03F02_WVC           AT%Q130.0      :INT ; (*空调机组NJ-3AP(KT)6-2-水阀控制*)",null,"AHU03F02_WVC",{"$f":"J114","v":"空调机组NJ-3AP(KT)6-2-水阀控制"},{"$f":"AS113+1","v":40065}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH115&AA115&\"-\"&AK115","v":"空调机组NJ-3AP(KT)6-3-水阀控制"},{"$nulls":16},"NJ-3AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-3","03F03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH115,List!$B$3:$D$445,2,FALSE)&AJ115&\"_\"&VLOOKUP(AK115,List!$K$2:$M$447,2,FALSE)","v":"AHU03F03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM115&\" \"&\"AT%Q\"&B114*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J115&\"*)\",\" \")","v":"LAHU03F03_WVC AT%Q132.0 :INT ; (*空调机组NJ-3AP(KT)6-3-水阀控制*)"},"LAHU03F03_WVC           AT%Q132.0      :INT ; (*空调机组NJ-3AP(KT)6-3-水阀控制*)",null,"AHU03F03_WVC","空调机组NJ-3AP(KT)6-3-水阀控制",{"$f":"AS114+1","v":40066}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH116&AA116&\"-\"&AK116","v":"空调机组NJ-3AP(KT)6-4-水阀控制"},{"$nulls":16},"NJ-3AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-4","03F04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH116,List!$B$3:$D$445,2,FALSE)&AJ116&\"_\"&VLOOKUP(AK116,List!$K$2:$M$447,2,FALSE)","v":"AHU03F04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM116&\" \"&\"AT%Q\"&B114*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J116&\"*)\",\" \")","v":"LAHU03F04_WVC AT%Q134.0 :INT ; (*空调机组NJ-3AP(KT)6-4-水阀控制*)"},"LAHU03F04_WVC           AT%Q134.0      :INT ; (*空调机组NJ-3AP(KT)6-4-水阀控制*)",null,"AHU03F04_WVC","空调机组NJ-3AP(KT)6-4-水阀控制",40067]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B126","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B126&\"地址: \"&B123&\" *)\"","v":"(* IOM 0401A地址: 9 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH122&AA122&\"-\"&AK122","v":"空调机组NJ-3AP(KT)6-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI122=\"\",\"\",AI122)","v":"NJ-3AP(KT)6-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-5","03F05","水阀控制",{"$f":"AH122&\"-\"&AK122","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH122,List!$B$3:$D$445,2,FALSE)&AJ122&\"_\"&VLOOKUP(AK122,List!$K$2:$M$447,2,FALSE)","v":"AHU03F05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM122&\" \"&\"AT%Q\"&B123*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J122&\"*)\",\" \")","v":"LAHU03F05_WVC AT%Q144.0 :INT ; (*空调机组NJ-3AP(KT)6-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN122,SEARCH(\"AT%\",AN122),,REPT(\" \",25-SEARCH(\"AT%\",AN122))),SEARCH(\":\",REPLACE(AN122,SEARCH(\"AT%\",AN122),,REPT(\" \",25-SEARCH(\"AT%\",AN122)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN122,SEARCH(\"AT%\",AN122),,REPT(\" \",25-SEARCH(\"AT%\",AN122)))))),\" \")","v":"LAHU03F05_WVC           AT%Q144.0      :INT ; (*空调机组NJ-3AP(KT)6-5-水阀控制*)"},null,{"$f":"AM122","v":"AHU03F05_WVC"},{"$f":"J122","v":"空调机组NJ-3AP(KT)6-5-水阀控制"},{"$f":"40000+($B123*8+F122-1)","v":40072}]
[null,9,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH123&AA123&\"-\"&AK123","v":"空调机组NJ-3AP(KT)6-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI123=\"\",\"\",AI123)","v":"NJ-3AP(KT)6-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)6-6","03F06","水阀控制",{"$f":"AH123&\"-\"&AK123","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH123,List!$B$3:$D$445,2,FALSE)&AJ123&\"_\"&VLOOKUP(AK123,List!$K$2:$M$447,2,FALSE)","v":"AHU03F06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM123&\" \"&\"AT%Q\"&B123*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J123&\"*)\",\" \")","v":"LAHU03F06_WVC AT%Q146.0 :INT ; (*空调机组NJ-3AP(KT)6-6-水阀控制*)"},"LAHU03F06_WVC           AT%Q146.0      :INT ; (*空调机组NJ-3AP(KT)6-6-水阀控制*)",null,"AHU03F06_WVC",{"$f":"J123","v":"空调机组NJ-3AP(KT)6-6-水阀控制"},{"$f":"AS122+1","v":40073}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH124&AA124&\"-\"&AK124","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH124,List!$B$3:$D$445,2,FALSE)&AJ124&\"_\"&VLOOKUP(AK124,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM124&\" \"&\"AT%Q\"&B123*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J124&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS123+1","v":40074}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH125&AA125&\"-\"&AK125","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH125,List!$B$3:$D$445,2,FALSE)&AJ125&\"_\"&VLOOKUP(AK125,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM125&\" \"&\"AT%Q\"&B123*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J125&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40075]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L406","index":37,"n_rows":154,"n_cols":45,"rows_kept":154,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[41,5,41,6],[41,9,41,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[75,5,75,6],[75,9,75,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[84,5,84,6],[84,9,84,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[92,5,92,6],[92,9,92,25],[93,5,93,6],[93,9,93,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[101,5,101,6],[101,9,101,25],[102,5,102,6],[102,9,102,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[110,5,110,6],[110,9,110,25],[111,5,111,6],[111,9,111,25],[112,5,112,6],[112,9,112,25],[113,5,113,6],[113,9,113,25],[114,5,114,6],[114,9,114,25],[115,5,115,6],[115,9,115,25],[116,5,116,6],[116,9,116,25],[117,5,117,6],[117,9,117,25],[119,5,119,6],[119,9,119,25],[120,5,120,6],[120,9,120,25],[121,5,121,6],[121,9,121,25],[122,5,122,6],[122,9,122,25],[123,5,123,6],[123,9,123,25],[124,5,124,6],[124,9,124,25],[125,5,125,6],[125,9,125,25],[126,5,126,6],[126,9,126,25],[128,5,128,6],[128,9,128,25],[129,5,129,6],[129,9,129,25],[130,5,130,6],[130,9,130,25],[131,5,131,6],[131,9,131,25],[132,5,132,6],[132,9,132,25],[133,5,133,6],[133,9,133,25],[134,5,134,6],[134,9,134,25],[135,5,135,6],[135,9,135,25],[137,5,137,6],[137,9,137,25],[138,5,138,6],[138,9,138,25],[139,5,139,6],[139,9,139,25],[140,5,140,6],[140,9,140,25],[141,5,141,6],[141,9,141,25],[142,5,142,6],[142,9,142,25],[143,5,143,6],[143,9,143,25],[144,5,144,6],[144,9,144,25],[146,5,146,6],[146,9,146,25],[147,5,147,6],[147,9,147,25],[148,5,148,6],[148,9,148,25],[149,5,149,6],[149,9,149,25],[150,5,150,6],[150,9,150,25],[151,5,151,6],[151,9,151,25],[152,5,152,6],[152,9,152,25],[153,5,153,6],[153,9,153,25],[4,1,5,1],[11,1,22,1],[28,1,39,1],[45,1,56,1],[62,1,73,1],[79,1,90,1],[96,1,99,1],[105,1,108,1],[114,1,117,1],[123,1,126,1],[132,1,135,1],[141,1,144,1],[150,1,153,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4],[32,2,39,4],[83,2,90,4],[49,2,56,4],[66,2,73,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L24",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 10 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH8&AA8&\"-\"&AK8","v":"空调机组NJ-4AP(KT)6-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-4AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-1","04F01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH8,List!$B$3:$D$445,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,List!$K$2:$M$447,2,FALSE)","v":"AHU04F01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LAHU04F01_R AT%I160.0 :BOOL; (*空调机组NJ-4AP(KT)6-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LAHU04F01_R             AT%I160.0      :BOOL; (*空调机组NJ-4AP(KT)6-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L24\\L24AHU04F01_R"},{"$f":"J8","v":"空调机组NJ-4AP(KT)6-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":11280}]
[null,10,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},2,null,3,4,"空调机组NJ-4AP(KT)6-1-故障状态",{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-4AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-1","04F01","故障状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU04F01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU04F01_F AT%I160.1 :BOOL; (*空调机组NJ-4AP(KT)6-1-故障状态*)"},"LAHU04F01_F             AT%I160.1      :BOOL; (*空调机组NJ-4AP(KT)6-1-故障状态*)",null,"L24\\L24AHU04F01_F",{"$f":"J9","v":"空调机组NJ-4AP(KT)6-1-故障状态"},{"$f":"AS8+1","v":11281}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-4AP(KT)6-1-自动状态",{"$nulls":16},"NJ-4AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-1","04F01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU04F01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU04F01_A AT%I160.2 :BOOL; (*空调机组NJ-4AP(KT)6-1-自动状态*)"},"LAHU04F01_A             AT%I160.2      :BOOL; (*空调机组NJ-4AP(KT)6-1-自动状态*)",null,"L24\\L24AHU04F01_A","空调机组NJ-4AP(KT)6-1-自动状态",{"$f":"AS9+1","v":11282}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-4AP(KT)6-1-风机压差",{"$nulls":16},"NJ-4AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-1","04F01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU04F01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU04F01_FPS AT%I160.3 :BOOL; (*空调机组NJ-4AP(KT)6-1-风机压差*)"},"LAHU04F01_FPS           AT%I160.3      :BOOL; (*空调机组NJ-4AP(KT)6-1-风机压差*)",null,"L24\\L24AHU04F01_FPS","空调机组NJ-4AP(KT)6-1-风机压差",11283]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-4AP(KT)6-2-运行状态",{"$nulls":16},"NJ-4AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-2","04F02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU04F02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU04F02_R AT%I160.4 :BOOL; (*空调机组NJ-4AP(KT)6-2-运行状态*)"},"LAHU04F02_R             AT%I160.4      :BOOL; (*空调机组NJ-4AP(KT)6-2-运行状态*)",null,"L24\\L24AHU04F02_R","空调机组NJ-4AP(KT)6-2-运行状态",11284]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-4AP(KT)6-2-故障状态",{"$nulls":16},"NJ-4AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-2","04F02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU04F02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU04F02_F AT%I160.5 :BOOL; (*空调机组NJ-4AP(KT)6-2-故障状态*)"},"LAHU04F02_F             AT%I160.5      :BOOL; (*空调机组NJ-4AP(KT)6-2-故障状态*)",null,"L24\\L24AHU04F02_F","空调机组NJ-4AP(KT)6-2-故障状态",11285]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-4AP(KT)6-2-自动状态",{"$nulls":16},"NJ-4AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-2","04F02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU04F02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU04F02_A AT%I160.6 :BOOL; (*空调机组NJ-4AP(KT)6-2-自动状态*)"},"LAHU04F02_A             AT%I160.6      :BOOL; (*空调机组NJ-4AP(KT)6-2-自动状态*)",null,"L24\\L24AHU04F02_A","空调机组NJ-4AP(KT)6-2-自动状态",11286]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-4AP(KT)6-2-风机压差",{"$nulls":16},"NJ-4AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-2","04F02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU04F02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU04F02_FPS AT%I160.7 :BOOL; (*空调机组NJ-4AP(KT)6-2-风机压差*)"},"LAHU04F02_FPS           AT%I160.7      :BOOL; (*空调机组NJ-4AP(KT)6-2-风机压差*)",null,"L24\\L24AHU04F02_FPS","空调机组NJ-4AP(KT)6-2-风机压差",11287]
[{"$nulls":5},9,null,17,18,"空调机组NJ-4AP(KT)6-3-运行状态",{"$nulls":16},"NJ-4AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-3","04F03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU04F03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU04F03_R AT%I161.0 :BOOL; (*空调机组NJ-4AP(KT)6-3-运行状态*)"},"LAHU04F03_R             AT%I161.0      :BOOL; (*空调机组NJ-4AP(KT)6-3-运行状态*)",null,"L24\\L24AHU04F03_R","空调机组NJ-4AP(KT)6-3-运行状态",11288]
[{"$nulls":5},10,null,19,20,"空调机组NJ-4AP(KT)6-3-故障状态",{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-4AP(KT)6-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-3","04F03","故障状态",{"$f":"AH17&\"-\"&AK17","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU04F03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU04F03_F AT%I161.1 :BOOL; (*空调机组NJ-4AP(KT)6-3-故障状态*)"},"LAHU04F03_F             AT%I161.1      :BOOL; (*空调机组NJ-4AP(KT)6-3-故障状态*)",null,"L24\\L24AHU04F03_F","空调机组NJ-4AP(KT)6-3-故障状态",11289]
[{"$nulls":5},11,null,21,22,"空调机组NJ-4AP(KT)6-3-自动状态",{"$nulls":16},"NJ-4AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-3","04F03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU04F03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU04F03_A AT%I161.2 :BOOL; (*空调机组NJ-4AP(KT)6-3-自动状态*)"},"LAHU04F03_A             AT%I161.2      :BOOL; (*空调机组NJ-4AP(KT)6-3-自动状态*)",null,"L24\\L24AHU04F03_A","空调机组NJ-4AP(KT)6-3-自动状态",11290]
[{"$nulls":5},12,null,23,24,"空调机组NJ-4AP(KT)6-3-风机压差",{"$nulls":16},"NJ-4AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-3","04F03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU04F03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU04F03_FPS AT%I161.3 :BOOL; (*空调机组NJ-4AP(KT)6-3-风机压差*)"},"LAHU04F03_FPS           AT%I161.3      :BOOL; (*空调机组NJ-4AP(KT)6-3-风机压差*)",null,"L24\\L24AHU04F03_FPS","空调机组NJ-4AP(KT)6-3-风机压差",11291]
[{"$nulls":5},13,null,25,26,"空调机组NJ-4AP(KT)6-4-运行状态",{"$nulls":16},"NJ-4AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-4","04F04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU04F04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU04F04_R AT%I161.4 :BOOL; (*空调机组NJ-4AP(KT)6-4-运行状态*)"},"LAHU04F04_R             AT%I161.4      :BOOL; (*空调机组NJ-4AP(KT)6-4-运行状态*)",null,"L24\\L24AHU04F04_R","空调机组NJ-4AP(KT)6-4-运行状态",11292]
[{"$nulls":5},14,null,27,28,"空调机组NJ-4AP(KT)6-4-故障状态",{"$nulls":16},"NJ-4AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-4","04F04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU04F04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU04F04_F AT%I161.5 :BOOL; (*空调机组NJ-4AP(KT)6-4-故障状态*)"},"LAHU04F04_F             AT%I161.5      :BOOL; (*空调机组NJ-4AP(KT)6-4-故障状态*)",null,"L24\\L24AHU04F04_F","空调机组NJ-4AP(KT)6-4-故障状态",11293]
[{"$nulls":5},15,null,29,30,"空调机组NJ-4AP(KT)6-4-自动状态",{"$nulls":16},"NJ-4AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-4","04F04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU04F04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU04F04_A AT%I161.6 :BOOL; (*空调机组NJ-4AP(KT)6-4-自动状态*)"},"LAHU04F04_A             AT%I161.6      :BOOL; (*空调机组NJ-4AP(KT)6-4-自动状态*)",null,"L24\\L24AHU04F04_A","空调机组NJ-4AP(KT)6-4-自动状态",11294]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-4AP(KT)6-4-风机压差",{"$nulls":16},"NJ-4AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-4","04F04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU04F04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU04F04_FPS AT%I161.7 :BOOL; (*空调机组NJ-4AP(KT)6-4-风机压差*)"},"LAHU04F04_FPS           AT%I161.7      :BOOL; (*空调机组NJ-4AP(KT)6-4-风机压差*)",null,"L24\\L24AHU04F04_FPS","空调机组NJ-4AP(KT)6-4-风机压差",11295]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 1601R地址: 11 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH25&AA25&\"-\"&AK25","v":"空调机组NJ-4AP(KT)6-5-运行状态"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-4AP(KT)6-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-5","04F05","运行状态",{"$f":"AH25&\"-\"&AK25","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"AHU04F05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LAHU04F05_R AT%I176.0 :BOOL; (*空调机组NJ-4AP(KT)6-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LAHU04F05_R             AT%I176.0      :BOOL; (*空调机组NJ-4AP(KT)6-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L24\\L24AHU04F05_R"},{"$f":"J25","v":"空调机组NJ-4AP(KT)6-5-运行状态"},{"$f":"10000+($B26*16*8+F25-1)","v":11408}]
[null,11,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},2,null,3,4,"空调机组NJ-4AP(KT)6-5-故障状态",{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-4AP(KT)6-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-5","04F05","故障状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU04F05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU04F05_F AT%I176.1 :BOOL; (*空调机组NJ-4AP(KT)6-5-故障状态*)"},"LAHU04F05_F             AT%I176.1      :BOOL; (*空调机组NJ-4AP(KT)6-5-故障状态*)",null,"L24\\L24AHU04F05_F",{"$f":"J26","v":"空调机组NJ-4AP(KT)6-5-故障状态"},{"$f":"AS25+1","v":11409}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-4AP(KT)6-5-自动状态",{"$nulls":16},"NJ-4AP(KT)6-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-5","04F05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU04F05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU04F05_A AT%I176.2 :BOOL; (*空调机组NJ-4AP(KT)6-5-自动状态*)"},"LAHU04F05_A             AT%I176.2      :BOOL; (*空调机组NJ-4AP(KT)6-5-自动状态*)",null,"L24\\L24AHU04F05_A","空调机组NJ-4AP(KT)6-5-自动状态",{"$f":"AS26+1","v":11410}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-4AP(KT)6-5-风机压差",{"$nulls":16},"NJ-4AP(KT)6-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-5","04F05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU04F05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU04F05_FPS AT%I176.3 :BOOL; (*空调机组NJ-4AP(KT)6-5-风机压差*)"},"LAHU04F05_FPS           AT%I176.3      :BOOL; (*空调机组NJ-4AP(KT)6-5-风机压差*)",null,"L24\\L24AHU04F05_FPS","空调机组NJ-4AP(KT)6-5-风机压差",11411]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-4AP(KT)6-6-运行状态",{"$nulls":16},"NJ-4AP(KT)6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-6","04F06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU04F06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU04F06_R AT%I176.4 :BOOL; (*空调机组NJ-4AP(KT)6-6-运行状态*)"},"LAHU04F06_R             AT%I176.4      :BOOL; (*空调机组NJ-4AP(KT)6-6-运行状态*)",null,"L24\\L24AHU04F06_R","空调机组NJ-4AP(KT)6-6-运行状态",11412]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-4AP(KT)6-6-故障状态",{"$nulls":16},"NJ-4AP(KT)6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-6","04F06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU04F06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU04F06_F AT%I176.5 :BOOL; (*空调机组NJ-4AP(KT)6-6-故障状态*)"},"LAHU04F06_F             AT%I176.5      :BOOL; (*空调机组NJ-4AP(KT)6-6-故障状态*)",null,"L24\\L24AHU04F06_F","空调机组NJ-4AP(KT)6-6-故障状态",11413]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-4AP(KT)6-6-自动状态",{"$nulls":16},"NJ-4AP(KT)6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-6","04F06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU04F06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU04F06_A AT%I176.6 :BOOL; (*空调机组NJ-4AP(KT)6-6-自动状态*)"},"LAHU04F06_A             AT%I176.6      :BOOL; (*空调机组NJ-4AP(KT)6-6-自动状态*)",null,"L24\\L24AHU04F06_A","空调机组NJ-4AP(KT)6-6-自动状态",11414]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-4AP(KT)6-6-风机压差",{"$nulls":16},"NJ-4AP(KT)6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-6","04F06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU04F06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU04F06_FPS AT%I176.7 :BOOL; (*空调机组NJ-4AP(KT)6-6-风机压差*)"},"LAHU04F06_FPS           AT%I176.7      :BOOL; (*空调机组NJ-4AP(KT)6-6-风机压差*)",null,"L24\\L24AHU04F06_FPS","空调机组NJ-4AP(KT)6-6-风机压差",11415]
[{"$nulls":5},9,null,17,18,"空调机组NJ-4AP(KT)6-7-运行状态",{"$nulls":16},"NJ-4AP(KT)6-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-7","04F07","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU04F07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B26*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU04F07_R AT%I177.0 :BOOL; (*空调机组NJ-4AP(KT)6-7-运行状态*)"},"LAHU04F07_R             AT%I177.0      :BOOL; (*空调机组NJ-4AP(KT)6-7-运行状态*)",null,"L24\\L24AHU04F07_R","空调机组NJ-4AP(KT)6-7-运行状态",11416]
[{"$nulls":5},10,null,19,20,"空调机组NJ-4AP(KT)6-7-故障状态",{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-4AP(KT)6-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-7","04F07","故障状态",{"$f":"AH34&\"-\"&AK34","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU04F07_F"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B26*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU04F07_F AT%I177.1 :BOOL; (*空调机组NJ-4AP(KT)6-7-故障状态*)"},"LAHU04F07_F             AT%I177.1      :BOOL; (*空调机组NJ-4AP(KT)6-7-故障状态*)",null,"L24\\L24AHU04F07_F",{"$f":"J34","v":"空调机组NJ-4AP(KT)6-7-故障状态"},11417]
[{"$nulls":5},11,null,21,22,"空调机组NJ-4AP(KT)6-7-自动状态",{"$nulls":16},"NJ-4AP(KT)6-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-7","04F07","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU04F07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B26*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU04F07_A AT%I177.2 :BOOL; (*空调机组NJ-4AP(KT)6-7-自动状态*)"},"LAHU04F07_A             AT%I177.2      :BOOL; (*空调机组NJ-4AP(KT)6-7-自动状态*)",null,"L24\\L24AHU04F07_A","空调机组NJ-4AP(KT)6-7-自动状态",11418]
[{"$nulls":5},12,null,23,24,"空调机组NJ-4AP(KT)6-7-风机压差",{"$nulls":16},"NJ-4AP(KT)6-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-7","04F07","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU04F07_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B26*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU04F07_FPS AT%I177.3 :BOOL; (*空调机组NJ-4AP(KT)6-7-风机压差*)"},"LAHU04F07_FPS           AT%I177.3      :BOOL; (*空调机组NJ-4AP(KT)6-7-风机压差*)",null,"L24\\L24AHU04F07_FPS","空调机组NJ-4AP(KT)6-7-风机压差",11419]
[{"$nulls":5},13,null,25,26,"空调机组NJ-4AP(KT)6-8-运行状态",{"$nulls":16},"NJ-4AP(KT)6-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-8","04F08","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"AHU04F08_R"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B26*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LAHU04F08_R AT%I177.4 :BOOL; (*空调机组NJ-4AP(KT)6-8-运行状态*)"},"LAHU04F08_R             AT%I177.4      :BOOL; (*空调机组NJ-4AP(KT)6-8-运行状态*)",null,"L24\\L24AHU04F08_R","空调机组NJ-4AP(KT)6-8-运行状态",11420]
[{"$nulls":5},14,null,27,28,"空调机组NJ-4AP(KT)6-8-故障状态",{"$nulls":16},"NJ-4AP(KT)6-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-8","04F08","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"AHU04F08_F"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B26*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LAHU04F08_F AT%I177.5 :BOOL; (*空调机组NJ-4AP(KT)6-8-故障状态*)"},"LAHU04F08_F             AT%I177.5      :BOOL; (*空调机组NJ-4AP(KT)6-8-故障状态*)",null,"L24\\L24AHU04F08_F","空调机组NJ-4AP(KT)6-8-故障状态",11421]
[{"$nulls":5},15,null,29,30,"空调机组NJ-4AP(KT)6-8-自动状态",{"$nulls":16},"NJ-4AP(KT)6-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-8","04F08","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"AHU04F08_A"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B26*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LAHU04F08_A AT%I177.6 :BOOL; (*空调机组NJ-4AP(KT)6-8-自动状态*)"},"LAHU04F08_A             AT%I177.6      :BOOL; (*空调机组NJ-4AP(KT)6-8-自动状态*)",null,"L24\\L24AHU04F08_A","空调机组NJ-4AP(KT)6-8-自动状态",11422]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-4AP(KT)6-8-风机压差",{"$nulls":16},"NJ-4AP(KT)6-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-8","04F08","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"AHU04F08_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B26*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LAHU04F08_FPS AT%I177.7 :BOOL; (*空调机组NJ-4AP(KT)6-8-风机压差*)"},"LAHU04F08_FPS           AT%I177.7      :BOOL; (*空调机组NJ-4AP(KT)6-8-风机压差*)",null,"L24\\L24AHU04F08_FPS","空调机组NJ-4AP(KT)6-8-风机压差",11423]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B46&\"地址: \"&B43&\" *)\"","v":"(* IOM 1601R地址: 12 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH42&AA42&\"-\"&AK42","v":"空调机组NJ-4AP(KT)6-9-运行状态"},{"$nulls":16},{"$f":"IF(AI42=\"\",\"\",AI42)","v":"NJ-4AP(KT)6-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-9","04F09","运行状态",{"$f":"AH42&\"-\"&AK42","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":"AHU04F09_R"},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%I\"&B43*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":"LAHU04F09_R AT%I192.0 :BOOL; (*空调机组NJ-4AP(KT)6-9-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42))),SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))))),\" \")","v":"LAHU04F09_R             AT%I192.0      :BOOL; (*空调机组NJ-4AP(KT)6-9-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM42","v":"L24\\L24AHU04F09_R"},{"$f":"J42","v":"空调机组NJ-4AP(KT)6-9-运行状态"},{"$f":"10000+($B43*16*8+F42-1)","v":11536}]
[null,12,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-4AP(KT)6-9-故障状态",{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-4AP(KT)6-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-9","04F09","故障状态",{"$f":"AH43&\"-\"&AK43","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"AHU04F09_F"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B43*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LAHU04F09_F AT%I192.1 :BOOL; (*空调机组NJ-4AP(KT)6-9-故障状态*)"},"LAHU04F09_F             AT%I192.1      :BOOL; (*空调机组NJ-4AP(KT)6-9-故障状态*)",null,"L24\\L24AHU04F09_F",{"$f":"J43","v":"空调机组NJ-4AP(KT)6-9-故障状态"},{"$f":"AS42+1","v":11537}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":1},3,null,5,6,"空调机组NJ-4AP(KT)6-9-自动状态",{"$nulls":16},"NJ-4AP(KT)6-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-9","04F09","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"AHU04F09_A"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B43*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LAHU04F09_A AT%I192.2 :BOOL; (*空调机组NJ-4AP(KT)6-9-自动状态*)"},"LAHU04F09_A             AT%I192.2      :BOOL; (*空调机组NJ-4AP(KT)6-9-自动状态*)",null,"L24\\L24AHU04F09_A","空调机组NJ-4AP(KT)6-9-自动状态",{"$f":"AS43+1","v":11538}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-4AP(KT)6-9-风机压差",{"$nulls":16},"NJ-4AP(KT)6-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-9","04F09","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"AHU04F09_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B43*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LAHU04F09_FPS AT%I192.3 :BOOL; (*空调机组NJ-4AP(KT)6-9-风机压差*)"},"LAHU04F09_FPS           AT%I192.3      :BOOL; (*空调机组NJ-4AP(KT)6-9-风机压差*)",null,"L24\\L24AHU04F09_FPS","空调机组NJ-4AP(KT)6-9-风机压差",11539]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-4AL6-1-运行状态",{"$nulls":16},"NJ-4AL6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-1","04F01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"LCB04F01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B43*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LLCB04F01_R AT%I192.4 :BOOL; (*照明控制箱NJ-4AL6-1-运行状态*)"},"LLCB04F01_R             AT%I192.4      :BOOL; (*照明控制箱NJ-4AL6-1-运行状态*)",null,"L24\\L24LCB04F01_R","照明控制箱NJ-4AL6-1-运行状态",11540]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-4AL6-1-自动状态",{"$nulls":16},"NJ-4AL6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-1","04F01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"LCB04F01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B43*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LLCB04F01_A AT%I192.5 :BOOL; (*照明控制箱NJ-4AL6-1-自动状态*)"},"LLCB04F01_A             AT%I192.5      :BOOL; (*照明控制箱NJ-4AL6-1-自动状态*)",null,"L24\\L24LCB04F01_A","照明控制箱NJ-4AL6-1-自动状态",11541]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"照明控制箱NJ-4AL6-2-运行状态",{"$nulls":16},"NJ-4AL6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-2","04F02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"LCB04F02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B43*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LLCB04F02_R AT%I192.6 :BOOL; (*照明控制箱NJ-4AL6-2-运行状态*)"},"LLCB04F02_R             AT%I192.6      :BOOL; (*照明控制箱NJ-4AL6-2-运行状态*)",null,"L24\\L24LCB04F02_R","照明控制箱NJ-4AL6-2-运行状态",11542]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"照明控制箱NJ-4AL6-2-自动状态",{"$nulls":16},"NJ-4AL6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-2","04F02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"LCB04F02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B43*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LLCB04F02_A AT%I192.7 :BOOL; (*照明控制箱NJ-4AL6-2-自动状态*)"},"LLCB04F02_A             AT%I192.7      :BOOL; (*照明控制箱NJ-4AL6-2-自动状态*)",null,"L24\\L24LCB04F02_A","照明控制箱NJ-4AL6-2-自动状态",11543]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-4AL6-3-运行状态",{"$nulls":16},"NJ-4AL6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-3","04F03","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"LCB04F03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B43*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LLCB04F03_R AT%I193.0 :BOOL; (*照明控制箱NJ-4AL6-3-运行状态*)"},"LLCB04F03_R             AT%I193.0      :BOOL; (*照明控制箱NJ-4AL6-3-运行状态*)",null,"L24\\L24LCB04F03_R","照明控制箱NJ-4AL6-3-运行状态",11544]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-4AL6-3-自动状态",{"$nulls":16},{"$f":"IF(AI51=\"\",\"\",AI51)","v":"NJ-4AL6-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-3","04F03","自动状态",{"$f":"AH51&\"-\"&AK51","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"LCB04F03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B43*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LLCB04F03_A AT%I193.1 :BOOL; (*照明控制箱NJ-4AL6-3-自动状态*)"},"LLCB04F03_A             AT%I193.1      :BOOL; (*照明控制箱NJ-4AL6-3-自动状态*)",null,"L24\\L24LCB04F03_A",{"$f":"J51","v":"照明控制箱NJ-4AL6-3-自动状态"},11545]
[{"$nulls":5},11,null,21,22,"照明控制箱NJ-4AL6-4-运行状态",{"$nulls":16},"NJ-4AL6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-4","04F04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"LCB04F04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%I\"&B43*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LLCB04F04_R AT%I193.2 :BOOL; (*照明控制箱NJ-4AL6-4-运行状态*)"},"LLCB04F04_R             AT%I193.2      :BOOL; (*照明控制箱NJ-4AL6-4-运行状态*)",null,"L24\\L24LCB04F04_R","照明控制箱NJ-4AL6-4-运行状态",11546]
[{"$nulls":5},12,null,23,24,"照明控制箱NJ-4AL6-4-自动状态",{"$nulls":16},"NJ-4AL6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-4","04F04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"LCB04F04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%I\"&B43*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LLCB04F04_A AT%I193.3 :BOOL; (*照明控制箱NJ-4AL6-4-自动状态*)"},"LLCB04F04_A             AT%I193.3      :BOOL; (*照明控制箱NJ-4AL6-4-自动状态*)",null,"L24\\L24LCB04F04_A","照明控制箱NJ-4AL6-4-自动状态",11547]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-4AL6-5-运行状态",{"$nulls":16},"NJ-4AL6-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-5","04F05","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"LCB04F05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%I\"&B43*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LLCB04F05_R AT%I193.4 :BOOL; (*照明控制箱NJ-4AL6-5-运行状态*)"},"LLCB04F05_R             AT%I193.4      :BOOL; (*照明控制箱NJ-4AL6-5-运行状态*)",null,"L24\\L24LCB04F05_R","照明控制箱NJ-4AL6-5-运行状态",11548]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-4AL6-5-自动状态",{"$nulls":16},"NJ-4AL6-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-5","04F05","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"LCB04F05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%I\"&B43*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LLCB04F05_A AT%I193.5 :BOOL; (*照明控制箱NJ-4AL6-5-自动状态*)"},"LLCB04F05_A             AT%I193.5      :BOOL; (*照明控制箱NJ-4AL6-5-自动状态*)",null,"L24\\L24LCB04F05_A","照明控制箱NJ-4AL6-5-自动状态",11549]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-4AL6-6-运行状态",{"$nulls":16},"NJ-4AL6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-6","04F06","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"LCB04F06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%I\"&B43*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LLCB04F06_R AT%I193.6 :BOOL; (*照明控制箱NJ-4AL6-6-运行状态*)"},"LLCB04F06_R             AT%I193.6      :BOOL; (*照明控制箱NJ-4AL6-6-运行状态*)",null,"L24\\L24LCB04F06_R","照明控制箱NJ-4AL6-6-运行状态",11550]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-4AL6-6-自动状态",{"$nulls":16},"NJ-4AL6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-6","04F06","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"LCB04F06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%I\"&B43*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LLCB04F06_A AT%I193.7 :BOOL; (*照明控制箱NJ-4AL6-6-自动状态*)"},"LLCB04F06_A             AT%I193.7      :BOOL; (*照明控制箱NJ-4AL6-6-自动状态*)",null,"L24\\L24LCB04F06_A","照明控制箱NJ-4AL6-6-自动状态",11551]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B63&\"地址: \"&B60&\" *)\"","v":"(* IOM 1601R地址: 13 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH59&AA59&\"-\"&AK59","v":"照明控制箱NJ-4AL6-7-运行状态"},{"$nulls":16},{"$f":"IF(AI59=\"\",\"\",AI59)","v":"NJ-4AL6-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-7","04F07","运行状态",{"$f":"AH59&\"-\"&AK59","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH59,List!$B$3:$D$445,2,FALSE)&AJ59&\"_\"&VLOOKUP(AK59,List!$K$2:$M$447,2,FALSE)","v":"LCB04F07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM59&\" \"&\"AT%I\"&B60*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J59&\"*)\",\" \")","v":"LLCB04F07_R AT%I208.0 :BOOL; (*照明控制箱NJ-4AL6-7-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59))),SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))))),\" \")","v":"LLCB04F07_R             AT%I208.0      :BOOL; (*照明控制箱NJ-4AL6-7-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM59","v":"L24\\L24LCB04F07_R"},{"$f":"J59","v":"照明控制箱NJ-4AL6-7-运行状态"},{"$f":"10000+($B60*16*8+F59-1)","v":11664}]
[null,13,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH60&AA60&\"-\"&AK60","v":"照明控制箱NJ-4AL6-7-自动状态"},{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-4AL6-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-7","04F07","自动状态",{"$f":"AH60&\"-\"&AK60","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"LCB04F07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%I\"&B60*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LLCB04F07_A AT%I208.1 :BOOL; (*照明控制箱NJ-4AL6-7-自动状态*)"},"LLCB04F07_A             AT%I208.1      :BOOL; (*照明控制箱NJ-4AL6-7-自动状态*)",null,"L24\\L24LCB04F07_A",{"$f":"J60","v":"照明控制箱NJ-4AL6-7-自动状态"},{"$f":"AS59+1","v":11665}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH61&AA61&\"-\"&AK61","v":"排风机NJ-4AP(KT)6-1-运行状态"},{"$nulls":16},"NJ-4AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)6-1","04F01","运行状态",{"$f":"AH61&\"-\"&AK61","v":"排风机-运行状态"},{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"EAF04F01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%I\"&B60*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LEAF04F01_R AT%I208.2 :BOOL; (*排风机NJ-4AP(KT)6-1-运行状态*)"},"LEAF04F01_R             AT%I208.2      :BOOL; (*排风机NJ-4AP(KT)6-1-运行状态*)",null,"L24\\L24EAF04F01_R","排风机NJ-4AP(KT)6-1-运行状态",{"$f":"AS60+1","v":11666}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH62&AA62&\"-\"&AK62","v":"排风机NJ-4AP(KT)6-1-故障状态"},{"$nulls":16},"NJ-4AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)6-1","04F01","故障状态",{"$f":"AH62&\"-\"&AK62","v":"排风机-故障状态"},{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"EAF04F01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B60*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LEAF04F01_F AT%I208.3 :BOOL; (*排风机NJ-4AP(KT)6-1-故障状态*)"},"LEAF04F01_F             AT%I208.3      :BOOL; (*排风机NJ-4AP(KT)6-1-故障状态*)",null,"L24\\L24EAF04F01_F","排风机NJ-4AP(KT)6-1-故障状态",11667]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},5,null,9,10,"排风机NJ-4AP(KT)6-1-自动状态",{"$nulls":16},"NJ-4AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)6-1","04F01","自动状态","排风机-自动状态",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"EAF04F01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B60*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LEAF04F01_A AT%I208.4 :BOOL; (*排风机NJ-4AP(KT)6-1-自动状态*)"},"LEAF04F01_A             AT%I208.4      :BOOL; (*排风机NJ-4AP(KT)6-1-自动状态*)",null,"L24\\L24EAF04F01_A","排风机NJ-4AP(KT)6-1-自动状态",11668]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"遮阳帘-运行状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04F01","运行状态","遮阳帘-运行状态",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"SSC04F01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B60*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LSSC04F01_R AT%I208.5 :BOOL; (*遮阳帘-运行状态*)"},"LSSC04F01_R             AT%I208.5      :BOOL; (*遮阳帘-运行状态*)",null,"L24\\L24SSC04F01_R","遮阳帘-运行状态",11669]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"遮阳帘-自动状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04F01","自动状态","遮阳帘-自动状态",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":"SSC04F01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B60*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":"LSSC04F01_A AT%I208.6 :BOOL; (*遮阳帘-自动状态*)"},"LSSC04F01_A             AT%I208.6      :BOOL; (*遮阳帘-自动状态*)",null,"L24\\L24SSC04F01_A","遮阳帘-自动状态",11670]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"遮阳帘-运行状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04F02","运行状态","遮阳帘-运行状态",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":"SSC04F02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B60*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":"LSSC04F02_R AT%I208.7 :BOOL; (*遮阳帘-运行状态*)"},"LSSC04F02_R             AT%I208.7      :BOOL; (*遮阳帘-运行状态*)",null,"L24\\L24SSC04F02_R","遮阳帘-运行状态",11671]
[{"$nulls":5},9,null,17,18,"遮阳帘-自动状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04F02","自动状态","遮阳帘-自动状态",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":"SSC04F02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%I\"&B60*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":"LSSC04F02_A AT%I209.0 :BOOL; (*遮阳帘-自动状态*)"},"LSSC04F02_A             AT%I209.0      :BOOL; (*遮阳帘-自动状态*)",null,"L24\\L24SSC04F02_A","遮阳帘-自动状态",11672]
[{"$nulls":5},10,null,19,20,"风机盘管NJ-4AP(KT)6-1-运行状态",{"$nulls":16},{"$f":"IF(AI68=\"\",\"\",AI68)","v":"NJ-4AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)6-1","04F01","运行状态",{"$f":"AH68&\"-\"&AK68","v":"风机盘管-运行状态"},{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"FCU04F01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%I\"&B60*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LFCU04F01_R AT%I209.1 :BOOL; (*风机盘管NJ-4AP(KT)6-1-运行状态*)"},"LFCU04F01_R             AT%I209.1      :BOOL; (*风机盘管NJ-4AP(KT)6-1-运行状态*)",null,"L24\\L24FCU04F01_R",{"$f":"J68","v":"风机盘管NJ-4AP(KT)6-1-运行状态"},11673]
[{"$nulls":5},11,null,21,22,"风机盘管NJ-4AP(KT)6-1-自动状态",{"$nulls":16},"NJ-4AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)6-1","04F01","自动状态","风机盘管-自动状态",{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"FCU04F01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%I\"&B60*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LFCU04F01_A AT%I209.2 :BOOL; (*风机盘管NJ-4AP(KT)6-1-自动状态*)"},"LFCU04F01_A             AT%I209.2      :BOOL; (*风机盘管NJ-4AP(KT)6-1-自动状态*)",null,"L24\\L24FCU04F01_A","风机盘管NJ-4AP(KT)6-1-自动状态",11674]
[{"$nulls":5},12,null,23,24,"风机盘管NJ-4AP(KT)6-1-电磁阀开启状态",{"$nulls":16},"NJ-4AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)6-1","04F01","电磁阀开启状态","风机盘管-电磁阀开启状态",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"FCU04F01_EVR"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%I\"&B60*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LFCU04F01_EVR AT%I209.3 :BOOL; (*风机盘管NJ-4AP(KT)6-1-电磁阀开启状态*)"},"LFCU04F01_EVR           AT%I209.3      :BOOL; (*风机盘管NJ-4AP(KT)6-1-电磁阀开启状态*)",null,"L24\\L24FCU04F01_EVR","风机盘管NJ-4AP(KT)6-1-电磁阀开启状态",11675]
[{"$nulls":5},13,null,25,26,"风机盘管NJ-4AP(KT)6-1-电磁阀自动状态",{"$nulls":16},"NJ-4AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)6-1","04F01","电磁阀自动状态","风机盘管-电磁阀自动状态",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"FCU04F01_EVA"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%I\"&B60*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LFCU04F01_EVA AT%I209.4 :BOOL; (*风机盘管NJ-4AP(KT)6-1-电磁阀自动状态*)"},"LFCU04F01_EVA           AT%I209.4      :BOOL; (*风机盘管NJ-4AP(KT)6-1-电磁阀自动状态*)",null,"L24\\L24FCU04F01_EVA","风机盘管NJ-4AP(KT)6-1-电磁阀自动状态",11676]
[{"$nulls":5},14,null,27,28,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%I\"&B60*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN72,SEARCH(\"AT%\",AN72),,REPT(\" \",30-SEARCH(\"AT%\",AN72))),SEARCH(\":\",REPLACE(AN72,SEARCH(\"AT%\",AN72),,REPT(\" \",30-SEARCH(\"AT%\",AN72)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN72,SEARCH(\"AT%\",AN72),,REPT(\" \",25-SEARCH(\"AT%\",AN72)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",11677]
[{"$nulls":5},15,null,29,30,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%I\"&B60*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11678]
[".",{"$nulls":4},16,null,31,32,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%I\"&B60*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11679]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B80&\"地址: \"&B77&\" *)\"","v":"(* IOM 1601D地址: 14 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH76&AA76&\"-\"&AK76","v":"空调机组NJ-4AP(KT)6-1-启停控制"},{"$nulls":16},{"$f":"IF(AI76=\"\",\"\",AI76)","v":"NJ-4AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-1","04F01","启停控制",{"$f":"AH76&\"-\"&AK76","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH76,List!$B$3:$D$445,2,FALSE)&AJ76&\"_\"&VLOOKUP(AK76,List!$K$2:$M$447,2,FALSE)","v":"AHU04F01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM76&\" \"&\"AT%Q\"&B77*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J76&\"*)\",\" \")","v":"LAHU04F01_C AT%Q224.0 :BOOL; (*空调机组NJ-4AP(KT)6-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN76,SEARCH(\"AT%\",AN76),,REPT(\" \",25-SEARCH(\"AT%\",AN76))),SEARCH(\":\",REPLACE(AN76,SEARCH(\"AT%\",AN76),,REPT(\" \",25-SEARCH(\"AT%\",AN76)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN76,SEARCH(\"AT%\",AN76),,REPT(\" \",25-SEARCH(\"AT%\",AN76)))))),\" \")","v":"LAHU04F01_C             AT%Q224.0      :BOOL; (*空调机组NJ-4AP(KT)6-1-启停控制*)"},null,{"$f":"AM76","v":"AHU04F01_C"},{"$f":"J76","v":"空调机组NJ-4AP(KT)6-1-启停控制"},{"$f":"($B77*16*8+F76-1)","v":1792}]
[null,14,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-4AP(KT)6-2-启停控制",{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-4AP(KT)6-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-2","04F02","启停控制",{"$f":"AH77&\"-\"&AK77","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"AHU04F02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%Q\"&B77*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LAHU04F02_C AT%Q224.1 :BOOL; (*空调机组NJ-4AP(KT)6-2-启停控制*)"},"LAHU04F02_C             AT%Q224.1      :BOOL; (*空调机组NJ-4AP(KT)6-2-启停控制*)",null,"AHU04F02_C",{"$f":"J77","v":"空调机组NJ-4AP(KT)6-2-启停控制"},{"$f":"AS76+1","v":1793}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-4AP(KT)6-3-启停控制",{"$nulls":16},"NJ-4AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-3","04F03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU04F03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B77*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU04F03_C AT%Q224.2 :BOOL; (*空调机组NJ-4AP(KT)6-3-启停控制*)"},"LAHU04F03_C             AT%Q224.2      :BOOL; (*空调机组NJ-4AP(KT)6-3-启停控制*)",null,"AHU04F03_C","空调机组NJ-4AP(KT)6-3-启停控制",{"$f":"AS77+1","v":1794}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","空调机组NJ-4AP(KT)6-4-启停控制",{"$nulls":16},"NJ-4AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-4","04F04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU04F04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B77*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU04F04_C AT%Q224.3 :BOOL; (*空调机组NJ-4AP(KT)6-4-启停控制*)"},"LAHU04F04_C             AT%Q224.3      :BOOL; (*空调机组NJ-4AP(KT)6-4-启停控制*)",null,"AHU04F04_C","空调机组NJ-4AP(KT)6-4-启停控制",1795]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B77),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-4AP(KT)6-5-启停控制",{"$nulls":16},"NJ-4AP(KT)6-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-5","04F05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU04F05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B77*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU04F05_C AT%Q224.4 :BOOL; (*空调机组NJ-4AP(KT)6-5-启停控制*)"},"LAHU04F05_C             AT%Q224.4      :BOOL; (*空调机组NJ-4AP(KT)6-5-启停控制*)",null,"AHU04F05_C","空调机组NJ-4AP(KT)6-5-启停控制",1796]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-4AP(KT)6-6-启停控制",{"$nulls":16},"NJ-4AP(KT)6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-6","04F06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"AHU04F06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%Q\"&B77*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LAHU04F06_C AT%Q224.5 :BOOL; (*空调机组NJ-4AP(KT)6-6-启停控制*)"},"LAHU04F06_C             AT%Q224.5      :BOOL; (*空调机组NJ-4AP(KT)6-6-启停控制*)",null,"AHU04F06_C","空调机组NJ-4AP(KT)6-6-启停控制",1797]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","空调机组NJ-4AP(KT)6-7-启停控制",{"$nulls":16},"NJ-4AP(KT)6-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-7","04F07","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":"AHU04F07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%Q\"&B77*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":"LAHU04F07_C AT%Q224.6 :BOOL; (*空调机组NJ-4AP(KT)6-7-启停控制*)"},"LAHU04F07_C             AT%Q224.6      :BOOL; (*空调机组NJ-4AP(KT)6-7-启停控制*)",null,"AHU04F07_C","空调机组NJ-4AP(KT)6-7-启停控制",1798]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B79=20,1,IF(B79=50,10,IF(B79=125,11,IF(B79=250,100,IF(B79=500,101,IF(B79=800,110,IF(B79=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","空调机组NJ-4AP(KT)6-8-启停控制",{"$nulls":16},"NJ-4AP(KT)6-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-8","04F08","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":"AHU04F08_C"},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%Q\"&B77*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":"LAHU04F08_C AT%Q224.7 :BOOL; (*空调机组NJ-4AP(KT)6-8-启停控制*)"},"LAHU04F08_C             AT%Q224.7      :BOOL; (*空调机组NJ-4AP(KT)6-8-启停控制*)",null,"AHU04F08_C","空调机组NJ-4AP(KT)6-8-启停控制",1799]
[{"$nulls":5},9,null,"9+","9-","空调机组NJ-4AP(KT)6-9-启停控制",{"$nulls":16},"NJ-4AP(KT)6-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-9","04F09","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH84,List!$B$3:$D$445,2,FALSE)&AJ84&\"_\"&VLOOKUP(AK84,List!$K$2:$M$447,2,FALSE)","v":"AHU04F09_C"},{"$f":"_xlfn.IFNA(\"L\"&AM84&\" \"&\"AT%Q\"&B77*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J84&\"*)\",\" \")","v":"LAHU04F09_C AT%Q225.0 :BOOL; (*空调机组NJ-4AP(KT)6-9-启停控制*)"},"LAHU04F09_C             AT%Q225.0      :BOOL; (*空调机组NJ-4AP(KT)6-9-启停控制*)",null,"AHU04F09_C","空调机组NJ-4AP(KT)6-9-启停控制",1800]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-4AL6-1-启停控制",{"$nulls":16},{"$f":"IF(AI85=\"\",\"\",AI85)","v":"NJ-4AL6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-1","04F01","启停控制",{"$f":"AH85&\"-\"&AK85","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH85,List!$B$3:$D$445,2,FALSE)&AJ85&\"_\"&VLOOKUP(AK85,List!$K$2:$M$447,2,FALSE)","v":"LCB04F01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM85&\" \"&\"AT%Q\"&B77*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J85&\"*)\",\" \")","v":"LLCB04F01_C AT%Q225.1 :BOOL; (*照明控制箱NJ-4AL6-1-启停控制*)"},"LLCB04F01_C             AT%Q225.1      :BOOL; (*照明控制箱NJ-4AL6-1-启停控制*)",null,"LCB04F01_C",{"$f":"J85","v":"照明控制箱NJ-4AL6-1-启停控制"},1801]
[{"$nulls":5},11,null,"11+","11-","照明控制箱NJ-4AL6-2-启停控制",{"$nulls":16},"NJ-4AL6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-2","04F02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"LCB04F02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%Q\"&B77*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LLCB04F02_C AT%Q225.2 :BOOL; (*照明控制箱NJ-4AL6-2-启停控制*)"},"LLCB04F02_C             AT%Q225.2      :BOOL; (*照明控制箱NJ-4AL6-2-启停控制*)",null,"LCB04F02_C","照明控制箱NJ-4AL6-2-启停控制",1802]
[{"$nulls":5},12,null,"12+","12-","照明控制箱NJ-4AL6-3-启停控制",{"$nulls":16},"NJ-4AL6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-3","04F03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"LCB04F03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%Q\"&B77*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LLCB04F03_C AT%Q225.3 :BOOL; (*照明控制箱NJ-4AL6-3-启停控制*)"},"LLCB04F03_C             AT%Q225.3      :BOOL; (*照明控制箱NJ-4AL6-3-启停控制*)",null,"LCB04F03_C","照明控制箱NJ-4AL6-3-启停控制",1803]
[{"$nulls":5},13,null,"13+","13-","照明控制箱NJ-4AL6-4-启停控制",{"$nulls":16},"NJ-4AL6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-4","04F04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"LCB04F04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%Q\"&B77*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LLCB04F04_C AT%Q225.4 :BOOL; (*照明控制箱NJ-4AL6-4-启停控制*)"},"LLCB04F04_C             AT%Q225.4      :BOOL; (*照明控制箱NJ-4AL6-4-启停控制*)",null,"LCB04F04_C","照明控制箱NJ-4AL6-4-启停控制",1804]
[{"$nulls":5},14,null,"14+","14-","照明控制箱NJ-4AL6-5-启停控制",{"$nulls":16},"NJ-4AL6-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-5","04F05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"LCB04F05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%Q\"&B77*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LLCB04F05_C AT%Q225.5 :BOOL; (*照明控制箱NJ-4AL6-5-启停控制*)"},"LLCB04F05_C             AT%Q225.5      :BOOL; (*照明控制箱NJ-4AL6-5-启停控制*)",null,"LCB04F05_C","照明控制箱NJ-4AL6-5-启停控制",1805]
[{"$nulls":5},15,null,"15+","15-","照明控制箱NJ-4AL6-6-启停控制",{"$nulls":16},"NJ-4AL6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-6","04F06","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":"LCB04F06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%Q\"&B77*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":"LLCB04F06_C AT%Q225.6 :BOOL; (*照明控制箱NJ-4AL6-6-启停控制*)"},"LLCB04F06_C             AT%Q225.6      :BOOL; (*照明控制箱NJ-4AL6-6-启停控制*)",null,"LCB04F06_C","照明控制箱NJ-4AL6-6-启停控制",1806]
[".",{"$nulls":4},16,null,"16+","16-","照明控制箱NJ-4AL6-7-启停控制",{"$nulls":16},"NJ-4AL6-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-4AL6-7","04F07","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH91,List!$B$3:$D$445,2,FALSE)&AJ91&\"_\"&VLOOKUP(AK91,List!$K$2:$M$447,2,FALSE)","v":"LCB04F07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM91&\" \"&\"AT%Q\"&B77*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J91&\"*)\",\" \")","v":"LLCB04F07_C AT%Q225.7 :BOOL; (*照明控制箱NJ-4AL6-7-启停控制*)"},"LLCB04F07_C             AT%Q225.7      :BOOL; (*照明控制箱NJ-4AL6-7-启停控制*)",null,"LCB04F07_C","照明控制箱NJ-4AL6-7-启停控制",1807]
[null,"IOM 0801D",{"$nulls":38},{"$f":"\"(* \"&B97&\"地址: \"&B94&\" *)\"","v":"(* IOM 0801D地址: 15 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH93&AA93&\"-\"&AK93","v":"排风机NJ-4AP(KT)6-1-启停控制"},{"$nulls":16},{"$f":"IF(AI93=\"\",\"\",AI93)","v":"NJ-4AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL93,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL93,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)6-1","04F01","启停控制",{"$f":"AH93&\"-\"&AK93","v":"排风机-启停控制"},{"$f":"VLOOKUP(AH93,List!$B$3:$D$445,2,FALSE)&AJ93&\"_\"&VLOOKUP(AK93,List!$K$2:$M$447,2,FALSE)","v":"EAF04F01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM93&\" \"&\"AT%Q\"&B94*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J93&\"*)\",\" \")","v":"LEAF04F01_C AT%Q240.0 :BOOL; (*排风机NJ-4AP(KT)6-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN93,SEARCH(\"AT%\",AN93),,REPT(\" \",25-SEARCH(\"AT%\",AN93))),SEARCH(\":\",REPLACE(AN93,SEARCH(\"AT%\",AN93),,REPT(\" \",25-SEARCH(\"AT%\",AN93)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN93,SEARCH(\"AT%\",AN93),,REPT(\" \",25-SEARCH(\"AT%\",AN93)))))),\" \")","v":"LEAF04F01_C             AT%Q240.0      :BOOL; (*排风机NJ-4AP(KT)6-1-启停控制*)"},null,{"$f":"AM93","v":"EAF04F01_C"},{"$f":"J93","v":"排风机NJ-4AP(KT)6-1-启停控制"},{"$f":"($B94*16*8+F93-1)","v":1920}]
[null,15,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","遮阳帘-启停控制",{"$nulls":16},{"$f":"IF(AI94=\"\",\"\",AI94)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04F01","启停控制",{"$f":"AH94&\"-\"&AK94","v":"遮阳帘-启停控制"},{"$f":"VLOOKUP(AH94,List!$B$3:$D$445,2,FALSE)&AJ94&\"_\"&VLOOKUP(AK94,List!$K$2:$M$447,2,FALSE)","v":"SSC04F01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM94&\" \"&\"AT%Q\"&B94*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J94&\"*)\",\" \")","v":"LSSC04F01_C AT%Q240.1 :BOOL; (*遮阳帘-启停控制*)"},"LSSC04F01_C             AT%Q240.1      :BOOL; (*遮阳帘-启停控制*)",null,"SSC04F01_C",{"$f":"J94","v":"遮阳帘-启停控制"},{"$f":"AS93+1","v":1921}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","遮阳帘-启停控制",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04F02","启停控制","遮阳帘-启停控制",{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"SSC04F02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%Q\"&B94*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LSSC04F02_C AT%Q240.2 :BOOL; (*遮阳帘-启停控制*)"},"LSSC04F02_C             AT%Q240.2      :BOOL; (*遮阳帘-启停控制*)",null,"SSC04F02_C","遮阳帘-启停控制",{"$f":"AS94+1","v":1922}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","风机盘管NJ-4AP(KT)6-1-启停控制",{"$nulls":16},"NJ-4AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)6-1","04F01","启停控制","风机盘管-启停控制",{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"FCU04F01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%Q\"&B94*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LFCU04F01_C AT%Q240.3 :BOOL; (*风机盘管NJ-4AP(KT)6-1-启停控制*)"},"LFCU04F01_C             AT%Q240.3      :BOOL; (*风机盘管NJ-4AP(KT)6-1-启停控制*)",null,"FCU04F01_C","风机盘管NJ-4AP(KT)6-1-启停控制",1923]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B94),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","风机盘管NJ-4AP(KT)6-1-电磁阀开关控制",{"$nulls":16},"NJ-4AP(KT)6-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)6-1","04F01","电磁阀开关控制","风机盘管-电磁阀开关控制",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":"FCU04F01_EVC"},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%Q\"&B94*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":"LFCU04F01_EVC AT%Q240.4 :BOOL; (*风机盘管NJ-4AP(KT)6-1-电磁阀开关控制*)"},"LFCU04F01_EVC           AT%Q240.4      :BOOL; (*风机盘管NJ-4AP(KT)6-1-电磁阀开关控制*)",null,"FCU04F01_EVC","风机盘管NJ-4AP(KT)6-1-电磁阀开关控制",1924]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B96=20,1,IF(B96=50,10,IF(B96=125,11,IF(B96=250,100,IF(B96=500,101,IF(B96=800,110,IF(B96=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B96=20,1,IF(B96=50,10,IF(B96=125,11,IF(B96=250,100,IF(B96=500,101,IF(B96=800,110,IF(B96=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%Q\"&B94*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1925]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B96=20,1,IF(B96=50,10,IF(B96=125,11,IF(B96=250,100,IF(B96=500,101,IF(B96=800,110,IF(B96=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B96=20,1,IF(B96=50,10,IF(B96=125,11,IF(B96=250,100,IF(B96=500,101,IF(B96=800,110,IF(B96=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH99,List!$B$3:$D$445,2,FALSE)&AJ99&\"_\"&VLOOKUP(AK99,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM99&\" \"&\"AT%Q\"&B94*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J99&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1926]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B96=20,1,IF(B96=50,10,IF(B96=125,11,IF(B96=250,100,IF(B96=500,101,IF(B96=800,110,IF(B96=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B96=20,1,IF(B96=50,10,IF(B96=125,11,IF(B96=250,100,IF(B96=500,101,IF(B96=800,110,IF(B96=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH100,List!$B$3:$D$445,2,FALSE)&AJ100&\"_\"&VLOOKUP(AK100,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM100&\" \"&\"AT%Q\"&B94*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J100&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1927]
[null,{"$f":"B106","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B106&\"地址: \"&B103&\" *)\"","v":"(* IOM 0801U地址: 16 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH102&AA102&\"-\"&AK102","v":"空调机组NJ-4AP(KT)6-1-回风温度"},{"$nulls":16},{"$f":"IF(AI102=\"\",\"\",AI102)","v":"NJ-4AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL102,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL102,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-1","04F01","回风温度",{"$f":"AH102&\"-\"&AK102","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH102,List!$B$3:$D$445,2,FALSE)&AJ102&\"_\"&VLOOKUP(AK102,List!$K$2:$M$447,2,FALSE)","v":"AHU04F01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM102&\" \"&\"AT%I\"&B103*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J102&\"*)\",\" \")","v":"LAHU04F01_RT AT%I256.0 :INT ; (*空调机组NJ-4AP(KT)6-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN102,SEARCH(\"AT%\",AN102),,REPT(\" \",25-SEARCH(\"AT%\",AN102))),SEARCH(\":\",REPLACE(AN102,SEARCH(\"AT%\",AN102),,REPT(\" \",25-SEARCH(\"AT%\",AN102)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN102,SEARCH(\"AT%\",AN102),,REPT(\" \",25-SEARCH(\"AT%\",AN102)))))),\" \")","v":"LAHU04F01_RT            AT%I256.0      :INT ; (*空调机组NJ-4AP(KT)6-1-回风温度*)"},null,{"$f":"AM102","v":"AHU04F01_RT"},{"$f":"J102","v":"空调机组NJ-4AP(KT)6-1-回风温度"},{"$f":"30000+($B103*8+F102-1)","v":30128}]
[null,16,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-4AP(KT)6-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI103=\"\",\"\",AI103)","v":"NJ-4AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-1","04F01","水阀反馈",{"$f":"AH103&\"-\"&AK103","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH103,List!$B$3:$D$445,2,FALSE)&AJ103&\"_\"&VLOOKUP(AK103,List!$K$2:$M$447,2,FALSE)","v":"AHU04F01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM103&\" \"&\"AT%I\"&B103*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J103&\"*)\",\" \")","v":"LAHU04F01_WVB AT%I258.0 :INT ; (*空调机组NJ-4AP(KT)6-1-水阀反馈*)"},"LAHU04F01_WVB           AT%I258.0      :INT ; (*空调机组NJ-4AP(KT)6-1-水阀反馈*)",null,"AHU04F01_WVB",{"$f":"J103","v":"空调机组NJ-4AP(KT)6-1-水阀反馈"},{"$f":"AS102+1","v":30129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-4AP(KT)6-2-回风温度",{"$nulls":16},"NJ-4AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-2","04F02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"AHU04F02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%I\"&B103*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LAHU04F02_RT AT%I260.0 :INT ; (*空调机组NJ-4AP(KT)6-2-回风温度*)"},"LAHU04F02_RT            AT%I260.0      :INT ; (*空调机组NJ-4AP(KT)6-2-回风温度*)",null,"AHU04F02_RT","空调机组NJ-4AP(KT)6-2-回风温度",{"$f":"AS103+1","v":30130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-4AP(KT)6-2-水阀反馈",{"$nulls":16},"NJ-4AP(KT)6-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-2","04F02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"AHU04F02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%I\"&B103*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LAHU04F02_WVB AT%I262.0 :INT ; (*空调机组NJ-4AP(KT)6-2-水阀反馈*)"},"LAHU04F02_WVB           AT%I262.0      :INT ; (*空调机组NJ-4AP(KT)6-2-水阀反馈*)",null,"AHU04F02_WVB","空调机组NJ-4AP(KT)6-2-水阀反馈",30131]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B103),REPT(0,5))),1,1))","v":1},5,null,5,"0V","空调机组NJ-4AP(KT)6-3-回风温度",{"$nulls":16},"NJ-4AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-3","04F03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":"AHU04F03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%I\"&B103*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":"LAHU04F03_RT AT%I264.0 :INT ; (*空调机组NJ-4AP(KT)6-3-回风温度*)"},"LAHU04F03_RT            AT%I264.0      :INT ; (*空调机组NJ-4AP(KT)6-3-回风温度*)",null,"AHU04F03_RT","空调机组NJ-4AP(KT)6-3-回风温度",30132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B105=20,1,IF(B105=50,10,IF(B105=125,11,IF(B105=250,100,IF(B105=500,101,IF(B105=800,110,IF(B105=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B105=20,1,IF(B105=50,10,IF(B105=125,11,IF(B105=250,100,IF(B105=500,101,IF(B105=800,110,IF(B105=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-4AP(KT)6-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI107=\"\",\"\",AI107)","v":"NJ-4AP(KT)6-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-3","04F03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH107,List!$B$3:$D$445,2,FALSE)&AJ107&\"_\"&VLOOKUP(AK107,List!$K$2:$M$447,2,FALSE)","v":"AHU04F03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM107&\" \"&\"AT%I\"&B103*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J107&\"*)\",\" \")","v":"LAHU04F03_WVB AT%I266.0 :INT ; (*空调机组NJ-4AP(KT)6-3-水阀反馈*)"},"LAHU04F03_WVB           AT%I266.0      :INT ; (*空调机组NJ-4AP(KT)6-3-水阀反馈*)",null,"AHU04F03_WVB",{"$f":"J107","v":"空调机组NJ-4AP(KT)6-3-水阀反馈"},30133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B105=20,1,IF(B105=50,10,IF(B105=125,11,IF(B105=250,100,IF(B105=500,101,IF(B105=800,110,IF(B105=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B105=20,1,IF(B105=50,10,IF(B105=125,11,IF(B105=250,100,IF(B105=500,101,IF(B105=800,110,IF(B105=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-4AP(KT)6-4-回风温度",{"$nulls":16},"NJ-4AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-4","04F04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH108,List!$B$3:$D$445,2,FALSE)&AJ108&\"_\"&VLOOKUP(AK108,List!$K$2:$M$447,2,FALSE)","v":"AHU04F04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM108&\" \"&\"AT%I\"&B103*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J108&\"*)\",\" \")","v":"LAHU04F04_RT AT%I268.0 :INT ; (*空调机组NJ-4AP(KT)6-4-回风温度*)"},"LAHU04F04_RT            AT%I268.0      :INT ; (*空调机组NJ-4AP(KT)6-4-回风温度*)",null,"AHU04F04_RT","空调机组NJ-4AP(KT)6-4-回风温度",30134]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B105=20,1,IF(B105=50,10,IF(B105=125,11,IF(B105=250,100,IF(B105=500,101,IF(B105=800,110,IF(B105=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B105=20,1,IF(B105=50,10,IF(B105=125,11,IF(B105=250,100,IF(B105=500,101,IF(B105=800,110,IF(B105=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-4AP(KT)6-4-水阀反馈",{"$nulls":16},"NJ-4AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-4","04F04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH109,List!$B$3:$D$445,2,FALSE)&AJ109&\"_\"&VLOOKUP(AK109,List!$K$2:$M$447,2,FALSE)","v":"AHU04F04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM109&\" \"&\"AT%I\"&B103*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J109&\"*)\",\" \")","v":"LAHU04F04_WVB AT%I270.0 :INT ; (*空调机组NJ-4AP(KT)6-4-水阀反馈*)"},"LAHU04F04_WVB           AT%I270.0      :INT ; (*空调机组NJ-4AP(KT)6-4-水阀反馈*)",null,"AHU04F04_WVB","空调机组NJ-4AP(KT)6-4-水阀反馈",30135]
[null,{"$f":"B115","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B115&\"地址: \"&B112&\" *)\"","v":"(* IOM 0801U地址: 17 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH111&AA111&\"-\"&AK111","v":"空调机组NJ-4AP(KT)6-5-回风温度"},{"$nulls":16},{"$f":"IF(AI111=\"\",\"\",AI111)","v":"NJ-4AP(KT)6-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL111,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL111,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-5","04F05","回风温度",{"$f":"AH111&\"-\"&AK111","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH111,List!$B$3:$D$445,2,FALSE)&AJ111&\"_\"&VLOOKUP(AK111,List!$K$2:$M$447,2,FALSE)","v":"AHU04F05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM111&\" \"&\"AT%I\"&B112*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J111&\"*)\",\" \")","v":"LAHU04F05_RT AT%I272.0 :INT ; (*空调机组NJ-4AP(KT)6-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN111,SEARCH(\"AT%\",AN111),,REPT(\" \",25-SEARCH(\"AT%\",AN111))),SEARCH(\":\",REPLACE(AN111,SEARCH(\"AT%\",AN111),,REPT(\" \",25-SEARCH(\"AT%\",AN111)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN111,SEARCH(\"AT%\",AN111),,REPT(\" \",25-SEARCH(\"AT%\",AN111)))))),\" \")","v":"LAHU04F05_RT            AT%I272.0      :INT ; (*空调机组NJ-4AP(KT)6-5-回风温度*)"},null,{"$f":"AM111","v":"AHU04F05_RT"},{"$f":"J111","v":"空调机组NJ-4AP(KT)6-5-回风温度"},{"$f":"30000+($B112*8+F111-1)","v":30136}]
[null,17,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-4AP(KT)6-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI112=\"\",\"\",AI112)","v":"NJ-4AP(KT)6-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-5","04F05","水阀反馈",{"$f":"AH112&\"-\"&AK112","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH112,List!$B$3:$D$445,2,FALSE)&AJ112&\"_\"&VLOOKUP(AK112,List!$K$2:$M$447,2,FALSE)","v":"AHU04F05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM112&\" \"&\"AT%I\"&B112*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J112&\"*)\",\" \")","v":"LAHU04F05_WVB AT%I274.0 :INT ; (*空调机组NJ-4AP(KT)6-5-水阀反馈*)"},"LAHU04F05_WVB           AT%I274.0      :INT ; (*空调机组NJ-4AP(KT)6-5-水阀反馈*)",null,"AHU04F05_WVB",{"$f":"J112","v":"空调机组NJ-4AP(KT)6-5-水阀反馈"},{"$f":"AS111+1","v":30137}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-4AP(KT)6-6-回风温度",{"$nulls":16},"NJ-4AP(KT)6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-6","04F06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH113,List!$B$3:$D$445,2,FALSE)&AJ113&\"_\"&VLOOKUP(AK113,List!$K$2:$M$447,2,FALSE)","v":"AHU04F06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM113&\" \"&\"AT%I\"&B112*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J113&\"*)\",\" \")","v":"LAHU04F06_RT AT%I276.0 :INT ; (*空调机组NJ-4AP(KT)6-6-回风温度*)"},"LAHU04F06_RT            AT%I276.0      :INT ; (*空调机组NJ-4AP(KT)6-6-回风温度*)",null,"AHU04F06_RT","空调机组NJ-4AP(KT)6-6-回风温度",{"$f":"AS112+1","v":30138}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-4AP(KT)6-6-水阀反馈",{"$nulls":16},"NJ-4AP(KT)6-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-6","04F06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH114,List!$B$3:$D$445,2,FALSE)&AJ114&\"_\"&VLOOKUP(AK114,List!$K$2:$M$447,2,FALSE)","v":"AHU04F06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM114&\" \"&\"AT%I\"&B112*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J114&\"*)\",\" \")","v":"LAHU04F06_WVB AT%I278.0 :INT ; (*空调机组NJ-4AP(KT)6-6-水阀反馈*)"},"LAHU04F06_WVB           AT%I278.0      :INT ; (*空调机组NJ-4AP(KT)6-6-水阀反馈*)",null,"AHU04F06_WVB","空调机组NJ-4AP(KT)6-6-水阀反馈",30139]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B112),REPT(0,5))),1,1))","v":1},5,null,5,"0V","空调机组NJ-4AP(KT)6-7-回风温度",{"$nulls":16},"NJ-4AP(KT)6-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-7","04F07","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH115,List!$B$3:$D$445,2,FALSE)&AJ115&\"_\"&VLOOKUP(AK115,List!$K$2:$M$447,2,FALSE)","v":"AHU04F07_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM115&\" \"&\"AT%I\"&B112*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J115&\"*)\",\" \")","v":"LAHU04F07_RT AT%I280.0 :INT ; (*空调机组NJ-4AP(KT)6-7-回风温度*)"},"LAHU04F07_RT            AT%I280.0      :INT ; (*空调机组NJ-4AP(KT)6-7-回风温度*)",null,"AHU04F07_RT","空调机组NJ-4AP(KT)6-7-回风温度",30140]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B114=20,1,IF(B114=50,10,IF(B114=125,11,IF(B114=250,100,IF(B114=500,101,IF(B114=800,110,IF(B114=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B114=20,1,IF(B114=50,10,IF(B114=125,11,IF(B114=250,100,IF(B114=500,101,IF(B114=800,110,IF(B114=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-4AP(KT)6-7-水阀反馈",{"$nulls":16},{"$f":"IF(AI116=\"\",\"\",AI116)","v":"NJ-4AP(KT)6-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-7","04F07","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH116,List!$B$3:$D$445,2,FALSE)&AJ116&\"_\"&VLOOKUP(AK116,List!$K$2:$M$447,2,FALSE)","v":"AHU04F07_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM116&\" \"&\"AT%I\"&B112*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J116&\"*)\",\" \")","v":"LAHU04F07_WVB AT%I282.0 :INT ; (*空调机组NJ-4AP(KT)6-7-水阀反馈*)"},"LAHU04F07_WVB           AT%I282.0      :INT ; (*空调机组NJ-4AP(KT)6-7-水阀反馈*)",null,"AHU04F07_WVB",{"$f":"J116","v":"空调机组NJ-4AP(KT)6-7-水阀反馈"},30141]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B114=20,1,IF(B114=50,10,IF(B114=125,11,IF(B114=250,100,IF(B114=500,101,IF(B114=800,110,IF(B114=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B114=20,1,IF(B114=50,10,IF(B114=125,11,IF(B114=250,100,IF(B114=500,101,IF(B114=800,110,IF(B114=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-4AP(KT)6-8-回风温度",{"$nulls":16},"NJ-4AP(KT)6-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL117,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL117,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-8","04F08","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH117,List!$B$3:$D$445,2,FALSE)&AJ117&\"_\"&VLOOKUP(AK117,List!$K$2:$M$447,2,FALSE)","v":"AHU04F08_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM117&\" \"&\"AT%I\"&B112*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J117&\"*)\",\" \")","v":"LAHU04F08_RT AT%I284.0 :INT ; (*空调机组NJ-4AP(KT)6-8-回风温度*)"},"LAHU04F08_RT            AT%I284.0      :INT ; (*空调机组NJ-4AP(KT)6-8-回风温度*)",null,"AHU04F08_RT","空调机组NJ-4AP(KT)6-8-回风温度",30142]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B114=20,1,IF(B114=50,10,IF(B114=125,11,IF(B114=250,100,IF(B114=500,101,IF(B114=800,110,IF(B114=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B114=20,1,IF(B114=50,10,IF(B114=125,11,IF(B114=250,100,IF(B114=500,101,IF(B114=800,110,IF(B114=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-4AP(KT)6-8-水阀反馈",{"$nulls":16},"NJ-4AP(KT)6-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL118,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL118,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-8","04F08","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH118,List!$B$3:$D$445,2,FALSE)&AJ118&\"_\"&VLOOKUP(AK118,List!$K$2:$M$447,2,FALSE)","v":"AHU04F08_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM118&\" \"&\"AT%I\"&B112*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J118&\"*)\",\" \")","v":"LAHU04F08_WVB AT%I286.0 :INT ; (*空调机组NJ-4AP(KT)6-8-水阀反馈*)"},"LAHU04F08_WVB           AT%I286.0      :INT ; (*空调机组NJ-4AP(KT)6-8-水阀反馈*)",null,"AHU04F08_WVB","空调机组NJ-4AP(KT)6-8-水阀反馈",30143]
[null,{"$f":"B124","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B124&\"地址: \"&B121&\" *)\"","v":"(* IOM 0801U地址: 18 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH120&AA120&\"-\"&AK120","v":"空调机组NJ-4AP(KT)6-9-回风温度"},{"$nulls":16},{"$f":"IF(AI120=\"\",\"\",AI120)","v":"NJ-4AP(KT)6-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL120,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL120,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-9","04F09","回风温度",{"$f":"AH120&\"-\"&AK120","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH120,List!$B$3:$D$445,2,FALSE)&AJ120&\"_\"&VLOOKUP(AK120,List!$K$2:$M$447,2,FALSE)","v":"AHU04F09_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM120&\" \"&\"AT%I\"&B121*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J120&\"*)\",\" \")","v":"LAHU04F09_RT AT%I288.0 :INT ; (*空调机组NJ-4AP(KT)6-9-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN120,SEARCH(\"AT%\",AN120),,REPT(\" \",25-SEARCH(\"AT%\",AN120))),SEARCH(\":\",REPLACE(AN120,SEARCH(\"AT%\",AN120),,REPT(\" \",25-SEARCH(\"AT%\",AN120)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN120,SEARCH(\"AT%\",AN120),,REPT(\" \",25-SEARCH(\"AT%\",AN120)))))),\" \")","v":"LAHU04F09_RT            AT%I288.0      :INT ; (*空调机组NJ-4AP(KT)6-9-回风温度*)"},null,{"$f":"AM120","v":"AHU04F09_RT"},{"$f":"J120","v":"空调机组NJ-4AP(KT)6-9-回风温度"},{"$f":"30000+($B121*8+F120-1)","v":30144}]
[null,18,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-4AP(KT)6-9-水阀反馈",{"$nulls":16},{"$f":"IF(AI121=\"\",\"\",AI121)","v":"NJ-4AP(KT)6-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-9","04F09","水阀反馈",{"$f":"AH121&\"-\"&AK121","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH121,List!$B$3:$D$445,2,FALSE)&AJ121&\"_\"&VLOOKUP(AK121,List!$K$2:$M$447,2,FALSE)","v":"AHU04F09_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM121&\" \"&\"AT%I\"&B121*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J121&\"*)\",\" \")","v":"LAHU04F09_WVB AT%I290.0 :INT ; (*空调机组NJ-4AP(KT)6-9-水阀反馈*)"},"LAHU04F09_WVB           AT%I290.0      :INT ; (*空调机组NJ-4AP(KT)6-9-水阀反馈*)",null,"AHU04F09_WVB",{"$f":"J121","v":"空调机组NJ-4AP(KT)6-9-水阀反馈"},{"$f":"AS120+1","v":30145}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),3,1))","v":0},3,null,3,"0V","室内环境状态T-05-温度状态",{"$nulls":16},"T-05",{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","T-05","04F01","温度状态","室内环境状态-温度状态",{"$f":"VLOOKUP(AH122,List!$B$3:$D$445,2,FALSE)&AJ122&\"_\"&VLOOKUP(AK122,List!$K$2:$M$447,2,FALSE)","v":"IES04F01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM122&\" \"&\"AT%I\"&B121*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J122&\"*)\",\" \")","v":"LIES04F01_T AT%I292.0 :INT ; (*室内环境状态T-05-温度状态*)"},"LIES04F01_T             AT%I292.0      :INT ; (*室内环境状态T-05-温度状态*)",null,"IES04F01_T","室内环境状态T-05-温度状态",{"$f":"AS121+1","v":30146}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),2,1))","v":0},4,null,4,"0V","室内环境状态T-06-温度状态",{"$nulls":16},"T-06",{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","T-06","04F02","温度状态","室内环境状态-温度状态",{"$f":"VLOOKUP(AH123,List!$B$3:$D$445,2,FALSE)&AJ123&\"_\"&VLOOKUP(AK123,List!$K$2:$M$447,2,FALSE)","v":"IES04F02_T"},{"$f":"_xlfn.IFNA(\"L\"&AM123&\" \"&\"AT%I\"&B121*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J123&\"*)\",\" \")","v":"LIES04F02_T AT%I294.0 :INT ; (*室内环境状态T-06-温度状态*)"},"LIES04F02_T             AT%I294.0      :INT ; (*室内环境状态T-06-温度状态*)",null,"IES04F02_T","室内环境状态T-06-温度状态",30147]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B121),REPT(0,5))),1,1))","v":1},5,null,5,"0V","风机盘管-温度状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管",null,"04F01","温度状态","风机盘管-温度状态",{"$f":"VLOOKUP(AH124,List!$B$3:$D$445,2,FALSE)&AJ124&\"_\"&VLOOKUP(AK124,List!$K$2:$M$447,2,FALSE)","v":"FCU04F01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM124&\" \"&\"AT%I\"&B121*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J124&\"*)\",\" \")","v":"LFCU04F01_T AT%I296.0 :INT ; (*风机盘管-温度状态*)"},"LFCU04F01_T             AT%I296.0      :INT ; (*风机盘管-温度状态*)",null,"FCU04F01_T","风机盘管-温度状态",30148]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B123=20,1,IF(B123=50,10,IF(B123=125,11,IF(B123=250,100,IF(B123=500,101,IF(B123=800,110,IF(B123=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B123=20,1,IF(B123=50,10,IF(B123=125,11,IF(B123=250,100,IF(B123=500,101,IF(B123=800,110,IF(B123=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","室内环境状态LUX-01-照度状态",{"$nulls":16},{"$f":"IF(AI125=\"\",\"\",AI125)","v":"LUX-01"},{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","LUX-01","04F01","照度状态","室内环境状态-照度状态",{"$f":"VLOOKUP(AH125,List!$B$3:$D$445,2,FALSE)&AJ125&\"_\"&VLOOKUP(AK125,List!$K$2:$M$447,2,FALSE)","v":"IES04F01_I"},{"$f":"_xlfn.IFNA(\"L\"&AM125&\" \"&\"AT%I\"&B121*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J125&\"*)\",\" \")","v":"LIES04F01_I AT%I298.0 :INT ; (*室内环境状态LUX-01-照度状态*)"},"LIES04F01_I             AT%I298.0      :INT ; (*室内环境状态LUX-01-照度状态*)",null,"IES04F01_I",{"$f":"J125","v":"室内环境状态LUX-01-照度状态"},30149]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B123=20,1,IF(B123=50,10,IF(B123=125,11,IF(B123=250,100,IF(B123=500,101,IF(B123=800,110,IF(B123=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B123=20,1,IF(B123=50,10,IF(B123=125,11,IF(B123=250,100,IF(B123=500,101,IF(B123=800,110,IF(B123=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","室内环境状态CO2-04-二氧化碳浓度状态",{"$nulls":16},"CO2-04",{"$f":"_xlfn.IFNA(VLOOKUP(AL126,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL126,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","CO2-04","04F01","二氧化碳浓度状态","室内环境状态-二氧化碳浓度状态",{"$f":"VLOOKUP(AH126,List!$B$3:$D$445,2,FALSE)&AJ126&\"_\"&VLOOKUP(AK126,List!$K$2:$M$447,2,FALSE)","v":"IES04F01_CO2"},{"$f":"_xlfn.IFNA(\"L\"&AM126&\" \"&\"AT%I\"&B121*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J126&\"*)\",\" \")","v":"LIES04F01_CO2 AT%I300.0 :INT ; (*室内环境状态CO2-04-二氧化碳浓度状态*)"},"LIES04F01_CO2           AT%I300.0      :INT ; (*室内环境状态CO2-04-二氧化碳浓度状态*)",null,"IES04F01_CO2","室内环境状态CO2-04-二氧化碳浓度状态",30150]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B123=20,1,IF(B123=50,10,IF(B123=125,11,IF(B123=250,100,IF(B123=500,101,IF(B123=800,110,IF(B123=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B123=20,1,IF(B123=50,10,IF(B123=125,11,IF(B123=250,100,IF(B123=500,101,IF(B123=800,110,IF(B123=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL127,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL127,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH127,List!$B$3:$D$445,2,FALSE)&AJ127&\"_\"&VLOOKUP(AK127,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM127&\" \"&\"AT%I\"&B121*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J127&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30151]
[null,{"$f":"B133","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B133&\"地址: \"&B130&\" *)\"","v":"(* IOM 0401A地址: 19 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH129&AA129&\"-\"&AK129","v":"空调机组NJ-4AP(KT)6-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI129=\"\",\"\",AI129)","v":"NJ-4AP(KT)6-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL129,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL129,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-1","04F01","水阀控制",{"$f":"AH129&\"-\"&AK129","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH129,List!$B$3:$D$445,2,FALSE)&AJ129&\"_\"&VLOOKUP(AK129,List!$K$2:$M$447,2,FALSE)","v":"AHU04F01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM129&\" \"&\"AT%Q\"&B130*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J129&\"*)\",\" \")","v":"LAHU04F01_WVC AT%Q304.0 :INT ; (*空调机组NJ-4AP(KT)6-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN129,SEARCH(\"AT%\",AN129),,REPT(\" \",25-SEARCH(\"AT%\",AN129))),SEARCH(\":\",REPLACE(AN129,SEARCH(\"AT%\",AN129),,REPT(\" \",25-SEARCH(\"AT%\",AN129)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN129,SEARCH(\"AT%\",AN129),,REPT(\" \",25-SEARCH(\"AT%\",AN129)))))),\" \")","v":"LAHU04F01_WVC           AT%Q304.0      :INT ; (*空调机组NJ-4AP(KT)6-1-水阀控制*)"},null,{"$f":"AM129","v":"AHU04F01_WVC"},{"$f":"J129","v":"空调机组NJ-4AP(KT)6-1-水阀控制"},{"$f":"40000+($B130*8+F129-1)","v":40152}]
[null,19,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH130&AA130&\"-\"&AK130","v":"空调机组NJ-4AP(KT)6-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI130=\"\",\"\",AI130)","v":"NJ-4AP(KT)6-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL130,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL130,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-2","04F02","水阀控制",{"$f":"AH130&\"-\"&AK130","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH130,List!$B$3:$D$445,2,FALSE)&AJ130&\"_\"&VLOOKUP(AK130,List!$K$2:$M$447,2,FALSE)","v":"AHU04F02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM130&\" \"&\"AT%Q\"&B130*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J130&\"*)\",\" \")","v":"LAHU04F02_WVC AT%Q306.0 :INT ; (*空调机组NJ-4AP(KT)6-2-水阀控制*)"},"LAHU04F02_WVC           AT%Q306.0      :INT ; (*空调机组NJ-4AP(KT)6-2-水阀控制*)",null,"AHU04F02_WVC",{"$f":"J130","v":"空调机组NJ-4AP(KT)6-2-水阀控制"},{"$f":"AS129+1","v":40153}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH131&AA131&\"-\"&AK131","v":"空调机组NJ-4AP(KT)6-3-水阀控制"},{"$nulls":16},"NJ-4AP(KT)6-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL131,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL131,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-3","04F03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH131,List!$B$3:$D$445,2,FALSE)&AJ131&\"_\"&VLOOKUP(AK131,List!$K$2:$M$447,2,FALSE)","v":"AHU04F03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM131&\" \"&\"AT%Q\"&B130*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J131&\"*)\",\" \")","v":"LAHU04F03_WVC AT%Q308.0 :INT ; (*空调机组NJ-4AP(KT)6-3-水阀控制*)"},"LAHU04F03_WVC           AT%Q308.0      :INT ; (*空调机组NJ-4AP(KT)6-3-水阀控制*)",null,"AHU04F03_WVC","空调机组NJ-4AP(KT)6-3-水阀控制",{"$f":"AS130+1","v":40154}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH132&AA132&\"-\"&AK132","v":"空调机组NJ-4AP(KT)6-4-水阀控制"},{"$nulls":16},"NJ-4AP(KT)6-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL132,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL132,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-4","04F04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH132,List!$B$3:$D$445,2,FALSE)&AJ132&\"_\"&VLOOKUP(AK132,List!$K$2:$M$447,2,FALSE)","v":"AHU04F04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM132&\" \"&\"AT%Q\"&B130*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J132&\"*)\",\" \")","v":"LAHU04F04_WVC AT%Q310.0 :INT ; (*空调机组NJ-4AP(KT)6-4-水阀控制*)"},"LAHU04F04_WVC           AT%Q310.0      :INT ; (*空调机组NJ-4AP(KT)6-4-水阀控制*)",null,"AHU04F04_WVC","空调机组NJ-4AP(KT)6-4-水阀控制",40155]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B130),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B132=20,1,IF(B132=50,10,IF(B132=125,11,IF(B132=250,100,IF(B132=500,101,IF(B132=800,110,IF(B132=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B132=20,1,IF(B132=50,10,IF(B132=125,11,IF(B132=250,100,IF(B132=500,101,IF(B132=800,110,IF(B132=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B132=20,1,IF(B132=50,10,IF(B132=125,11,IF(B132=250,100,IF(B132=500,101,IF(B132=800,110,IF(B132=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B132=20,1,IF(B132=50,10,IF(B132=125,11,IF(B132=250,100,IF(B132=500,101,IF(B132=800,110,IF(B132=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B132=20,1,IF(B132=50,10,IF(B132=125,11,IF(B132=250,100,IF(B132=500,101,IF(B132=800,110,IF(B132=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B132=20,1,IF(B132=50,10,IF(B132=125,11,IF(B132=250,100,IF(B132=500,101,IF(B132=800,110,IF(B132=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B142","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B142&\"地址: \"&B139&\" *)\"","v":"(* IOM 0401A地址: 20 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH138&AA138&\"-\"&AK138","v":"空调机组NJ-4AP(KT)6-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI138=\"\",\"\",AI138)","v":"NJ-4AP(KT)6-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL138,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL138,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-5","04F05","水阀控制",{"$f":"AH138&\"-\"&AK138","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH138,List!$B$3:$D$445,2,FALSE)&AJ138&\"_\"&VLOOKUP(AK138,List!$K$2:$M$447,2,FALSE)","v":"AHU04F05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM138&\" \"&\"AT%Q\"&B139*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J138&\"*)\",\" \")","v":"LAHU04F05_WVC AT%Q320.0 :INT ; (*空调机组NJ-4AP(KT)6-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN138,SEARCH(\"AT%\",AN138),,REPT(\" \",25-SEARCH(\"AT%\",AN138))),SEARCH(\":\",REPLACE(AN138,SEARCH(\"AT%\",AN138),,REPT(\" \",25-SEARCH(\"AT%\",AN138)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN138,SEARCH(\"AT%\",AN138),,REPT(\" \",25-SEARCH(\"AT%\",AN138)))))),\" \")","v":"LAHU04F05_WVC           AT%Q320.0      :INT ; (*空调机组NJ-4AP(KT)6-5-水阀控制*)"},null,{"$f":"AM138","v":"AHU04F05_WVC"},{"$f":"J138","v":"空调机组NJ-4AP(KT)6-5-水阀控制"},{"$f":"40000+($B139*8+F138-1)","v":40160}]
[null,20,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH139&AA139&\"-\"&AK139","v":"空调机组NJ-4AP(KT)6-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI139=\"\",\"\",AI139)","v":"NJ-4AP(KT)6-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL139,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL139,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-6","04F06","水阀控制",{"$f":"AH139&\"-\"&AK139","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH139,List!$B$3:$D$445,2,FALSE)&AJ139&\"_\"&VLOOKUP(AK139,List!$K$2:$M$447,2,FALSE)","v":"AHU04F06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM139&\" \"&\"AT%Q\"&B139*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J139&\"*)\",\" \")","v":"LAHU04F06_WVC AT%Q322.0 :INT ; (*空调机组NJ-4AP(KT)6-6-水阀控制*)"},"LAHU04F06_WVC           AT%Q322.0      :INT ; (*空调机组NJ-4AP(KT)6-6-水阀控制*)",null,"AHU04F06_WVC",{"$f":"J139","v":"空调机组NJ-4AP(KT)6-6-水阀控制"},{"$f":"AS138+1","v":40161}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH140&AA140&\"-\"&AK140","v":"空调机组NJ-4AP(KT)6-7-水阀控制"},{"$nulls":16},"NJ-4AP(KT)6-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL140,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL140,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-7","04F07","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH140,List!$B$3:$D$445,2,FALSE)&AJ140&\"_\"&VLOOKUP(AK140,List!$K$2:$M$447,2,FALSE)","v":"AHU04F07_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM140&\" \"&\"AT%Q\"&B139*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J140&\"*)\",\" \")","v":"LAHU04F07_WVC AT%Q324.0 :INT ; (*空调机组NJ-4AP(KT)6-7-水阀控制*)"},"LAHU04F07_WVC           AT%Q324.0      :INT ; (*空调机组NJ-4AP(KT)6-7-水阀控制*)",null,"AHU04F07_WVC","空调机组NJ-4AP(KT)6-7-水阀控制",{"$f":"AS139+1","v":40162}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH141&AA141&\"-\"&AK141","v":"空调机组NJ-4AP(KT)6-8-水阀控制"},{"$nulls":16},"NJ-4AP(KT)6-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL141,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL141,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-8","04F08","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH141,List!$B$3:$D$445,2,FALSE)&AJ141&\"_\"&VLOOKUP(AK141,List!$K$2:$M$447,2,FALSE)","v":"AHU04F08_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM141&\" \"&\"AT%Q\"&B139*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J141&\"*)\",\" \")","v":"LAHU04F08_WVC AT%Q326.0 :INT ; (*空调机组NJ-4AP(KT)6-8-水阀控制*)"},"LAHU04F08_WVC           AT%Q326.0      :INT ; (*空调机组NJ-4AP(KT)6-8-水阀控制*)",null,"AHU04F08_WVC","空调机组NJ-4AP(KT)6-8-水阀控制",40163]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B139),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B141=20,1,IF(B141=50,10,IF(B141=125,11,IF(B141=250,100,IF(B141=500,101,IF(B141=800,110,IF(B141=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B141=20,1,IF(B141=50,10,IF(B141=125,11,IF(B141=250,100,IF(B141=500,101,IF(B141=800,110,IF(B141=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B141=20,1,IF(B141=50,10,IF(B141=125,11,IF(B141=250,100,IF(B141=500,101,IF(B141=800,110,IF(B141=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B141=20,1,IF(B141=50,10,IF(B141=125,11,IF(B141=250,100,IF(B141=500,101,IF(B141=800,110,IF(B141=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B141=20,1,IF(B141=50,10,IF(B141=125,11,IF(B141=250,100,IF(B141=500,101,IF(B141=800,110,IF(B141=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B141=20,1,IF(B141=50,10,IF(B141=125,11,IF(B141=250,100,IF(B141=500,101,IF(B141=800,110,IF(B141=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B151","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B151&\"地址: \"&B148&\" *)\"","v":"(* IOM 0401A地址: 21 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH147&AA147&\"-\"&AK147","v":"空调机组NJ-4AP(KT)6-9-水阀控制"},{"$nulls":16},{"$f":"IF(AI147=\"\",\"\",AI147)","v":"NJ-4AP(KT)6-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL147,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL147,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)6-9","04F09","水阀控制",{"$f":"AH147&\"-\"&AK147","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH147,List!$B$3:$D$445,2,FALSE)&AJ147&\"_\"&VLOOKUP(AK147,List!$K$2:$M$447,2,FALSE)","v":"AHU04F09_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM147&\" \"&\"AT%Q\"&B148*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J147&\"*)\",\" \")","v":"LAHU04F09_WVC AT%Q336.0 :INT ; (*空调机组NJ-4AP(KT)6-9-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN147,SEARCH(\"AT%\",AN147),,REPT(\" \",25-SEARCH(\"AT%\",AN147))),SEARCH(\":\",REPLACE(AN147,SEARCH(\"AT%\",AN147),,REPT(\" \",25-SEARCH(\"AT%\",AN147)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN147,SEARCH(\"AT%\",AN147),,REPT(\" \",25-SEARCH(\"AT%\",AN147)))))),\" \")","v":"LAHU04F09_WVC           AT%Q336.0      :INT ; (*空调机组NJ-4AP(KT)6-9-水阀控制*)"},null,{"$f":"AM147","v":"AHU04F09_WVC"},{"$f":"J147","v":"空调机组NJ-4AP(KT)6-9-水阀控制"},{"$f":"40000+($B148*8+F147-1)","v":40168}]
[null,21,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH148&AA148&\"-\"&AK148","v":"-"},{"$nulls":16},{"$f":"IF(AI148=\"\",\"\",AI148)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL148,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL148,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},{"$f":"AH148&\"-\"&AK148","v":"-"},{"$f":"VLOOKUP(AH148,List!$B$3:$D$445,2,FALSE)&AJ148&\"_\"&VLOOKUP(AK148,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM148&\" \"&\"AT%Q\"&B148*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J148&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J148","v":"-"},{"$f":"AS147+1","v":40169}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH149&AA149&\"-\"&AK149","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL149,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL149,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH149,List!$B$3:$D$445,2,FALSE)&AJ149&\"_\"&VLOOKUP(AK149,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM149&\" \"&\"AT%Q\"&B148*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J149&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS148+1","v":40170}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH150&AA150&\"-\"&AK150","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL150,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL150,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH150,List!$B$3:$D$445,2,FALSE)&AJ150&\"_\"&VLOOKUP(AK150,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM150&\" \"&\"AT%Q\"&B148*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J150&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40171]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B148),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B150=20,1,IF(B150=50,10,IF(B150=125,11,IF(B150=250,100,IF(B150=500,101,IF(B150=800,110,IF(B150=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B150=20,1,IF(B150=50,10,IF(B150=125,11,IF(B150=250,100,IF(B150=500,101,IF(B150=800,110,IF(B150=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B150=20,1,IF(B150=50,10,IF(B150=125,11,IF(B150=250,100,IF(B150=500,101,IF(B150=800,110,IF(B150=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B150=20,1,IF(B150=50,10,IF(B150=125,11,IF(B150=250,100,IF(B150=500,101,IF(B150=800,110,IF(B150=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B150=20,1,IF(B150=50,10,IF(B150=125,11,IF(B150=250,100,IF(B150=500,101,IF(B150=800,110,IF(B150=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B150=20,1,IF(B150=50,10,IF(B150=125,11,IF(B150=250,100,IF(B150=500,101,IF(B150=800,110,IF(B150=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L501","index":38,"n_rows":42,"n_cols":45,"rows_kept":42,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[41,5,41,6],[41,9,41,25],[4,1,5,1],[11,1,14,1],[20,1,23,1],[29,1,32,1],[38,1,41,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L01",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.0801R D7",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 0801R地址: 22 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH8&AA8&\"-\"&AK8","v":"F新风机组NJ-5AP(KT)6-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-5AP(KT)6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)6","05A01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"F新风机组-运行状态"},{"$f":"VLOOKUP(AH8,[1]List!$D$3:$F$527,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05A01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LFAU05A01_R AT%I352.0 :BOOL; (*F新风机组NJ-5AP(KT)6-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",30-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",30-SEARCH(\"AT%\",AN8)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LFAU05A01_R                  AT%I352.0 :BOOL; (*F新风机组NJ-5AP(KT)6-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L01\\L01FAU05A01_R"},{"$f":"J8","v":"F新风机组NJ-5AP(KT)6-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":12816}]
[null,22,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},2,null,2,"C","F新风机组NJ-5AP(KT)6-故障状态",{"$nulls":16},"NJ-5AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)6","05A01","故障状态","F新风机组-故障状态",{"$f":"VLOOKUP(AH9,[1]List!$D$3:$F$527,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05A01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LFAU05A01_F AT%I352.1 :BOOL; (*F新风机组NJ-5AP(KT)6-故障状态*)"},"LFAU05A01_F                  AT%I352.1 :BOOL; (*F新风机组NJ-5AP(KT)6-故障状态*)",null,"L01\\L01FAU05A01_F","F新风机组NJ-5AP(KT)6-故障状态",{"$f":"AS8+1","v":12817}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},3,null,3,"C","F新风机组NJ-5AP(KT)6-自动状态",{"$nulls":16},"NJ-5AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)6","05A01","自动状态","F新风机组-自动状态",{"$f":"VLOOKUP(AH10,[1]List!$D$3:$F$527,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05A01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LFAU05A01_A AT%I352.2 :BOOL; (*F新风机组NJ-5AP(KT)6-自动状态*)"},"LFAU05A01_A                  AT%I352.2 :BOOL; (*F新风机组NJ-5AP(KT)6-自动状态*)",null,"L01\\L01FAU05A01_A","F新风机组NJ-5AP(KT)6-自动状态",12818]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},4,null,4,"C","F新风机组NJ-5AP(KT)6-风机压差",{"$nulls":16},"NJ-5AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)6","05A01","风机压差","F新风机组-风机压差",{"$f":"VLOOKUP(AH11,[1]List!$D$3:$F$527,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05A01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LFAU05A01_FPS AT%I352.3 :BOOL; (*F新风机组NJ-5AP(KT)6-风机压差*)"},"LFAU05A01_FPS                AT%I352.3 :BOOL; (*F新风机组NJ-5AP(KT)6-风机压差*)",null,"L01\\L01FAU05A01_FPS","F新风机组NJ-5AP(KT)6-风机压差",12819]
[null,"IOM 0801R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},5,null,5,"C","F新风机组NJ-5AP(KT)6-初效滤网压差",{"$nulls":16},"NJ-5AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)6","05A01","初效滤网压差","F新风机组-初效滤网压差",{"$f":"VLOOKUP(AH12,[1]List!$D$3:$F$527,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05A01_IPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LFAU05A01_IPS AT%I352.4 :BOOL; (*F新风机组NJ-5AP(KT)6-初效滤网压差*)"},"LFAU05A01_IPS                AT%I352.4 :BOOL; (*F新风机组NJ-5AP(KT)6-初效滤网压差*)",null,"L01\\L01FAU05A01_IPS","F新风机组NJ-5AP(KT)6-初效滤网压差",12820]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","F新风机组NJ-5AP(KT)6-低温断路开关",{"$nulls":16},"NJ-5AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)6","05A01","低温断路开关","F新风机组-低温断路开关",{"$f":"VLOOKUP(AH13,[1]List!$D$3:$F$527,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05A01_AFS"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LFAU05A01_AFS AT%I352.5 :BOOL; (*F新风机组NJ-5AP(KT)6-低温断路开关*)"},"LFAU05A01_AFS                AT%I352.5 :BOOL; (*F新风机组NJ-5AP(KT)6-低温断路开关*)",null,"L01\\L01FAU05A01_AFS","F新风机组NJ-5AP(KT)6-低温断路开关",12821]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","F新风机组NJ-5AP(KT)6-新风阀开状态",{"$nulls":16},"NJ-5AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)6","05A01","新风阀开状态","F新风机组-新风阀开状态",{"$f":"VLOOKUP(AH14,[1]List!$D$3:$F$527,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05A01_FDOB"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LFAU05A01_FDOB AT%I352.6 :BOOL; (*F新风机组NJ-5AP(KT)6-新风阀开状态*)"},"LFAU05A01_FDOB               AT%I352.6 :BOOL; (*F新风机组NJ-5AP(KT)6-新风阀开状态*)",null,"L01\\L01FAU05A01_FDOB","F新风机组NJ-5AP(KT)6-新风阀开状态",12822]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","F新风机组NJ-5AP(KT)6-新风阀关状态",{"$nulls":16},"NJ-5AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)6","05A01","新风阀关状态","F新风机组-新风阀关状态",{"$f":"VLOOKUP(AH15,[1]List!$D$3:$F$527,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05A01_FDSB"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LFAU05A01_FDSB AT%I352.7 :BOOL; (*F新风机组NJ-5AP(KT)6-新风阀关状态*)"},"LFAU05A01_FDSB               AT%I352.7 :BOOL; (*F新风机组NJ-5AP(KT)6-新风阀关状态*)",null,"L01\\L01FAU05A01_FDSB","F新风机组NJ-5AP(KT)6-新风阀关状态",12823]
[null,{"$f":"B21","v":"IOM 0801D"},{"$nulls":38},{"$f":"\"(* \"&B21&\"地址: \"&B18&\" *)\"","v":"(* IOM 0801D地址: 23 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH17&AA17&\"-\"&AK17","v":"F新风机组NJ-5AP(KT)6-启停控制"},{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-5AP(KT)6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)6","05A01","启停控制",{"$f":"AH17&\"-\"&AK17","v":"F新风机组-启停控制"},{"$f":"VLOOKUP(AH17,[1]List!$D$3:$F$527,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%Q\"&B18*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LFAU05A01_C AT%Q368.0 :BOOL; (*F新风机组NJ-5AP(KT)6-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",30-SEARCH(\"AT%\",AN17))),SEARCH(\":\",REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",30-SEARCH(\"AT%\",AN17)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",25-SEARCH(\"AT%\",AN17)))))),\" \")","v":"LFAU05A01_C                  AT%Q368.0 :BOOL; (*F新风机组NJ-5AP(KT)6-启停控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM17","v":"L01\\L01FAU05A01_C"},{"$f":"J17","v":"F新风机组NJ-5AP(KT)6-启停控制"},{"$f":"($B18*16*8+F17-1)","v":2944}]
[null,23,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","F新风机组NJ-5AP(KT)6-新风阀开控制",{"$nulls":16},"NJ-5AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)6","05A01","新风阀开控制","F新风机组-新风阀开控制",{"$f":"VLOOKUP(AH18,[1]List!$D$3:$F$527,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05A01_FDOC"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%Q\"&B18*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LFAU05A01_FDOC AT%Q368.1 :BOOL; (*F新风机组NJ-5AP(KT)6-新风阀开控制*)"},"LFAU05A01_FDOC               AT%Q368.1 :BOOL; (*F新风机组NJ-5AP(KT)6-新风阀开控制*)",null,"L01\\L01FAU05A01_FDOC","F新风机组NJ-5AP(KT)6-新风阀开控制",{"$f":"AS17+1","v":2945}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","F新风机组NJ-5AP(KT)6-新风阀关控制",{"$nulls":16},"NJ-5AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)6","05A01","新风阀关控制","F新风机组-新风阀关控制",{"$f":"VLOOKUP(AH19,[1]List!$D$3:$F$527,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05A01_FDSC"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%Q\"&B18*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LFAU05A01_FDSC AT%Q368.2 :BOOL; (*F新风机组NJ-5AP(KT)6-新风阀关控制*)"},"LFAU05A01_FDSC               AT%Q368.2 :BOOL; (*F新风机组NJ-5AP(KT)6-新风阀关控制*)",null,"L01\\L01FAU05A01_FDSC","F新风机组NJ-5AP(KT)6-新风阀关控制",2946]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH20,[1]List!$D$3:$F$527,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%Q\"&B18*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2947]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),1,1))","v":1},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH21,[1]List!$D$3:$F$527,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%Q\"&B18*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2948]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH22,[1]List!$D$3:$F$527,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%Q\"&B18*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2949]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH23,[1]List!$D$3:$F$527,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%Q\"&B18*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2950]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH24,[1]List!$D$3:$F$527,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%Q\"&B18*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2951]
[null,{"$f":"B30","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 0401U地址: 24 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH26&AA26&\"-\"&AK26","v":"F新风机组NJ-5AP(KT)6-送风温度"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-5AP(KT)6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)6","05A01","送风温度",{"$f":"AH26&\"-\"&AK26","v":"F新风机组-送风温度"},{"$f":"VLOOKUP(AH26,[1]List!$D$3:$F$527,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05A01_ST"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LFAU05A01_ST AT%I384.0 :INT; (*F新风机组NJ-5AP(KT)6-送风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",30-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",30-SEARCH(\"AT%\",AN26)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LFAU05A01_ST                 AT%I384.0 :INT; (*F新风机组NJ-5AP(KT)6-送风温度*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L01\\L01FAU05A01_ST"},{"$f":"J26","v":"F新风机组NJ-5AP(KT)6-送风温度"},{"$f":"30000+($B27*8+F26-1)","v":30192}]
[null,24,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,2,"0V","F新风机组NJ-5AP(KT)6-水阀反馈",{"$nulls":16},"NJ-5AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)6","05A01","水阀反馈","F新风机组-水阀反馈",{"$f":"VLOOKUP(AH27,[1]List!$D$3:$F$527,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05A01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LFAU05A01_WVB AT%I386.0 :INT; (*F新风机组NJ-5AP(KT)6-水阀反馈*)"},"LFAU05A01_WVB                AT%I386.0 :INT; (*F新风机组NJ-5AP(KT)6-水阀反馈*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM27","v":"L01\\L01FAU05A01_WVB"},"F新风机组NJ-5AP(KT)6-水阀反馈",{"$f":"AS26+1","v":30193}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,3,"0V","F新风机组NJ-5AP(KT)6-变频器频率反馈",{"$nulls":16},"NJ-5AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)6","05A01","变频器频率反馈","F新风机组-变频器频率反馈",{"$f":"VLOOKUP(AH28,[1]List!$D$3:$F$527,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05A01_VFB"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LFAU05A01_VFB AT%I388.0 :INT; (*F新风机组NJ-5AP(KT)6-变频器频率反馈*)"},"LFAU05A01_VFB                AT%I388.0 :INT; (*F新风机组NJ-5AP(KT)6-变频器频率反馈*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM28","v":"L01\\L01FAU05A01_VFB"},"F新风机组NJ-5AP(KT)6-变频器频率反馈",30194]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":1},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH29,[1]List!$D$3:$F$527,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM29","v":{"$error":"#N/A"}},"-",30195]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":1}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B39","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B39&\"地址: \"&B36&\" *)\"","v":"(* IOM 0401A地址: 25 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH35&AA35&\"-\"&AK35","v":"F新风机组NJ-5AP(KT)6-水阀控制"},{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-5AP(KT)6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)6","05A01","水阀控制",{"$f":"AH35&\"-\"&AK35","v":"F新风机组-水阀控制"},{"$f":"VLOOKUP(AH35,[1]List!$D$3:$F$527,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05A01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%Q\"&B36*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LFAU05A01_WVC AT%Q400.0 :INT; (*F新风机组NJ-5AP(KT)6-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",30-SEARCH(\"AT%\",AN35))),SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",30-SEARCH(\"AT%\",AN35)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35)))))),\" \")","v":"LFAU05A01_WVC                AT%Q400.0 :INT; (*F新风机组NJ-5AP(KT)6-水阀控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM35","v":"L01\\L01FAU05A01_WVC"},{"$f":"J35","v":"F新风机组NJ-5AP(KT)6-水阀控制"},{"$f":"40000+($B36*8+F35-1)","v":40200}]
[null,25,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":0},2,null,3,4,"F新风机组NJ-5AP(KT)6-变频器频率控制",{"$nulls":16},"NJ-5AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)6","05A01","变频器频率控制","F新风机组-变频器频率控制",{"$f":"VLOOKUP(AH36,[1]List!$D$3:$F$527,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05A01_VFC"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%Q\"&B36*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LFAU05A01_VFC AT%Q402.0 :INT; (*F新风机组NJ-5AP(KT)6-变频器频率控制*)"},"LFAU05A01_VFC                AT%Q402.0 :INT; (*F新风机组NJ-5AP(KT)6-变频器频率控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM36","v":"L01\\L01FAU05A01_VFC"},"F新风机组NJ-5AP(KT)6-变频器频率控制",{"$f":"AS35+1","v":40201}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":0},3,null,5,6,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH37,[1]List!$D$3:$F$527,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%Q\"&B36*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM37","v":{"$error":"#N/A"}},"-",40202]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":1},4,null,7,8,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH38,[1]List!$D$3:$F$527,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%Q\"&B36*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM38","v":{"$error":"#N/A"}},"-",40203]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L601","index":39,"n_rows":42,"n_cols":45,"rows_kept":42,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[41,5,41,6],[41,9,41,25],[4,1,5,1],[11,1,14,1],[20,1,23,1],[29,1,32,1],[38,1,41,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L01",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.0801R D7",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 0801R地址: 26 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH8&AA8&\"-\"&AK8","v":"F新风机组NJ-6AP(KT)6-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-6AP(KT)6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-6AP(KT)6","06A01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"F新风机组-运行状态"},{"$f":"VLOOKUP(AH8,[1]List!$D$3:$F$527,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU06A01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LFAU06A01_R AT%I416.0 :BOOL; (*F新风机组NJ-6AP(KT)6-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",30-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",30-SEARCH(\"AT%\",AN8)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LFAU06A01_R                  AT%I416.0 :BOOL; (*F新风机组NJ-6AP(KT)6-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L01\\L01FAU06A01_R"},{"$f":"J8","v":"F新风机组NJ-6AP(KT)6-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":13328}]
[null,26,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},2,null,2,"C","F新风机组NJ-6AP(KT)6-故障状态",{"$nulls":16},"NJ-6AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-6AP(KT)6","06A01","故障状态","F新风机组-故障状态",{"$f":"VLOOKUP(AH9,[1]List!$D$3:$F$527,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU06A01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LFAU06A01_F AT%I416.1 :BOOL; (*F新风机组NJ-6AP(KT)6-故障状态*)"},"LFAU06A01_F                  AT%I416.1 :BOOL; (*F新风机组NJ-6AP(KT)6-故障状态*)",null,"L01\\L01FAU06A01_F","F新风机组NJ-6AP(KT)6-故障状态",{"$f":"AS8+1","v":13329}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},3,null,3,"C","F新风机组NJ-6AP(KT)6-自动状态",{"$nulls":16},"NJ-6AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-6AP(KT)6","06A01","自动状态","F新风机组-自动状态",{"$f":"VLOOKUP(AH10,[1]List!$D$3:$F$527,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU06A01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LFAU06A01_A AT%I416.2 :BOOL; (*F新风机组NJ-6AP(KT)6-自动状态*)"},"LFAU06A01_A                  AT%I416.2 :BOOL; (*F新风机组NJ-6AP(KT)6-自动状态*)",null,"L01\\L01FAU06A01_A","F新风机组NJ-6AP(KT)6-自动状态",13330]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},4,null,4,"C","F新风机组NJ-6AP(KT)6-风机压差",{"$nulls":16},"NJ-6AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-6AP(KT)6","06A01","风机压差","F新风机组-风机压差",{"$f":"VLOOKUP(AH11,[1]List!$D$3:$F$527,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU06A01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LFAU06A01_FPS AT%I416.3 :BOOL; (*F新风机组NJ-6AP(KT)6-风机压差*)"},"LFAU06A01_FPS                AT%I416.3 :BOOL; (*F新风机组NJ-6AP(KT)6-风机压差*)",null,"L01\\L01FAU06A01_FPS","F新风机组NJ-6AP(KT)6-风机压差",13331]
[null,"IOM 0801R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},5,null,5,"C","F新风机组NJ-6AP(KT)6-初效滤网压差",{"$nulls":16},"NJ-6AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-6AP(KT)6","06A01","初效滤网压差","F新风机组-初效滤网压差",{"$f":"VLOOKUP(AH12,[1]List!$D$3:$F$527,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU06A01_IPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LFAU06A01_IPS AT%I416.4 :BOOL; (*F新风机组NJ-6AP(KT)6-初效滤网压差*)"},"LFAU06A01_IPS                AT%I416.4 :BOOL; (*F新风机组NJ-6AP(KT)6-初效滤网压差*)",null,"L01\\L01FAU06A01_IPS","F新风机组NJ-6AP(KT)6-初效滤网压差",13332]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","F新风机组NJ-6AP(KT)6-低温断路开关",{"$nulls":16},"NJ-6AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-6AP(KT)6","06A01","低温断路开关","F新风机组-低温断路开关",{"$f":"VLOOKUP(AH13,[1]List!$D$3:$F$527,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU06A01_AFS"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LFAU06A01_AFS AT%I416.5 :BOOL; (*F新风机组NJ-6AP(KT)6-低温断路开关*)"},"LFAU06A01_AFS                AT%I416.5 :BOOL; (*F新风机组NJ-6AP(KT)6-低温断路开关*)",null,"L01\\L01FAU06A01_AFS","F新风机组NJ-6AP(KT)6-低温断路开关",13333]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","F新风机组NJ-6AP(KT)6-新风阀开状态",{"$nulls":16},"NJ-6AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-6AP(KT)6","06A01","新风阀开状态","F新风机组-新风阀开状态",{"$f":"VLOOKUP(AH14,[1]List!$D$3:$F$527,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU06A01_FDOB"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LFAU06A01_FDOB AT%I416.6 :BOOL; (*F新风机组NJ-6AP(KT)6-新风阀开状态*)"},"LFAU06A01_FDOB               AT%I416.6 :BOOL; (*F新风机组NJ-6AP(KT)6-新风阀开状态*)",null,"L01\\L01FAU06A01_FDOB","F新风机组NJ-6AP(KT)6-新风阀开状态",13334]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","F新风机组NJ-6AP(KT)6-新风阀关状态",{"$nulls":16},"NJ-6AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-6AP(KT)6","06A01","新风阀关状态","F新风机组-新风阀关状态",{"$f":"VLOOKUP(AH15,[1]List!$D$3:$F$527,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU06A01_FDSB"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LFAU06A01_FDSB AT%I416.7 :BOOL; (*F新风机组NJ-6AP(KT)6-新风阀关状态*)"},"LFAU06A01_FDSB               AT%I416.7 :BOOL; (*F新风机组NJ-6AP(KT)6-新风阀关状态*)",null,"L01\\L01FAU06A01_FDSB","F新风机组NJ-6AP(KT)6-新风阀关状态",13335]
[null,{"$f":"B21","v":"IOM 0801D"},{"$nulls":38},{"$f":"\"(* \"&B21&\"地址: \"&B18&\" *)\"","v":"(* IOM 0801D地址: 27 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH17&AA17&\"-\"&AK17","v":"F新风机组NJ-6AP(KT)6-启停控制"},{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-6AP(KT)6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-6AP(KT)6","06A01","启停控制",{"$f":"AH17&\"-\"&AK17","v":"F新风机组-启停控制"},{"$f":"VLOOKUP(AH17,[1]List!$D$3:$F$527,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU06A01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%Q\"&B18*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LFAU06A01_C AT%Q432.0 :BOOL; (*F新风机组NJ-6AP(KT)6-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",30-SEARCH(\"AT%\",AN17))),SEARCH(\":\",REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",30-SEARCH(\"AT%\",AN17)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",25-SEARCH(\"AT%\",AN17)))))),\" \")","v":"LFAU06A01_C                  AT%Q432.0 :BOOL; (*F新风机组NJ-6AP(KT)6-启停控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM17","v":"L01\\L01FAU06A01_C"},{"$f":"J17","v":"F新风机组NJ-6AP(KT)6-启停控制"},{"$f":"($B18*16*8+F17-1)","v":3456}]
[null,27,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","F新风机组NJ-6AP(KT)6-新风阀开控制",{"$nulls":16},"NJ-6AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-6AP(KT)6","06A01","新风阀开控制","F新风机组-新风阀开控制",{"$f":"VLOOKUP(AH18,[1]List!$D$3:$F$527,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU06A01_FDOC"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%Q\"&B18*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LFAU06A01_FDOC AT%Q432.1 :BOOL; (*F新风机组NJ-6AP(KT)6-新风阀开控制*)"},"LFAU06A01_FDOC               AT%Q432.1 :BOOL; (*F新风机组NJ-6AP(KT)6-新风阀开控制*)",null,"L01\\L01FAU06A01_FDOC","F新风机组NJ-6AP(KT)6-新风阀开控制",{"$f":"AS17+1","v":3457}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","F新风机组NJ-6AP(KT)6-新风阀关控制",{"$nulls":16},"NJ-6AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-6AP(KT)6","06A01","新风阀关控制","F新风机组-新风阀关控制",{"$f":"VLOOKUP(AH19,[1]List!$D$3:$F$527,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU06A01_FDSC"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%Q\"&B18*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LFAU06A01_FDSC AT%Q432.2 :BOOL; (*F新风机组NJ-6AP(KT)6-新风阀关控制*)"},"LFAU06A01_FDSC               AT%Q432.2 :BOOL; (*F新风机组NJ-6AP(KT)6-新风阀关控制*)",null,"L01\\L01FAU06A01_FDSC","F新风机组NJ-6AP(KT)6-新风阀关控制",3458]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH20,[1]List!$D$3:$F$527,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%Q\"&B18*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN20,SEARCH(\"AT%\",AN20),,REPT(\" \",30-SEARCH(\"AT%\",AN20))),SEARCH(\":\",REPLACE(AN20,SEARCH(\"AT%\",AN20),,REPT(\" \",30-SEARCH(\"AT%\",AN20)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN20,SEARCH(\"AT%\",AN20),,REPT(\" \",25-SEARCH(\"AT%\",AN20)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",3459]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),1,1))","v":1},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH21,[1]List!$D$3:$F$527,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%Q\"&B18*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",3460]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH22,[1]List!$D$3:$F$527,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%Q\"&B18*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",3461]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH23,[1]List!$D$3:$F$527,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%Q\"&B18*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",3462]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH24,[1]List!$D$3:$F$527,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%Q\"&B18*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",3463]
[null,{"$f":"B30","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 0401U地址: 28 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH26&AA26&\"-\"&AK26","v":"F新风机组NJ-6AP(KT)6-送风温度"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-6AP(KT)6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-6AP(KT)6","06A01","送风温度",{"$f":"AH26&\"-\"&AK26","v":"F新风机组-送风温度"},{"$f":"VLOOKUP(AH26,[1]List!$D$3:$F$527,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU06A01_ST"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LFAU06A01_ST AT%I448.0 :INT; (*F新风机组NJ-6AP(KT)6-送风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",30-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",30-SEARCH(\"AT%\",AN26)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LFAU06A01_ST                 AT%I448.0 :INT; (*F新风机组NJ-6AP(KT)6-送风温度*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L01\\L01FAU06A01_ST"},{"$f":"J26","v":"F新风机组NJ-6AP(KT)6-送风温度"},{"$f":"30000+($B27*8+F26-1)","v":30224}]
[null,28,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,2,"0V","F新风机组NJ-6AP(KT)6-水阀反馈",{"$nulls":16},"NJ-6AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-6AP(KT)6","06A01","水阀反馈","F新风机组-水阀反馈",{"$f":"VLOOKUP(AH27,[1]List!$D$3:$F$527,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU06A01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LFAU06A01_WVB AT%I450.0 :INT; (*F新风机组NJ-6AP(KT)6-水阀反馈*)"},"LFAU06A01_WVB                AT%I450.0 :INT; (*F新风机组NJ-6AP(KT)6-水阀反馈*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM27","v":"L01\\L01FAU06A01_WVB"},"F新风机组NJ-6AP(KT)6-水阀反馈",{"$f":"AS26+1","v":30225}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":1},3,null,3,"0V","F新风机组NJ-6AP(KT)6-变频器频率反馈",{"$nulls":16},"NJ-6AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-6AP(KT)6","06A01","变频器频率反馈","F新风机组-变频器频率反馈",{"$f":"VLOOKUP(AH28,[1]List!$D$3:$F$527,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU06A01_VFB"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LFAU06A01_VFB AT%I452.0 :INT; (*F新风机组NJ-6AP(KT)6-变频器频率反馈*)"},"LFAU06A01_VFB                AT%I452.0 :INT; (*F新风机组NJ-6AP(KT)6-变频器频率反馈*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM28","v":"L01\\L01FAU06A01_VFB"},"F新风机组NJ-6AP(KT)6-变频器频率反馈",30226]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":1},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH29,[1]List!$D$3:$F$527,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM29","v":{"$error":"#N/A"}},"-",30227]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":1}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B39","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B39&\"地址: \"&B36&\" *)\"","v":"(* IOM 0401A地址: 29 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH35&AA35&\"-\"&AK35","v":"F新风机组NJ-6AP(KT)6-水阀控制"},{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-6AP(KT)6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-6AP(KT)6","06A01","水阀控制",{"$f":"AH35&\"-\"&AK35","v":"F新风机组-水阀控制"},{"$f":"VLOOKUP(AH35,[1]List!$D$3:$F$527,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU06A01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%Q\"&B36*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LFAU06A01_WVC AT%Q464.0 :INT; (*F新风机组NJ-6AP(KT)6-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",30-SEARCH(\"AT%\",AN35))),SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",30-SEARCH(\"AT%\",AN35)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35)))))),\" \")","v":"LFAU06A01_WVC                AT%Q464.0 :INT; (*F新风机组NJ-6AP(KT)6-水阀控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM35","v":"L01\\L01FAU06A01_WVC"},{"$f":"J35","v":"F新风机组NJ-6AP(KT)6-水阀控制"},{"$f":"40000+($B36*8+F35-1)","v":40232}]
[null,29,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":0},2,null,3,4,"F新风机组NJ-6AP(KT)6-变频器频率控制",{"$nulls":16},"NJ-6AP(KT)6",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-6AP(KT)6","06A01","变频器频率控制","F新风机组-变频器频率控制",{"$f":"VLOOKUP(AH36,[1]List!$D$3:$F$527,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU06A01_VFC"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%Q\"&B36*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LFAU06A01_VFC AT%Q466.0 :INT; (*F新风机组NJ-6AP(KT)6-变频器频率控制*)"},"LFAU06A01_VFC                AT%Q466.0 :INT; (*F新风机组NJ-6AP(KT)6-变频器频率控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM36","v":"L01\\L01FAU06A01_VFC"},"F新风机组NJ-6AP(KT)6-变频器频率控制",{"$f":"AS35+1","v":40233}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":1},3,null,5,6,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH37,[1]List!$D$3:$F$527,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%Q\"&B36*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN37,SEARCH(\"AT%\",AN37),,REPT(\" \",30-SEARCH(\"AT%\",AN37))),SEARCH(\":\",REPLACE(AN37,SEARCH(\"AT%\",AN37),,REPT(\" \",30-SEARCH(\"AT%\",AN37)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN37,SEARCH(\"AT%\",AN37),,REPT(\" \",25-SEARCH(\"AT%\",AN37)))))),\" \")","v":" "},null,{"$f":"$B$2&\"\\\"&$B$2&AM37","v":{"$error":"#N/A"}},"-",40234]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":1},4,null,7,8,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH38,[1]List!$D$3:$F$527,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%Q\"&B36*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM38","v":{"$error":"#N/A"}},"-",40235]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L307","index":40,"n_rows":155,"n_cols":45,"rows_kept":155,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[6,1,6,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[84,5,84,6],[84,9,84,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[93,5,93,6],[93,9,93,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[102,5,102,6],[102,9,102,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[109,5,109,6],[109,9,109,25],[111,5,111,6],[111,9,111,25],[112,5,112,6],[112,9,112,25],[113,5,113,6],[113,9,113,25],[114,5,114,6],[114,9,114,25],[115,5,115,6],[115,9,115,25],[116,5,116,6],[116,9,116,25],[117,5,117,6],[117,9,117,25],[118,5,118,6],[118,9,118,25],[120,5,120,6],[120,9,120,25],[121,5,121,6],[121,9,121,25],[122,5,122,6],[122,9,122,25],[123,5,123,6],[123,9,123,25],[124,5,124,6],[124,9,124,25],[125,5,125,6],[125,9,125,25],[126,5,126,6],[126,9,126,25],[127,5,127,6],[127,9,127,25],[129,5,129,6],[129,9,129,25],[130,5,130,6],[130,9,130,25],[131,5,131,6],[131,9,131,25],[132,5,132,6],[132,9,132,25],[133,5,133,6],[133,9,133,25],[134,5,134,6],[134,9,134,25],[135,5,135,6],[135,9,135,25],[136,5,136,6],[136,9,136,25],[138,5,138,6],[138,9,138,25],[139,5,139,6],[139,9,139,25],[140,5,140,6],[140,9,140,25],[141,5,141,6],[141,9,141,25],[142,5,142,6],[142,9,142,25],[143,5,143,6],[143,9,143,25],[144,5,144,6],[144,9,144,25],[145,5,145,6],[145,9,145,25],[147,5,147,6],[147,9,147,25],[148,5,148,6],[148,9,148,25],[149,5,149,6],[149,9,149,25],[150,5,150,6],[150,9,150,25],[151,5,151,6],[151,9,151,25],[152,5,152,6],[152,9,152,25],[153,5,153,6],[153,9,153,25],[154,5,154,6],[154,9,154,25],[4,1,5,1],[12,1,23,1],[29,1,40,1],[46,1,57,1],[63,1,74,1],[80,1,91,1],[97,1,100,1],[106,1,109,1],[115,1,118,1],[124,1,127,1],[133,1,136,1],[142,1,145,1],[151,1,154,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[16,2,23,4],[33,2,40,4],[50,2,57,4],[84,2,91,4],[67,2,74,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L25",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"EXC-1000"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B13&\"地址: \"&B10&\" *)\"","v":"(* IOM 1601R地址: 0 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH9&AA9&\"-\"&AK9","v":"空调机组NJ-3AP(KT)7-1-运行状态"},{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-3AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-1","03G01","运行状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU03G01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B10*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU03G01_R AT%I0.0 :BOOL; (*空调机组NJ-3AP(KT)7-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",30-SEARCH(\"AT%\",AN9))),SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",30-SEARCH(\"AT%\",AN9)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))))),\" \")","v":"LAHU03G01_R                  AT%I0.0   :BOOL; (*空调机组NJ-3AP(KT)7-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM9","v":"L25\\L25AHU03G01_R"},{"$f":"J9","v":"空调机组NJ-3AP(KT)7-1-运行状态"},{"$f":"10000+($B10*16*8+F9-1)","v":10000}]
[null,0,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-3AP(KT)7-1-故障状态",{"$nulls":16},{"$f":"IF(AI10=\"\",\"\",AI10)","v":"NJ-3AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-1","03G01","故障状态",{"$f":"AH10&\"-\"&AK10","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU03G01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B10*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU03G01_F AT%I0.1 :BOOL; (*空调机组NJ-3AP(KT)7-1-故障状态*)"},"LAHU03G01_F                  AT%I0.1   :BOOL; (*空调机组NJ-3AP(KT)7-1-故障状态*)",null,"L25\\L25AHU03G01_F",{"$f":"J10","v":"空调机组NJ-3AP(KT)7-1-故障状态"},{"$f":"AS9+1","v":10001}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)7-1-自动状态",{"$nulls":16},"NJ-3AP(KT)7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-1","03G01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU03G01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B10*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU03G01_A AT%I0.2 :BOOL; (*空调机组NJ-3AP(KT)7-1-自动状态*)"},"LAHU03G01_A                  AT%I0.2   :BOOL; (*空调机组NJ-3AP(KT)7-1-自动状态*)",null,"L25\\L25AHU03G01_A","空调机组NJ-3AP(KT)7-1-自动状态",{"$f":"AS10+1","v":10002}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)7-1-风机压差",{"$nulls":16},"NJ-3AP(KT)7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-1","03G01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU03G01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B10*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU03G01_FPS AT%I0.3 :BOOL; (*空调机组NJ-3AP(KT)7-1-风机压差*)"},"LAHU03G01_FPS                AT%I0.3   :BOOL; (*空调机组NJ-3AP(KT)7-1-风机压差*)",null,"L25\\L25AHU03G01_FPS","空调机组NJ-3AP(KT)7-1-风机压差",10003]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)7-2-运行状态",{"$nulls":16},"NJ-3AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-2","03G02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU03G02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B10*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU03G02_R AT%I0.4 :BOOL; (*空调机组NJ-3AP(KT)7-2-运行状态*)"},"LAHU03G02_R                  AT%I0.4   :BOOL; (*空调机组NJ-3AP(KT)7-2-运行状态*)",null,"L25\\L25AHU03G02_R","空调机组NJ-3AP(KT)7-2-运行状态",10004]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)7-2-故障状态",{"$nulls":16},"NJ-3AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-2","03G02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU03G02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B10*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU03G02_F AT%I0.5 :BOOL; (*空调机组NJ-3AP(KT)7-2-故障状态*)"},"LAHU03G02_F                  AT%I0.5   :BOOL; (*空调机组NJ-3AP(KT)7-2-故障状态*)",null,"L25\\L25AHU03G02_F","空调机组NJ-3AP(KT)7-2-故障状态",10005]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)7-2-自动状态",{"$nulls":16},"NJ-3AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-2","03G02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU03G02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B10*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU03G02_A AT%I0.6 :BOOL; (*空调机组NJ-3AP(KT)7-2-自动状态*)"},"LAHU03G02_A                  AT%I0.6   :BOOL; (*空调机组NJ-3AP(KT)7-2-自动状态*)",null,"L25\\L25AHU03G02_A","空调机组NJ-3AP(KT)7-2-自动状态",10006]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)7-2-风机压差",{"$nulls":16},"NJ-3AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-2","03G02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU03G02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B10*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU03G02_FPS AT%I0.7 :BOOL; (*空调机组NJ-3AP(KT)7-2-风机压差*)"},"LAHU03G02_FPS                AT%I0.7   :BOOL; (*空调机组NJ-3AP(KT)7-2-风机压差*)",null,"L25\\L25AHU03G02_FPS","空调机组NJ-3AP(KT)7-2-风机压差",10007]
[{"$nulls":5},9,null,17,18,"空调机组NJ-3AP(KT)7-3-运行状态",{"$nulls":16},"NJ-3AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-3","03G03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU03G03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B10*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU03G03_R AT%I1.0 :BOOL; (*空调机组NJ-3AP(KT)7-3-运行状态*)"},"LAHU03G03_R                  AT%I1.0   :BOOL; (*空调机组NJ-3AP(KT)7-3-运行状态*)",null,"L25\\L25AHU03G03_R","空调机组NJ-3AP(KT)7-3-运行状态",10008]
[{"$nulls":5},10,null,19,20,"空调机组NJ-3AP(KT)7-3-故障状态",{"$nulls":16},{"$f":"IF(AI18=\"\",\"\",AI18)","v":"NJ-3AP(KT)7-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-3","03G03","故障状态",{"$f":"AH18&\"-\"&AK18","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU03G03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B10*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU03G03_F AT%I1.1 :BOOL; (*空调机组NJ-3AP(KT)7-3-故障状态*)"},"LAHU03G03_F                  AT%I1.1   :BOOL; (*空调机组NJ-3AP(KT)7-3-故障状态*)",null,"L25\\L25AHU03G03_F","空调机组NJ-3AP(KT)7-3-故障状态",10009]
[{"$nulls":5},11,null,21,22,"空调机组NJ-3AP(KT)7-3-自动状态",{"$nulls":16},"NJ-3AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-3","03G03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU03G03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B10*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU03G03_A AT%I1.2 :BOOL; (*空调机组NJ-3AP(KT)7-3-自动状态*)"},"LAHU03G03_A                  AT%I1.2   :BOOL; (*空调机组NJ-3AP(KT)7-3-自动状态*)",null,"L25\\L25AHU03G03_A","空调机组NJ-3AP(KT)7-3-自动状态",10010]
[{"$nulls":5},12,null,23,24,"空调机组NJ-3AP(KT)7-3-风机压差",{"$nulls":16},"NJ-3AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-3","03G03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU03G03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B10*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU03G03_FPS AT%I1.3 :BOOL; (*空调机组NJ-3AP(KT)7-3-风机压差*)"},"LAHU03G03_FPS                AT%I1.3   :BOOL; (*空调机组NJ-3AP(KT)7-3-风机压差*)",null,"L25\\L25AHU03G03_FPS","空调机组NJ-3AP(KT)7-3-风机压差",10011]
[{"$nulls":5},13,null,25,26,"空调机组NJ-3AP(KT)7-4-运行状态",{"$nulls":16},"NJ-3AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-4","03G04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU03G04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B10*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU03G04_R AT%I1.4 :BOOL; (*空调机组NJ-3AP(KT)7-4-运行状态*)"},"LAHU03G04_R                  AT%I1.4   :BOOL; (*空调机组NJ-3AP(KT)7-4-运行状态*)",null,"L25\\L25AHU03G04_R","空调机组NJ-3AP(KT)7-4-运行状态",10012]
[{"$nulls":5},14,null,27,28,"空调机组NJ-3AP(KT)7-4-故障状态",{"$nulls":16},"NJ-3AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-4","03G04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU03G04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B10*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU03G04_F AT%I1.5 :BOOL; (*空调机组NJ-3AP(KT)7-4-故障状态*)"},"LAHU03G04_F                  AT%I1.5   :BOOL; (*空调机组NJ-3AP(KT)7-4-故障状态*)",null,"L25\\L25AHU03G04_F","空调机组NJ-3AP(KT)7-4-故障状态",10013]
[{"$nulls":5},15,null,29,30,"空调机组NJ-3AP(KT)7-4-自动状态",{"$nulls":16},"NJ-3AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-4","03G04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU03G04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B10*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU03G04_A AT%I1.6 :BOOL; (*空调机组NJ-3AP(KT)7-4-自动状态*)"},"LAHU03G04_A                  AT%I1.6   :BOOL; (*空调机组NJ-3AP(KT)7-4-自动状态*)",null,"L25\\L25AHU03G04_A","空调机组NJ-3AP(KT)7-4-自动状态",10014]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-3AP(KT)7-4-风机压差",{"$nulls":16},"NJ-3AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-4","03G04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH24,List!$B$3:$D$445,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,List!$K$2:$M$447,2,FALSE)","v":"AHU03G04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%I\"&B10*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":"LAHU03G04_FPS AT%I1.7 :BOOL; (*空调机组NJ-3AP(KT)7-4-风机压差*)"},"LAHU03G04_FPS                AT%I1.7   :BOOL; (*空调机组NJ-3AP(KT)7-4-风机压差*)",null,"L25\\L25AHU03G04_FPS","空调机组NJ-3AP(KT)7-4-风机压差",10015]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 1601R地址: 1 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH26&AA26&\"-\"&AK26","v":"空调机组NJ-3AP(KT)7-5-运行状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-3AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-5","03G05","运行状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU03G05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU03G05_R AT%I16.0 :BOOL; (*空调机组NJ-3AP(KT)7-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",30-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",30-SEARCH(\"AT%\",AN26)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LAHU03G05_R                  AT%I16.0  :BOOL; (*空调机组NJ-3AP(KT)7-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L25\\L25AHU03G05_R"},{"$f":"J26","v":"空调机组NJ-3AP(KT)7-5-运行状态"},{"$f":"10000+($B27*16*8+F26-1)","v":10128}]
[null,1,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-3AP(KT)7-5-故障状态",{"$nulls":16},{"$f":"IF(AI27=\"\",\"\",AI27)","v":"NJ-3AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-5","03G05","故障状态",{"$f":"AH27&\"-\"&AK27","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU03G05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU03G05_F AT%I16.1 :BOOL; (*空调机组NJ-3AP(KT)7-5-故障状态*)"},"LAHU03G05_F                  AT%I16.1  :BOOL; (*空调机组NJ-3AP(KT)7-5-故障状态*)",null,"L25\\L25AHU03G05_F",{"$f":"J27","v":"空调机组NJ-3AP(KT)7-5-故障状态"},{"$f":"AS26+1","v":10129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)7-5-自动状态",{"$nulls":16},"NJ-3AP(KT)7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-5","03G05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU03G05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU03G05_A AT%I16.2 :BOOL; (*空调机组NJ-3AP(KT)7-5-自动状态*)"},"LAHU03G05_A                  AT%I16.2  :BOOL; (*空调机组NJ-3AP(KT)7-5-自动状态*)",null,"L25\\L25AHU03G05_A","空调机组NJ-3AP(KT)7-5-自动状态",{"$f":"AS27+1","v":10130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)7-5-风机压差",{"$nulls":16},"NJ-3AP(KT)7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-5","03G05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU03G05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU03G05_FPS AT%I16.3 :BOOL; (*空调机组NJ-3AP(KT)7-5-风机压差*)"},"LAHU03G05_FPS                AT%I16.3  :BOOL; (*空调机组NJ-3AP(KT)7-5-风机压差*)",null,"L25\\L25AHU03G05_FPS","空调机组NJ-3AP(KT)7-5-风机压差",10131]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)7-6-运行状态",{"$nulls":16},"NJ-3AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-6","03G06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU03G06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B27*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU03G06_R AT%I16.4 :BOOL; (*空调机组NJ-3AP(KT)7-6-运行状态*)"},"LAHU03G06_R                  AT%I16.4  :BOOL; (*空调机组NJ-3AP(KT)7-6-运行状态*)",null,"L25\\L25AHU03G06_R","空调机组NJ-3AP(KT)7-6-运行状态",10132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)7-6-故障状态",{"$nulls":16},"NJ-3AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-6","03G06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU03G06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B27*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU03G06_F AT%I16.5 :BOOL; (*空调机组NJ-3AP(KT)7-6-故障状态*)"},"LAHU03G06_F                  AT%I16.5  :BOOL; (*空调机组NJ-3AP(KT)7-6-故障状态*)",null,"L25\\L25AHU03G06_F","空调机组NJ-3AP(KT)7-6-故障状态",10133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)7-6-自动状态",{"$nulls":16},"NJ-3AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-6","03G06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU03G06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B27*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU03G06_A AT%I16.6 :BOOL; (*空调机组NJ-3AP(KT)7-6-自动状态*)"},"LAHU03G06_A                  AT%I16.6  :BOOL; (*空调机组NJ-3AP(KT)7-6-自动状态*)",null,"L25\\L25AHU03G06_A","空调机组NJ-3AP(KT)7-6-自动状态",10134]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)7-6-风机压差",{"$nulls":16},"NJ-3AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-6","03G06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU03G06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B27*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU03G06_FPS AT%I16.7 :BOOL; (*空调机组NJ-3AP(KT)7-6-风机压差*)"},"LAHU03G06_FPS                AT%I16.7  :BOOL; (*空调机组NJ-3AP(KT)7-6-风机压差*)",null,"L25\\L25AHU03G06_FPS","空调机组NJ-3AP(KT)7-6-风机压差",10135]
[{"$nulls":5},9,null,17,18,"空调机组NJ-3AP(KT)7-7-运行状态",{"$nulls":16},"NJ-3AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-7","03G07","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU03G07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B27*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU03G07_R AT%I17.0 :BOOL; (*空调机组NJ-3AP(KT)7-7-运行状态*)"},"LAHU03G07_R                  AT%I17.0  :BOOL; (*空调机组NJ-3AP(KT)7-7-运行状态*)",null,"L25\\L25AHU03G07_R","空调机组NJ-3AP(KT)7-7-运行状态",10136]
[{"$nulls":5},10,null,19,20,"空调机组NJ-3AP(KT)7-7-故障状态",{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-3AP(KT)7-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-7","03G07","故障状态",{"$f":"AH35&\"-\"&AK35","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU03G07_F"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B27*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU03G07_F AT%I17.1 :BOOL; (*空调机组NJ-3AP(KT)7-7-故障状态*)"},"LAHU03G07_F                  AT%I17.1  :BOOL; (*空调机组NJ-3AP(KT)7-7-故障状态*)",null,"L25\\L25AHU03G07_F",{"$f":"J35","v":"空调机组NJ-3AP(KT)7-7-故障状态"},10137]
[{"$nulls":5},11,null,21,22,"空调机组NJ-3AP(KT)7-7-自动状态",{"$nulls":16},"NJ-3AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-7","03G07","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU03G07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B27*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU03G07_A AT%I17.2 :BOOL; (*空调机组NJ-3AP(KT)7-7-自动状态*)"},"LAHU03G07_A                  AT%I17.2  :BOOL; (*空调机组NJ-3AP(KT)7-7-自动状态*)",null,"L25\\L25AHU03G07_A","空调机组NJ-3AP(KT)7-7-自动状态",10138]
[{"$nulls":5},12,null,23,24,"空调机组NJ-3AP(KT)7-7-风机压差",{"$nulls":16},"NJ-3AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-7","03G07","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"AHU03G07_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B27*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LAHU03G07_FPS AT%I17.3 :BOOL; (*空调机组NJ-3AP(KT)7-7-风机压差*)"},"LAHU03G07_FPS                AT%I17.3  :BOOL; (*空调机组NJ-3AP(KT)7-7-风机压差*)",null,"L25\\L25AHU03G07_FPS","空调机组NJ-3AP(KT)7-7-风机压差",10139]
[{"$nulls":5},13,null,25,26,"空调机组NJ-3AP(KT)7-8-运行状态",{"$nulls":16},"NJ-3AP(KT)7-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-8","03G08","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"AHU03G08_R"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B27*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LAHU03G08_R AT%I17.4 :BOOL; (*空调机组NJ-3AP(KT)7-8-运行状态*)"},"LAHU03G08_R                  AT%I17.4  :BOOL; (*空调机组NJ-3AP(KT)7-8-运行状态*)",null,"L25\\L25AHU03G08_R","空调机组NJ-3AP(KT)7-8-运行状态",10140]
[{"$nulls":5},14,null,27,28,"空调机组NJ-3AP(KT)7-8-故障状态",{"$nulls":16},"NJ-3AP(KT)7-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-8","03G08","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"AHU03G08_F"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B27*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LAHU03G08_F AT%I17.5 :BOOL; (*空调机组NJ-3AP(KT)7-8-故障状态*)"},"LAHU03G08_F                  AT%I17.5  :BOOL; (*空调机组NJ-3AP(KT)7-8-故障状态*)",null,"L25\\L25AHU03G08_F","空调机组NJ-3AP(KT)7-8-故障状态",10141]
[{"$nulls":5},15,null,29,30,"空调机组NJ-3AP(KT)7-8-自动状态",{"$nulls":16},"NJ-3AP(KT)7-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-8","03G08","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"AHU03G08_A"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B27*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LAHU03G08_A AT%I17.6 :BOOL; (*空调机组NJ-3AP(KT)7-8-自动状态*)"},"LAHU03G08_A                  AT%I17.6  :BOOL; (*空调机组NJ-3AP(KT)7-8-自动状态*)",null,"L25\\L25AHU03G08_A","空调机组NJ-3AP(KT)7-8-自动状态",10142]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-3AP(KT)7-8-风机压差",{"$nulls":16},"NJ-3AP(KT)7-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-8","03G08","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":"AHU03G08_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%I\"&B27*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":"LAHU03G08_FPS AT%I17.7 :BOOL; (*空调机组NJ-3AP(KT)7-8-风机压差*)"},"LAHU03G08_FPS                AT%I17.7  :BOOL; (*空调机组NJ-3AP(KT)7-8-风机压差*)",null,"L25\\L25AHU03G08_FPS","空调机组NJ-3AP(KT)7-8-风机压差",10143]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 1601R地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH43&AA43&\"-\"&AK43","v":"空调机组NJ-3AP(KT)7-9-运行状态"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-3AP(KT)7-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-9","03G09","运行状态",{"$f":"AH43&\"-\"&AK43","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"AHU03G09_R"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B44*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LAHU03G09_R AT%I32.0 :BOOL; (*空调机组NJ-3AP(KT)7-9-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",30-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",30-SEARCH(\"AT%\",AN43)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LAHU03G09_R                  AT%I32.0  :BOOL; (*空调机组NJ-3AP(KT)7-9-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM43","v":"L25\\L25AHU03G09_R"},{"$f":"J43","v":"空调机组NJ-3AP(KT)7-9-运行状态"},{"$f":"10000+($B44*16*8+F43-1)","v":10256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},2,null,3,4,"空调机组NJ-3AP(KT)7-9-故障状态",{"$nulls":16},{"$f":"IF(AI44=\"\",\"\",AI44)","v":"NJ-3AP(KT)7-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-9","03G09","故障状态",{"$f":"AH44&\"-\"&AK44","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"AHU03G09_F"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B44*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LAHU03G09_F AT%I32.1 :BOOL; (*空调机组NJ-3AP(KT)7-9-故障状态*)"},"LAHU03G09_F                  AT%I32.1  :BOOL; (*空调机组NJ-3AP(KT)7-9-故障状态*)",null,"L25\\L25AHU03G09_F",{"$f":"J44","v":"空调机组NJ-3AP(KT)7-9-故障状态"},{"$f":"AS43+1","v":10257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)7-9-自动状态",{"$nulls":16},"NJ-3AP(KT)7-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-9","03G09","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"AHU03G09_A"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B44*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LAHU03G09_A AT%I32.2 :BOOL; (*空调机组NJ-3AP(KT)7-9-自动状态*)"},"LAHU03G09_A                  AT%I32.2  :BOOL; (*空调机组NJ-3AP(KT)7-9-自动状态*)",null,"L25\\L25AHU03G09_A","空调机组NJ-3AP(KT)7-9-自动状态",{"$f":"AS44+1","v":10258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)7-9-风机压差",{"$nulls":16},"NJ-3AP(KT)7-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-9","03G09","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"AHU03G09_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B44*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LAHU03G09_FPS AT%I32.3 :BOOL; (*空调机组NJ-3AP(KT)7-9-风机压差*)"},"LAHU03G09_FPS                AT%I32.3  :BOOL; (*空调机组NJ-3AP(KT)7-9-风机压差*)",null,"L25\\L25AHU03G09_FPS","空调机组NJ-3AP(KT)7-9-风机压差",10259]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)7-10-运行状态",{"$nulls":16},"NJ-3AP(KT)7-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-10","03G10","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"AHU03G10_R"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B44*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LAHU03G10_R AT%I32.4 :BOOL; (*空调机组NJ-3AP(KT)7-10-运行状态*)"},"LAHU03G10_R                  AT%I32.4  :BOOL; (*空调机组NJ-3AP(KT)7-10-运行状态*)",null,"L25\\L25AHU03G10_R","空调机组NJ-3AP(KT)7-10-运行状态",10260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)7-10-故障状态",{"$nulls":16},"NJ-3AP(KT)7-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-10","03G10","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"AHU03G10_F"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B44*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LAHU03G10_F AT%I32.5 :BOOL; (*空调机组NJ-3AP(KT)7-10-故障状态*)"},"LAHU03G10_F                  AT%I32.5  :BOOL; (*空调机组NJ-3AP(KT)7-10-故障状态*)",null,"L25\\L25AHU03G10_F","空调机组NJ-3AP(KT)7-10-故障状态",10261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)7-10-自动状态",{"$nulls":16},"NJ-3AP(KT)7-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-10","03G10","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"AHU03G10_A"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B44*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LAHU03G10_A AT%I32.6 :BOOL; (*空调机组NJ-3AP(KT)7-10-自动状态*)"},"LAHU03G10_A                  AT%I32.6  :BOOL; (*空调机组NJ-3AP(KT)7-10-自动状态*)",null,"L25\\L25AHU03G10_A","空调机组NJ-3AP(KT)7-10-自动状态",10262]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)7-10-风机压差",{"$nulls":16},"NJ-3AP(KT)7-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-10","03G10","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"AHU03G10_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B44*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LAHU03G10_FPS AT%I32.7 :BOOL; (*空调机组NJ-3AP(KT)7-10-风机压差*)"},"LAHU03G10_FPS                AT%I32.7  :BOOL; (*空调机组NJ-3AP(KT)7-10-风机压差*)",null,"L25\\L25AHU03G10_FPS","空调机组NJ-3AP(KT)7-10-风机压差",10263]
[{"$nulls":5},9,null,17,18,"空调机组NJ-3AP(KT)7-11-运行状态",{"$nulls":16},"NJ-3AP(KT)7-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-11","03G11","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"AHU03G11_R"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B44*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LAHU03G11_R AT%I33.0 :BOOL; (*空调机组NJ-3AP(KT)7-11-运行状态*)"},"LAHU03G11_R                  AT%I33.0  :BOOL; (*空调机组NJ-3AP(KT)7-11-运行状态*)",null,"L25\\L25AHU03G11_R","空调机组NJ-3AP(KT)7-11-运行状态",10264]
[{"$nulls":5},10,null,19,20,"空调机组NJ-3AP(KT)7-11-故障状态",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-3AP(KT)7-11"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-11","03G11","故障状态",{"$f":"AH52&\"-\"&AK52","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"AHU03G11_F"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%I\"&B44*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LAHU03G11_F AT%I33.1 :BOOL; (*空调机组NJ-3AP(KT)7-11-故障状态*)"},"LAHU03G11_F                  AT%I33.1  :BOOL; (*空调机组NJ-3AP(KT)7-11-故障状态*)",null,"L25\\L25AHU03G11_F",{"$f":"J52","v":"空调机组NJ-3AP(KT)7-11-故障状态"},10265]
[{"$nulls":5},11,null,21,22,"空调机组NJ-3AP(KT)7-11-自动状态",{"$nulls":16},"NJ-3AP(KT)7-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-11","03G11","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"AHU03G11_A"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%I\"&B44*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LAHU03G11_A AT%I33.2 :BOOL; (*空调机组NJ-3AP(KT)7-11-自动状态*)"},"LAHU03G11_A                  AT%I33.2  :BOOL; (*空调机组NJ-3AP(KT)7-11-自动状态*)",null,"L25\\L25AHU03G11_A","空调机组NJ-3AP(KT)7-11-自动状态",10266]
[{"$nulls":5},12,null,23,24,"空调机组NJ-3AP(KT)7-11-风机压差",{"$nulls":16},"NJ-3AP(KT)7-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-11","03G11","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"AHU03G11_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%I\"&B44*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LAHU03G11_FPS AT%I33.3 :BOOL; (*空调机组NJ-3AP(KT)7-11-风机压差*)"},"LAHU03G11_FPS                AT%I33.3  :BOOL; (*空调机组NJ-3AP(KT)7-11-风机压差*)",null,"L25\\L25AHU03G11_FPS","空调机组NJ-3AP(KT)7-11-风机压差",10267]
[{"$nulls":5},13,null,25,26,"空调机组NJ-3AP(KT)7-12-运行状态",{"$nulls":16},"NJ-3AP(KT)7-12",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-12","03G12","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"AHU03G12_R"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%I\"&B44*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LAHU03G12_R AT%I33.4 :BOOL; (*空调机组NJ-3AP(KT)7-12-运行状态*)"},"LAHU03G12_R                  AT%I33.4  :BOOL; (*空调机组NJ-3AP(KT)7-12-运行状态*)",null,"L25\\L25AHU03G12_R","空调机组NJ-3AP(KT)7-12-运行状态",10268]
[{"$nulls":5},14,null,27,28,"空调机组NJ-3AP(KT)7-12-故障状态",{"$nulls":16},"NJ-3AP(KT)7-12",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-12","03G12","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"AHU03G12_F"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%I\"&B44*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LAHU03G12_F AT%I33.5 :BOOL; (*空调机组NJ-3AP(KT)7-12-故障状态*)"},"LAHU03G12_F                  AT%I33.5  :BOOL; (*空调机组NJ-3AP(KT)7-12-故障状态*)",null,"L25\\L25AHU03G12_F","空调机组NJ-3AP(KT)7-12-故障状态",10269]
[{"$nulls":5},15,null,29,30,"空调机组NJ-3AP(KT)7-12-自动状态",{"$nulls":16},"NJ-3AP(KT)7-12",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-12","03G12","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"AHU03G12_A"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%I\"&B44*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LAHU03G12_A AT%I33.6 :BOOL; (*空调机组NJ-3AP(KT)7-12-自动状态*)"},"LAHU03G12_A                  AT%I33.6  :BOOL; (*空调机组NJ-3AP(KT)7-12-自动状态*)",null,"L25\\L25AHU03G12_A","空调机组NJ-3AP(KT)7-12-自动状态",10270]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-3AP(KT)7-12-风机压差",{"$nulls":16},"NJ-3AP(KT)7-12",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-12","03G12","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":"AHU03G12_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%I\"&B44*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":"LAHU03G12_FPS AT%I33.7 :BOOL; (*空调机组NJ-3AP(KT)7-12-风机压差*)"},"LAHU03G12_FPS                AT%I33.7  :BOOL; (*空调机组NJ-3AP(KT)7-12-风机压差*)",null,"L25\\L25AHU03G12_FPS","空调机组NJ-3AP(KT)7-12-风机压差",10271]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B64&\"地址: \"&B61&\" *)\"","v":"(* IOM 1601R地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH60&AA60&\"-\"&AK60","v":"照明控制箱NJ-3AL7-1-运行状态"},{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-3AL7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,null,"总线供电问题",null,"照明控制箱","NJ-3AL7-1","03G01","运行状态",{"$f":"AH60&\"-\"&AK60","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"LCB03G01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%I\"&B61*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LLCB03G01_R AT%I48.0 :BOOL; (*照明控制箱NJ-3AL7-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",30-SEARCH(\"AT%\",AN60))),SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",30-SEARCH(\"AT%\",AN60)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))))),\" \")","v":"LLCB03G01_R                  AT%I48.0  :BOOL; (*照明控制箱NJ-3AL7-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM60","v":"L25\\L25LCB03G01_R"},{"$f":"J60","v":"照明控制箱NJ-3AL7-1-运行状态"},{"$f":"10000+($B61*16*8+F60-1)","v":10384}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},2,null,3,4,"照明控制箱NJ-3AL7-1-自动状态",{"$nulls":16},{"$f":"IF(AI61=\"\",\"\",AI61)","v":"NJ-3AL7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL7-1","03G01","自动状态",{"$f":"AH61&\"-\"&AK61","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"LCB03G01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%I\"&B61*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LLCB03G01_A AT%I48.1 :BOOL; (*照明控制箱NJ-3AL7-1-自动状态*)"},"LLCB03G01_A                  AT%I48.1  :BOOL; (*照明控制箱NJ-3AL7-1-自动状态*)",null,"L25\\L25LCB03G01_A",{"$f":"J61","v":"照明控制箱NJ-3AL7-1-自动状态"},{"$f":"AS60+1","v":10385}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},3,null,5,6,"照明控制箱NJ-3AL7-2-运行状态",{"$nulls":16},"NJ-3AL7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL7-2","03G02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"LCB03G02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B61*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LLCB03G02_R AT%I48.2 :BOOL; (*照明控制箱NJ-3AL7-2-运行状态*)"},"LLCB03G02_R                  AT%I48.2  :BOOL; (*照明控制箱NJ-3AL7-2-运行状态*)",null,"L25\\L25LCB03G02_R","照明控制箱NJ-3AL7-2-运行状态",{"$f":"AS61+1","v":10386}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},4,null,7,8,"照明控制箱NJ-3AL7-2-自动状态",{"$nulls":16},"NJ-3AL7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL7-2","03G02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"LCB03G02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B61*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LLCB03G02_A AT%I48.3 :BOOL; (*照明控制箱NJ-3AL7-2-自动状态*)"},"LLCB03G02_A                  AT%I48.3  :BOOL; (*照明控制箱NJ-3AL7-2-自动状态*)",null,"L25\\L25LCB03G02_A","照明控制箱NJ-3AL7-2-自动状态",10387]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},5,null,9,10,"照明控制箱NJ-3AL7-3-运行状态",{"$nulls":16},"NJ-3AL7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL7-3","03G03","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"LCB03G03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B61*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LLCB03G03_R AT%I48.4 :BOOL; (*照明控制箱NJ-3AL7-3-运行状态*)"},"LLCB03G03_R                  AT%I48.4  :BOOL; (*照明控制箱NJ-3AL7-3-运行状态*)",null,"L25\\L25LCB03G03_R","照明控制箱NJ-3AL7-3-运行状态",10388]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"照明控制箱NJ-3AL7-3-自动状态",{"$nulls":16},"NJ-3AL7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL7-3","03G03","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":"LCB03G03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B61*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":"LLCB03G03_A AT%I48.5 :BOOL; (*照明控制箱NJ-3AL7-3-自动状态*)"},"LLCB03G03_A                  AT%I48.5  :BOOL; (*照明控制箱NJ-3AL7-3-自动状态*)",null,"L25\\L25LCB03G03_A","照明控制箱NJ-3AL7-3-自动状态",10389]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"照明控制箱NJ-3AL7-4-运行状态",{"$nulls":16},"NJ-3AL7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL7-4","03G04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":"LCB03G04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B61*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":"LLCB03G04_R AT%I48.6 :BOOL; (*照明控制箱NJ-3AL7-4-运行状态*)"},"LLCB03G04_R                  AT%I48.6  :BOOL; (*照明控制箱NJ-3AL7-4-运行状态*)",null,"L25\\L25LCB03G04_R","照明控制箱NJ-3AL7-4-运行状态",10390]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"照明控制箱NJ-3AL7-4-自动状态",{"$nulls":16},"NJ-3AL7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL7-4","03G04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":"LCB03G04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%I\"&B61*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":"LLCB03G04_A AT%I48.7 :BOOL; (*照明控制箱NJ-3AL7-4-自动状态*)"},"LLCB03G04_A                  AT%I48.7  :BOOL; (*照明控制箱NJ-3AL7-4-自动状态*)",null,"L25\\L25LCB03G04_A","照明控制箱NJ-3AL7-4-自动状态",10391]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-3AL7-5-运行状态",{"$nulls":16},"NJ-3AL7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL7-5","03G05","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"LCB03G05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%I\"&B61*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LLCB03G05_R AT%I49.0 :BOOL; (*照明控制箱NJ-3AL7-5-运行状态*)"},"LLCB03G05_R                  AT%I49.0  :BOOL; (*照明控制箱NJ-3AL7-5-运行状态*)",null,"L25\\L25LCB03G05_R","照明控制箱NJ-3AL7-5-运行状态",10392]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-3AL7-5-自动状态",{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-3AL7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL7-5","03G05","自动状态",{"$f":"AH69&\"-\"&AK69","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"LCB03G05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%I\"&B61*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LLCB03G05_A AT%I49.1 :BOOL; (*照明控制箱NJ-3AL7-5-自动状态*)"},"LLCB03G05_A                  AT%I49.1  :BOOL; (*照明控制箱NJ-3AL7-5-自动状态*)",null,"L25\\L25LCB03G05_A",{"$f":"J69","v":"照明控制箱NJ-3AL7-5-自动状态"},10393]
[{"$nulls":5},11,null,21,22,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%I\"&B61*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10394]
[{"$nulls":5},12,null,23,24,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%I\"&B61*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10395]
[{"$nulls":5},13,null,25,26,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%I\"&B61*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10396]
[{"$nulls":5},14,null,27,28,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%I\"&B61*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10397]
[{"$nulls":5},15,null,29,30,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%I\"&B61*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10398]
[".",{"$nulls":4},16,null,31,32,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%I\"&B61*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10399]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B81&\"地址: \"&B78&\" *)\"","v":"(* IOM 1601D地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH77&AA77&\"-\"&AK77","v":"空调机组NJ-3AP(KT)7-1-启停控制"},{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-3AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-1","03G01","启停控制",{"$f":"AH77&\"-\"&AK77","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"AHU03G01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%Q\"&B78*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LAHU03G01_C AT%Q64.0 :BOOL; (*空调机组NJ-3AP(KT)7-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77))),SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))))),\" \")","v":"LAHU03G01_C             AT%Q64.0       :BOOL; (*空调机组NJ-3AP(KT)7-1-启停控制*)"},null,{"$f":"AM77","v":"AHU03G01_C"},{"$f":"J77","v":"空调机组NJ-3AP(KT)7-1-启停控制"},{"$f":"($B78*16*8+F77-1)","v":512}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","空调机组NJ-3AP(KT)7-2-启停控制",{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-3AP(KT)7-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-2","03G02","启停控制",{"$f":"AH78&\"-\"&AK78","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU03G02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B78*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU03G02_C AT%Q64.1 :BOOL; (*空调机组NJ-3AP(KT)7-2-启停控制*)"},"LAHU03G02_C             AT%Q64.1       :BOOL; (*空调机组NJ-3AP(KT)7-2-启停控制*)",null,"AHU03G02_C",{"$f":"J78","v":"空调机组NJ-3AP(KT)7-2-启停控制"},{"$f":"AS77+1","v":513}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-3AP(KT)7-3-启停控制",{"$nulls":16},"NJ-3AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-3","03G03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU03G03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B78*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU03G03_C AT%Q64.2 :BOOL; (*空调机组NJ-3AP(KT)7-3-启停控制*)"},"LAHU03G03_C             AT%Q64.2       :BOOL; (*空调机组NJ-3AP(KT)7-3-启停控制*)",null,"AHU03G03_C","空调机组NJ-3AP(KT)7-3-启停控制",{"$f":"AS78+1","v":514}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","空调机组NJ-3AP(KT)7-4-启停控制",{"$nulls":16},"NJ-3AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-4","03G04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU03G04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B78*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU03G04_C AT%Q64.3 :BOOL; (*空调机组NJ-3AP(KT)7-4-启停控制*)"},"LAHU03G04_C             AT%Q64.3       :BOOL; (*空调机组NJ-3AP(KT)7-4-启停控制*)",null,"AHU03G04_C","空调机组NJ-3AP(KT)7-4-启停控制",515]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-3AP(KT)7-5-启停控制",{"$nulls":16},"NJ-3AP(KT)7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-5","03G05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"AHU03G05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%Q\"&B78*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LAHU03G05_C AT%Q64.4 :BOOL; (*空调机组NJ-3AP(KT)7-5-启停控制*)"},"LAHU03G05_C             AT%Q64.4       :BOOL; (*空调机组NJ-3AP(KT)7-5-启停控制*)",null,"AHU03G05_C","空调机组NJ-3AP(KT)7-5-启停控制",516]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-3AP(KT)7-6-启停控制",{"$nulls":16},"NJ-3AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-6","03G06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":"AHU03G06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%Q\"&B78*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":"LAHU03G06_C AT%Q64.5 :BOOL; (*空调机组NJ-3AP(KT)7-6-启停控制*)"},"LAHU03G06_C             AT%Q64.5       :BOOL; (*空调机组NJ-3AP(KT)7-6-启停控制*)",null,"AHU03G06_C","空调机组NJ-3AP(KT)7-6-启停控制",517]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","空调机组NJ-3AP(KT)7-7-启停控制",{"$nulls":16},"NJ-3AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-7","03G07","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":"AHU03G07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%Q\"&B78*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":"LAHU03G07_C AT%Q64.6 :BOOL; (*空调机组NJ-3AP(KT)7-7-启停控制*)"},"LAHU03G07_C             AT%Q64.6       :BOOL; (*空调机组NJ-3AP(KT)7-7-启停控制*)",null,"AHU03G07_C","空调机组NJ-3AP(KT)7-7-启停控制",518]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","空调机组NJ-3AP(KT)7-8-启停控制",{"$nulls":16},"NJ-3AP(KT)7-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-8","03G08","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH84,List!$B$3:$D$445,2,FALSE)&AJ84&\"_\"&VLOOKUP(AK84,List!$K$2:$M$447,2,FALSE)","v":"AHU03G08_C"},{"$f":"_xlfn.IFNA(\"L\"&AM84&\" \"&\"AT%Q\"&B78*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J84&\"*)\",\" \")","v":"LAHU03G08_C AT%Q64.7 :BOOL; (*空调机组NJ-3AP(KT)7-8-启停控制*)"},"LAHU03G08_C             AT%Q64.7       :BOOL; (*空调机组NJ-3AP(KT)7-8-启停控制*)",null,"AHU03G08_C","空调机组NJ-3AP(KT)7-8-启停控制",519]
[{"$nulls":5},9,null,"9+","9-","空调机组NJ-3AP(KT)7-9-启停控制",{"$nulls":16},"NJ-3AP(KT)7-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-9","03G09","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH85,List!$B$3:$D$445,2,FALSE)&AJ85&\"_\"&VLOOKUP(AK85,List!$K$2:$M$447,2,FALSE)","v":"AHU03G09_C"},{"$f":"_xlfn.IFNA(\"L\"&AM85&\" \"&\"AT%Q\"&B78*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J85&\"*)\",\" \")","v":"LAHU03G09_C AT%Q65.0 :BOOL; (*空调机组NJ-3AP(KT)7-9-启停控制*)"},"LAHU03G09_C             AT%Q65.0       :BOOL; (*空调机组NJ-3AP(KT)7-9-启停控制*)",null,"AHU03G09_C","空调机组NJ-3AP(KT)7-9-启停控制",520]
[{"$nulls":5},10,null,"10+","10-","空调机组NJ-3AP(KT)7-10-启停控制",{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-3AP(KT)7-10"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-10","03G10","启停控制",{"$f":"AH86&\"-\"&AK86","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"AHU03G10_C"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%Q\"&B78*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LAHU03G10_C AT%Q65.1 :BOOL; (*空调机组NJ-3AP(KT)7-10-启停控制*)"},"LAHU03G10_C             AT%Q65.1       :BOOL; (*空调机组NJ-3AP(KT)7-10-启停控制*)",null,"AHU03G10_C",{"$f":"J86","v":"空调机组NJ-3AP(KT)7-10-启停控制"},521]
[{"$nulls":5},11,null,"11+","11-","空调机组NJ-3AP(KT)7-11-启停控制",{"$nulls":16},"NJ-3AP(KT)7-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-11","03G11","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"AHU03G11_C"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%Q\"&B78*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LAHU03G11_C AT%Q65.2 :BOOL; (*空调机组NJ-3AP(KT)7-11-启停控制*)"},"LAHU03G11_C             AT%Q65.2       :BOOL; (*空调机组NJ-3AP(KT)7-11-启停控制*)",null,"AHU03G11_C","空调机组NJ-3AP(KT)7-11-启停控制",522]
[{"$nulls":5},12,null,"12+","12-","空调机组NJ-3AP(KT)7-12-启停控制",{"$nulls":16},"NJ-3AP(KT)7-12",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-12","03G12","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"AHU03G12_C"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%Q\"&B78*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LAHU03G12_C AT%Q65.3 :BOOL; (*空调机组NJ-3AP(KT)7-12-启停控制*)"},"LAHU03G12_C             AT%Q65.3       :BOOL; (*空调机组NJ-3AP(KT)7-12-启停控制*)",null,"AHU03G12_C","空调机组NJ-3AP(KT)7-12-启停控制",523]
[{"$nulls":5},13,null,"13+","13-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%Q\"&B78*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",524]
[{"$nulls":5},14,null,"14+","14-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%Q\"&B78*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",525]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH91,List!$B$3:$D$445,2,FALSE)&AJ91&\"_\"&VLOOKUP(AK91,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM91&\" \"&\"AT%Q\"&B78*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J91&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",526]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH92,List!$B$3:$D$445,2,FALSE)&AJ92&\"_\"&VLOOKUP(AK92,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM92&\" \"&\"AT%Q\"&B78*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J92&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",527]
[null,"IOM 0801D",{"$nulls":38},{"$f":"\"(* \"&B98&\"地址: \"&B95&\" *)\"","v":"(* IOM 0801D地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH94&AA94&\"-\"&AK94","v":"照明控制箱NJ-3AL7-1-启停控制"},{"$nulls":16},{"$f":"IF(AI94=\"\",\"\",AI94)","v":"NJ-3AL7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL7-1","03G01","启停控制",{"$f":"AH94&\"-\"&AK94","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH94,List!$B$3:$D$445,2,FALSE)&AJ94&\"_\"&VLOOKUP(AK94,List!$K$2:$M$447,2,FALSE)","v":"LCB03G01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM94&\" \"&\"AT%Q\"&B95*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J94&\"*)\",\" \")","v":"LLCB03G01_C AT%Q80.0 :BOOL; (*照明控制箱NJ-3AL7-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94))),SEARCH(\":\",REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94)))))),\" \")","v":"LLCB03G01_C             AT%Q80.0       :BOOL; (*照明控制箱NJ-3AL7-1-启停控制*)"},null,{"$f":"AM94","v":"LCB03G01_C"},{"$f":"J94","v":"照明控制箱NJ-3AL7-1-启停控制"},{"$f":"($B95*16*8+F94-1)","v":640}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","照明控制箱NJ-3AL7-2-启停控制",{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-3AL7-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL7-2","03G02","启停控制",{"$f":"AH95&\"-\"&AK95","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"LCB03G02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%Q\"&B95*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LLCB03G02_C AT%Q80.1 :BOOL; (*照明控制箱NJ-3AL7-2-启停控制*)"},"LLCB03G02_C             AT%Q80.1       :BOOL; (*照明控制箱NJ-3AL7-2-启停控制*)",null,"LCB03G02_C",{"$f":"J95","v":"照明控制箱NJ-3AL7-2-启停控制"},{"$f":"AS94+1","v":641}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","照明控制箱NJ-3AL7-3-启停控制",{"$nulls":16},"NJ-3AL7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL7-3","03G03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"LCB03G03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%Q\"&B95*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LLCB03G03_C AT%Q80.2 :BOOL; (*照明控制箱NJ-3AL7-3-启停控制*)"},"LLCB03G03_C             AT%Q80.2       :BOOL; (*照明控制箱NJ-3AL7-3-启停控制*)",null,"LCB03G03_C","照明控制箱NJ-3AL7-3-启停控制",{"$f":"AS95+1","v":642}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","照明控制箱NJ-3AL7-4-启停控制",{"$nulls":16},"NJ-3AL7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL7-4","03G04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":"LCB03G04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%Q\"&B95*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":"LLCB03G04_C AT%Q80.3 :BOOL; (*照明控制箱NJ-3AL7-4-启停控制*)"},"LLCB03G04_C             AT%Q80.3       :BOOL; (*照明控制箱NJ-3AL7-4-启停控制*)",null,"LCB03G04_C","照明控制箱NJ-3AL7-4-启停控制",643]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","照明控制箱NJ-3AL7-5-启停控制",{"$nulls":16},"NJ-3AL7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL7-5","03G05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":"LCB03G05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%Q\"&B95*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":"LLCB03G05_C AT%Q80.4 :BOOL; (*照明控制箱NJ-3AL7-5-启停控制*)"},"LLCB03G05_C             AT%Q80.4       :BOOL; (*照明控制箱NJ-3AL7-5-启停控制*)",null,"LCB03G05_C","照明控制箱NJ-3AL7-5-启停控制",644]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH99,List!$B$3:$D$445,2,FALSE)&AJ99&\"_\"&VLOOKUP(AK99,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM99&\" \"&\"AT%Q\"&B95*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J99&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",645]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH100,List!$B$3:$D$445,2,FALSE)&AJ100&\"_\"&VLOOKUP(AK100,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM100&\" \"&\"AT%Q\"&B95*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J100&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",646]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH101,List!$B$3:$D$445,2,FALSE)&AJ101&\"_\"&VLOOKUP(AK101,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM101&\" \"&\"AT%Q\"&B95*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J101&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",647]
[null,{"$f":"B107","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B107&\"地址: \"&B104&\" *)\"","v":"(* IOM 0801U地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH103&AA103&\"-\"&AK103","v":"空调机组NJ-3AP(KT)7-1-回风温度"},{"$nulls":16},{"$f":"IF(AI103=\"\",\"\",AI103)","v":"NJ-3AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-1","03G01","回风温度",{"$f":"AH103&\"-\"&AK103","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH103,List!$B$3:$D$445,2,FALSE)&AJ103&\"_\"&VLOOKUP(AK103,List!$K$2:$M$447,2,FALSE)","v":"AHU03G01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM103&\" \"&\"AT%I\"&B104*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J103&\"*)\",\" \")","v":"LAHU03G01_RT AT%I96.0 :INT ; (*空调机组NJ-3AP(KT)7-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103))),SEARCH(\":\",REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103)))))),\" \")","v":"LAHU03G01_RT            AT%I96.0       :INT ; (*空调机组NJ-3AP(KT)7-1-回风温度*)"},null,{"$f":"AM103","v":"AHU03G01_RT"},{"$f":"J103","v":"空调机组NJ-3AP(KT)7-1-回风温度"},{"$f":"30000+($B104*8+F103-1)","v":30048}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-3AP(KT)7-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI104=\"\",\"\",AI104)","v":"NJ-3AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-1","03G01","水阀反馈",{"$f":"AH104&\"-\"&AK104","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"AHU03G01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%I\"&B104*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LAHU03G01_WVB AT%I98.0 :INT ; (*空调机组NJ-3AP(KT)7-1-水阀反馈*)"},"LAHU03G01_WVB           AT%I98.0       :INT ; (*空调机组NJ-3AP(KT)7-1-水阀反馈*)",null,"AHU03G01_WVB",{"$f":"J104","v":"空调机组NJ-3AP(KT)7-1-水阀反馈"},{"$f":"AS103+1","v":30049}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)7-2-回风温度",{"$nulls":16},"NJ-3AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-2","03G02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"AHU03G02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%I\"&B104*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LAHU03G02_RT AT%I100.0 :INT ; (*空调机组NJ-3AP(KT)7-2-回风温度*)"},"LAHU03G02_RT            AT%I100.0      :INT ; (*空调机组NJ-3AP(KT)7-2-回风温度*)",null,"AHU03G02_RT","空调机组NJ-3AP(KT)7-2-回风温度",{"$f":"AS104+1","v":30050}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-3AP(KT)7-2-水阀反馈",{"$nulls":16},"NJ-3AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-2","03G02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":"AHU03G02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%I\"&B104*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":"LAHU03G02_WVB AT%I102.0 :INT ; (*空调机组NJ-3AP(KT)7-2-水阀反馈*)"},"LAHU03G02_WVB           AT%I102.0      :INT ; (*空调机组NJ-3AP(KT)7-2-水阀反馈*)",null,"AHU03G02_WVB","空调机组NJ-3AP(KT)7-2-水阀反馈",30051]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-3AP(KT)7-3-回风温度",{"$nulls":16},"NJ-3AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-3","03G03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH107,List!$B$3:$D$445,2,FALSE)&AJ107&\"_\"&VLOOKUP(AK107,List!$K$2:$M$447,2,FALSE)","v":"AHU03G03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM107&\" \"&\"AT%I\"&B104*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J107&\"*)\",\" \")","v":"LAHU03G03_RT AT%I104.0 :INT ; (*空调机组NJ-3AP(KT)7-3-回风温度*)"},"LAHU03G03_RT            AT%I104.0      :INT ; (*空调机组NJ-3AP(KT)7-3-回风温度*)",null,"AHU03G03_RT","空调机组NJ-3AP(KT)7-3-回风温度",30052]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-3AP(KT)7-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI108=\"\",\"\",AI108)","v":"NJ-3AP(KT)7-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-3","03G03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH108,List!$B$3:$D$445,2,FALSE)&AJ108&\"_\"&VLOOKUP(AK108,List!$K$2:$M$447,2,FALSE)","v":"AHU03G03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM108&\" \"&\"AT%I\"&B104*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J108&\"*)\",\" \")","v":"LAHU03G03_WVB AT%I106.0 :INT ; (*空调机组NJ-3AP(KT)7-3-水阀反馈*)"},"LAHU03G03_WVB           AT%I106.0      :INT ; (*空调机组NJ-3AP(KT)7-3-水阀反馈*)",null,"AHU03G03_WVB",{"$f":"J108","v":"空调机组NJ-3AP(KT)7-3-水阀反馈"},30053]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-3AP(KT)7-4-回风温度",{"$nulls":16},"NJ-3AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-4","03G04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH109,List!$B$3:$D$445,2,FALSE)&AJ109&\"_\"&VLOOKUP(AK109,List!$K$2:$M$447,2,FALSE)","v":"AHU03G04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM109&\" \"&\"AT%I\"&B104*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J109&\"*)\",\" \")","v":"LAHU03G04_RT AT%I108.0 :INT ; (*空调机组NJ-3AP(KT)7-4-回风温度*)"},"LAHU03G04_RT            AT%I108.0      :INT ; (*空调机组NJ-3AP(KT)7-4-回风温度*)",null,"AHU03G04_RT","空调机组NJ-3AP(KT)7-4-回风温度",30054]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-3AP(KT)7-4-水阀反馈",{"$nulls":16},"NJ-3AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL110,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL110,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-4","03G04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH110,List!$B$3:$D$445,2,FALSE)&AJ110&\"_\"&VLOOKUP(AK110,List!$K$2:$M$447,2,FALSE)","v":"AHU03G04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM110&\" \"&\"AT%I\"&B104*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J110&\"*)\",\" \")","v":"LAHU03G04_WVB AT%I110.0 :INT ; (*空调机组NJ-3AP(KT)7-4-水阀反馈*)"},"LAHU03G04_WVB           AT%I110.0      :INT ; (*空调机组NJ-3AP(KT)7-4-水阀反馈*)",null,"AHU03G04_WVB","空调机组NJ-3AP(KT)7-4-水阀反馈",30055]
[null,{"$f":"B116","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B116&\"地址: \"&B113&\" *)\"","v":"(* IOM 0801U地址: 7 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH112&AA112&\"-\"&AK112","v":"空调机组NJ-3AP(KT)7-5-回风温度"},{"$nulls":16},{"$f":"IF(AI112=\"\",\"\",AI112)","v":"NJ-3AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-5","03G05","回风温度",{"$f":"AH112&\"-\"&AK112","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH112,List!$B$3:$D$445,2,FALSE)&AJ112&\"_\"&VLOOKUP(AK112,List!$K$2:$M$447,2,FALSE)","v":"AHU03G05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM112&\" \"&\"AT%I\"&B113*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J112&\"*)\",\" \")","v":"LAHU03G05_RT AT%I112.0 :INT ; (*空调机组NJ-3AP(KT)7-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112))),SEARCH(\":\",REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112)))))),\" \")","v":"LAHU03G05_RT            AT%I112.0      :INT ; (*空调机组NJ-3AP(KT)7-5-回风温度*)"},null,{"$f":"AM112","v":"AHU03G05_RT"},{"$f":"J112","v":"空调机组NJ-3AP(KT)7-5-回风温度"},{"$f":"30000+($B113*8+F112-1)","v":30056}]
[null,7,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-3AP(KT)7-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI113=\"\",\"\",AI113)","v":"NJ-3AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-5","03G05","水阀反馈",{"$f":"AH113&\"-\"&AK113","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH113,List!$B$3:$D$445,2,FALSE)&AJ113&\"_\"&VLOOKUP(AK113,List!$K$2:$M$447,2,FALSE)","v":"AHU03G05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM113&\" \"&\"AT%I\"&B113*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J113&\"*)\",\" \")","v":"LAHU03G05_WVB AT%I114.0 :INT ; (*空调机组NJ-3AP(KT)7-5-水阀反馈*)"},"LAHU03G05_WVB           AT%I114.0      :INT ; (*空调机组NJ-3AP(KT)7-5-水阀反馈*)",null,"AHU03G05_WVB",{"$f":"J113","v":"空调机组NJ-3AP(KT)7-5-水阀反馈"},{"$f":"AS112+1","v":30057}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)7-6-回风温度",{"$nulls":16},"NJ-3AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-6","03G06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH114,List!$B$3:$D$445,2,FALSE)&AJ114&\"_\"&VLOOKUP(AK114,List!$K$2:$M$447,2,FALSE)","v":"AHU03G06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM114&\" \"&\"AT%I\"&B113*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J114&\"*)\",\" \")","v":"LAHU03G06_RT AT%I116.0 :INT ; (*空调机组NJ-3AP(KT)7-6-回风温度*)"},"LAHU03G06_RT            AT%I116.0      :INT ; (*空调机组NJ-3AP(KT)7-6-回风温度*)",null,"AHU03G06_RT","空调机组NJ-3AP(KT)7-6-回风温度",{"$f":"AS113+1","v":30058}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-3AP(KT)7-6-水阀反馈",{"$nulls":16},"NJ-3AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-6","03G06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH115,List!$B$3:$D$445,2,FALSE)&AJ115&\"_\"&VLOOKUP(AK115,List!$K$2:$M$447,2,FALSE)","v":"AHU03G06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM115&\" \"&\"AT%I\"&B113*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J115&\"*)\",\" \")","v":"LAHU03G06_WVB AT%I118.0 :INT ; (*空调机组NJ-3AP(KT)7-6-水阀反馈*)"},"LAHU03G06_WVB           AT%I118.0      :INT ; (*空调机组NJ-3AP(KT)7-6-水阀反馈*)",null,"AHU03G06_WVB","空调机组NJ-3AP(KT)7-6-水阀反馈",30059]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-3AP(KT)7-7-回风温度",{"$nulls":16},"NJ-3AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-7","03G07","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH116,List!$B$3:$D$445,2,FALSE)&AJ116&\"_\"&VLOOKUP(AK116,List!$K$2:$M$447,2,FALSE)","v":"AHU03G07_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM116&\" \"&\"AT%I\"&B113*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J116&\"*)\",\" \")","v":"LAHU03G07_RT AT%I120.0 :INT ; (*空调机组NJ-3AP(KT)7-7-回风温度*)"},"LAHU03G07_RT            AT%I120.0      :INT ; (*空调机组NJ-3AP(KT)7-7-回风温度*)",null,"AHU03G07_RT","空调机组NJ-3AP(KT)7-7-回风温度",30060]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-3AP(KT)7-7-水阀反馈",{"$nulls":16},"NJ-3AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL117,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL117,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-7","03G07","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH117,List!$B$3:$D$445,2,FALSE)&AJ117&\"_\"&VLOOKUP(AK117,List!$K$2:$M$447,2,FALSE)","v":"AHU03G07_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM117&\" \"&\"AT%I\"&B113*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J117&\"*)\",\" \")","v":"LAHU03G07_WVB AT%I122.0 :INT ; (*空调机组NJ-3AP(KT)7-7-水阀反馈*)"},"LAHU03G07_WVB           AT%I122.0      :INT ; (*空调机组NJ-3AP(KT)7-7-水阀反馈*)",null,"AHU03G07_WVB",{"$f":"J117","v":"空调机组NJ-3AP(KT)7-7-水阀反馈"},30061]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-3AP(KT)7-8-回风温度",{"$nulls":16},"NJ-3AP(KT)7-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL118,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL118,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-8","03G08","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH118,List!$B$3:$D$445,2,FALSE)&AJ118&\"_\"&VLOOKUP(AK118,List!$K$2:$M$447,2,FALSE)","v":"AHU03G08_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM118&\" \"&\"AT%I\"&B113*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J118&\"*)\",\" \")","v":"LAHU03G08_RT AT%I124.0 :INT ; (*空调机组NJ-3AP(KT)7-8-回风温度*)"},"LAHU03G08_RT            AT%I124.0      :INT ; (*空调机组NJ-3AP(KT)7-8-回风温度*)",null,"AHU03G08_RT","空调机组NJ-3AP(KT)7-8-回风温度",30062]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-3AP(KT)7-8-水阀反馈",{"$nulls":16},{"$f":"IF(AI119=\"\",\"\",AI119)","v":"NJ-3AP(KT)7-8"},{"$f":"_xlfn.IFNA(VLOOKUP(AL119,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL119,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-8","03G08","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH119,List!$B$3:$D$445,2,FALSE)&AJ119&\"_\"&VLOOKUP(AK119,List!$K$2:$M$447,2,FALSE)","v":"AHU03G08_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM119&\" \"&\"AT%I\"&B113*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J119&\"*)\",\" \")","v":"LAHU03G08_WVB AT%I126.0 :INT ; (*空调机组NJ-3AP(KT)7-8-水阀反馈*)"},"LAHU03G08_WVB           AT%I126.0      :INT ; (*空调机组NJ-3AP(KT)7-8-水阀反馈*)",null,"AHU03G08_WVB","空调机组NJ-3AP(KT)7-8-水阀反馈",30063]
[null,{"$f":"B125","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B125&\"地址: \"&B122&\" *)\"","v":"(* IOM 0801U地址: 8 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH121&AA121&\"-\"&AK121","v":"空调机组NJ-3AP(KT)7-9-回风温度"},{"$nulls":16},{"$f":"IF(AI121=\"\",\"\",AI121)","v":"NJ-3AP(KT)7-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-9","03G09","回风温度",{"$f":"AH121&\"-\"&AK121","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH121,List!$B$3:$D$445,2,FALSE)&AJ121&\"_\"&VLOOKUP(AK121,List!$K$2:$M$447,2,FALSE)","v":"AHU03G09_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM121&\" \"&\"AT%I\"&B122*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J121&\"*)\",\" \")","v":"LAHU03G09_RT AT%I128.0 :INT ; (*空调机组NJ-3AP(KT)7-9-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121))),SEARCH(\":\",REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121)))))),\" \")","v":"LAHU03G09_RT            AT%I128.0      :INT ; (*空调机组NJ-3AP(KT)7-9-回风温度*)"},null,{"$f":"AM121","v":"AHU03G09_RT"},{"$f":"J121","v":"空调机组NJ-3AP(KT)7-9-回风温度"},{"$f":"30000+($B122*8+F121-1)","v":30064}]
[null,8,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-3AP(KT)7-9-水阀反馈",{"$nulls":16},{"$f":"IF(AI122=\"\",\"\",AI122)","v":"NJ-3AP(KT)7-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-9","03G09","水阀反馈",{"$f":"AH122&\"-\"&AK122","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH122,List!$B$3:$D$445,2,FALSE)&AJ122&\"_\"&VLOOKUP(AK122,List!$K$2:$M$447,2,FALSE)","v":"AHU03G09_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM122&\" \"&\"AT%I\"&B122*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J122&\"*)\",\" \")","v":"LAHU03G09_WVB AT%I130.0 :INT ; (*空调机组NJ-3AP(KT)7-9-水阀反馈*)"},"LAHU03G09_WVB           AT%I130.0      :INT ; (*空调机组NJ-3AP(KT)7-9-水阀反馈*)",null,"AHU03G09_WVB",{"$f":"J122","v":"空调机组NJ-3AP(KT)7-9-水阀反馈"},{"$f":"AS121+1","v":30065}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-3AP(KT)7-10-回风温度",{"$nulls":16},"NJ-3AP(KT)7-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-10","03G10","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH123,List!$B$3:$D$445,2,FALSE)&AJ123&\"_\"&VLOOKUP(AK123,List!$K$2:$M$447,2,FALSE)","v":"AHU03G10_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM123&\" \"&\"AT%I\"&B122*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J123&\"*)\",\" \")","v":"LAHU03G10_RT AT%I132.0 :INT ; (*空调机组NJ-3AP(KT)7-10-回风温度*)"},"LAHU03G10_RT            AT%I132.0      :INT ; (*空调机组NJ-3AP(KT)7-10-回风温度*)",null,"AHU03G10_RT","空调机组NJ-3AP(KT)7-10-回风温度",{"$f":"AS122+1","v":30066}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),2,1))","v":1},4,null,4,"0V","空调机组NJ-3AP(KT)7-10-水阀反馈",{"$nulls":16},"NJ-3AP(KT)7-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-10","03G10","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH124,List!$B$3:$D$445,2,FALSE)&AJ124&\"_\"&VLOOKUP(AK124,List!$K$2:$M$447,2,FALSE)","v":"AHU03G10_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM124&\" \"&\"AT%I\"&B122*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J124&\"*)\",\" \")","v":"LAHU03G10_WVB AT%I134.0 :INT ; (*空调机组NJ-3AP(KT)7-10-水阀反馈*)"},"LAHU03G10_WVB           AT%I134.0      :INT ; (*空调机组NJ-3AP(KT)7-10-水阀反馈*)",null,"AHU03G10_WVB","空调机组NJ-3AP(KT)7-10-水阀反馈",30067]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-3AP(KT)7-11-回风温度",{"$nulls":16},"NJ-3AP(KT)7-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-11","03G11","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH125,List!$B$3:$D$445,2,FALSE)&AJ125&\"_\"&VLOOKUP(AK125,List!$K$2:$M$447,2,FALSE)","v":"AHU03G11_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM125&\" \"&\"AT%I\"&B122*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J125&\"*)\",\" \")","v":"LAHU03G11_RT AT%I136.0 :INT ; (*空调机组NJ-3AP(KT)7-11-回风温度*)"},"LAHU03G11_RT            AT%I136.0      :INT ; (*空调机组NJ-3AP(KT)7-11-回风温度*)",null,"AHU03G11_RT","空调机组NJ-3AP(KT)7-11-回风温度",30068]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-3AP(KT)7-11-水阀反馈",{"$nulls":16},"NJ-3AP(KT)7-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL126,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL126,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-11","03G11","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH126,List!$B$3:$D$445,2,FALSE)&AJ126&\"_\"&VLOOKUP(AK126,List!$K$2:$M$447,2,FALSE)","v":"AHU03G11_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM126&\" \"&\"AT%I\"&B122*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J126&\"*)\",\" \")","v":"LAHU03G11_WVB AT%I138.0 :INT ; (*空调机组NJ-3AP(KT)7-11-水阀反馈*)"},"LAHU03G11_WVB           AT%I138.0      :INT ; (*空调机组NJ-3AP(KT)7-11-水阀反馈*)",null,"AHU03G11_WVB",{"$f":"J126","v":"空调机组NJ-3AP(KT)7-11-水阀反馈"},30069]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-3AP(KT)7-12-回风温度",{"$nulls":16},"NJ-3AP(KT)7-12",{"$f":"_xlfn.IFNA(VLOOKUP(AL127,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL127,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-12","03G12","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH127,List!$B$3:$D$445,2,FALSE)&AJ127&\"_\"&VLOOKUP(AK127,List!$K$2:$M$447,2,FALSE)","v":"AHU03G12_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM127&\" \"&\"AT%I\"&B122*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J127&\"*)\",\" \")","v":"LAHU03G12_RT AT%I140.0 :INT ; (*空调机组NJ-3AP(KT)7-12-回风温度*)"},"LAHU03G12_RT            AT%I140.0      :INT ; (*空调机组NJ-3AP(KT)7-12-回风温度*)",null,"AHU03G12_RT","空调机组NJ-3AP(KT)7-12-回风温度",30070]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-3AP(KT)7-12-水阀反馈",{"$nulls":16},{"$f":"IF(AI128=\"\",\"\",AI128)","v":"NJ-3AP(KT)7-12"},{"$f":"_xlfn.IFNA(VLOOKUP(AL128,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL128,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-12","03G12","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH128,List!$B$3:$D$445,2,FALSE)&AJ128&\"_\"&VLOOKUP(AK128,List!$K$2:$M$447,2,FALSE)","v":"AHU03G12_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM128&\" \"&\"AT%I\"&B122*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J128&\"*)\",\" \")","v":"LAHU03G12_WVB AT%I142.0 :INT ; (*空调机组NJ-3AP(KT)7-12-水阀反馈*)"},"LAHU03G12_WVB           AT%I142.0      :INT ; (*空调机组NJ-3AP(KT)7-12-水阀反馈*)",null,"AHU03G12_WVB","空调机组NJ-3AP(KT)7-12-水阀反馈",30071]
[null,{"$f":"B134","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B134&\"地址: \"&B131&\" *)\"","v":"(* IOM 0401A地址: 9 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH130&AA130&\"-\"&AK130","v":"空调机组NJ-3AP(KT)7-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI130=\"\",\"\",AI130)","v":"NJ-3AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL130,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL130,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-1","03G01","水阀控制",{"$f":"AH130&\"-\"&AK130","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH130,List!$B$3:$D$445,2,FALSE)&AJ130&\"_\"&VLOOKUP(AK130,List!$K$2:$M$447,2,FALSE)","v":"AHU03G01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM130&\" \"&\"AT%Q\"&B131*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J130&\"*)\",\" \")","v":"LAHU03G01_WVC AT%Q144.0 :INT ; (*空调机组NJ-3AP(KT)7-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN130,SEARCH(\"AT%\",AN130),,REPT(\" \",25-SEARCH(\"AT%\",AN130))),SEARCH(\":\",REPLACE(AN130,SEARCH(\"AT%\",AN130),,REPT(\" \",25-SEARCH(\"AT%\",AN130)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN130,SEARCH(\"AT%\",AN130),,REPT(\" \",25-SEARCH(\"AT%\",AN130)))))),\" \")","v":"LAHU03G01_WVC           AT%Q144.0      :INT ; (*空调机组NJ-3AP(KT)7-1-水阀控制*)"},null,{"$f":"AM130","v":"AHU03G01_WVC"},{"$f":"J130","v":"空调机组NJ-3AP(KT)7-1-水阀控制"},{"$f":"40000+($B131*8+F130-1)","v":40072}]
[null,9,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH131&AA131&\"-\"&AK131","v":"空调机组NJ-3AP(KT)7-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI131=\"\",\"\",AI131)","v":"NJ-3AP(KT)7-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL131,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL131,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-2","03G02","水阀控制",{"$f":"AH131&\"-\"&AK131","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH131,List!$B$3:$D$445,2,FALSE)&AJ131&\"_\"&VLOOKUP(AK131,List!$K$2:$M$447,2,FALSE)","v":"AHU03G02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM131&\" \"&\"AT%Q\"&B131*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J131&\"*)\",\" \")","v":"LAHU03G02_WVC AT%Q146.0 :INT ; (*空调机组NJ-3AP(KT)7-2-水阀控制*)"},"LAHU03G02_WVC           AT%Q146.0      :INT ; (*空调机组NJ-3AP(KT)7-2-水阀控制*)",null,"AHU03G02_WVC",{"$f":"J131","v":"空调机组NJ-3AP(KT)7-2-水阀控制"},{"$f":"AS130+1","v":40073}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH132&AA132&\"-\"&AK132","v":"空调机组NJ-3AP(KT)7-3-水阀控制"},{"$nulls":16},"NJ-3AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL132,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL132,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-3","03G03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH132,List!$B$3:$D$445,2,FALSE)&AJ132&\"_\"&VLOOKUP(AK132,List!$K$2:$M$447,2,FALSE)","v":"AHU03G03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM132&\" \"&\"AT%Q\"&B131*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J132&\"*)\",\" \")","v":"LAHU03G03_WVC AT%Q148.0 :INT ; (*空调机组NJ-3AP(KT)7-3-水阀控制*)"},"LAHU03G03_WVC           AT%Q148.0      :INT ; (*空调机组NJ-3AP(KT)7-3-水阀控制*)",null,"AHU03G03_WVC","空调机组NJ-3AP(KT)7-3-水阀控制",{"$f":"AS131+1","v":40074}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH133&AA133&\"-\"&AK133","v":"空调机组NJ-3AP(KT)7-4-水阀控制"},{"$nulls":16},"NJ-3AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL133,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL133,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-4","03G04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH133,List!$B$3:$D$445,2,FALSE)&AJ133&\"_\"&VLOOKUP(AK133,List!$K$2:$M$447,2,FALSE)","v":"AHU03G04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM133&\" \"&\"AT%Q\"&B131*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J133&\"*)\",\" \")","v":"LAHU03G04_WVC AT%Q150.0 :INT ; (*空调机组NJ-3AP(KT)7-4-水阀控制*)"},"LAHU03G04_WVC           AT%Q150.0      :INT ; (*空调机组NJ-3AP(KT)7-4-水阀控制*)",null,"AHU03G04_WVC","空调机组NJ-3AP(KT)7-4-水阀控制",40075]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B143","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B143&\"地址: \"&B140&\" *)\"","v":"(* IOM 0401A地址: 10 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH139&AA139&\"-\"&AK139","v":"空调机组NJ-3AP(KT)7-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI139=\"\",\"\",AI139)","v":"NJ-3AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL139,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL139,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-5","03G05","水阀控制",{"$f":"AH139&\"-\"&AK139","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH139,List!$B$3:$D$445,2,FALSE)&AJ139&\"_\"&VLOOKUP(AK139,List!$K$2:$M$447,2,FALSE)","v":"AHU03G05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM139&\" \"&\"AT%Q\"&B140*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J139&\"*)\",\" \")","v":"LAHU03G05_WVC AT%Q160.0 :INT ; (*空调机组NJ-3AP(KT)7-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN139,SEARCH(\"AT%\",AN139),,REPT(\" \",25-SEARCH(\"AT%\",AN139))),SEARCH(\":\",REPLACE(AN139,SEARCH(\"AT%\",AN139),,REPT(\" \",25-SEARCH(\"AT%\",AN139)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN139,SEARCH(\"AT%\",AN139),,REPT(\" \",25-SEARCH(\"AT%\",AN139)))))),\" \")","v":"LAHU03G05_WVC           AT%Q160.0      :INT ; (*空调机组NJ-3AP(KT)7-5-水阀控制*)"},null,{"$f":"AM139","v":"AHU03G05_WVC"},{"$f":"J139","v":"空调机组NJ-3AP(KT)7-5-水阀控制"},{"$f":"40000+($B140*8+F139-1)","v":40080}]
[null,10,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH140&AA140&\"-\"&AK140","v":"空调机组NJ-3AP(KT)7-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI140=\"\",\"\",AI140)","v":"NJ-3AP(KT)7-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL140,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL140,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-6","03G06","水阀控制",{"$f":"AH140&\"-\"&AK140","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH140,List!$B$3:$D$445,2,FALSE)&AJ140&\"_\"&VLOOKUP(AK140,List!$K$2:$M$447,2,FALSE)","v":"AHU03G06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM140&\" \"&\"AT%Q\"&B140*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J140&\"*)\",\" \")","v":"LAHU03G06_WVC AT%Q162.0 :INT ; (*空调机组NJ-3AP(KT)7-6-水阀控制*)"},"LAHU03G06_WVC           AT%Q162.0      :INT ; (*空调机组NJ-3AP(KT)7-6-水阀控制*)",null,"AHU03G06_WVC",{"$f":"J140","v":"空调机组NJ-3AP(KT)7-6-水阀控制"},{"$f":"AS139+1","v":40081}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH141&AA141&\"-\"&AK141","v":"空调机组NJ-3AP(KT)7-7-水阀控制"},{"$nulls":16},"NJ-3AP(KT)7-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL141,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL141,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-7","03G07","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH141,List!$B$3:$D$445,2,FALSE)&AJ141&\"_\"&VLOOKUP(AK141,List!$K$2:$M$447,2,FALSE)","v":"AHU03G07_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM141&\" \"&\"AT%Q\"&B140*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J141&\"*)\",\" \")","v":"LAHU03G07_WVC AT%Q164.0 :INT ; (*空调机组NJ-3AP(KT)7-7-水阀控制*)"},"LAHU03G07_WVC           AT%Q164.0      :INT ; (*空调机组NJ-3AP(KT)7-7-水阀控制*)",null,"AHU03G07_WVC","空调机组NJ-3AP(KT)7-7-水阀控制",{"$f":"AS140+1","v":40082}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH142&AA142&\"-\"&AK142","v":"空调机组NJ-3AP(KT)7-8-水阀控制"},{"$nulls":16},"NJ-3AP(KT)7-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL142,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL142,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-8","03G08","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH142,List!$B$3:$D$445,2,FALSE)&AJ142&\"_\"&VLOOKUP(AK142,List!$K$2:$M$447,2,FALSE)","v":"AHU03G08_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM142&\" \"&\"AT%Q\"&B140*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J142&\"*)\",\" \")","v":"LAHU03G08_WVC AT%Q166.0 :INT ; (*空调机组NJ-3AP(KT)7-8-水阀控制*)"},"LAHU03G08_WVC           AT%Q166.0      :INT ; (*空调机组NJ-3AP(KT)7-8-水阀控制*)",null,"AHU03G08_WVC","空调机组NJ-3AP(KT)7-8-水阀控制",40083]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B140),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B142=20,1,IF(B142=50,10,IF(B142=125,11,IF(B142=250,100,IF(B142=500,101,IF(B142=800,110,IF(B142=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B142=20,1,IF(B142=50,10,IF(B142=125,11,IF(B142=250,100,IF(B142=500,101,IF(B142=800,110,IF(B142=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B142=20,1,IF(B142=50,10,IF(B142=125,11,IF(B142=250,100,IF(B142=500,101,IF(B142=800,110,IF(B142=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B142=20,1,IF(B142=50,10,IF(B142=125,11,IF(B142=250,100,IF(B142=500,101,IF(B142=800,110,IF(B142=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B142=20,1,IF(B142=50,10,IF(B142=125,11,IF(B142=250,100,IF(B142=500,101,IF(B142=800,110,IF(B142=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B142=20,1,IF(B142=50,10,IF(B142=125,11,IF(B142=250,100,IF(B142=500,101,IF(B142=800,110,IF(B142=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B152","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B152&\"地址: \"&B149&\" *)\"","v":"(* IOM 0401A地址: 11 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH148&AA148&\"-\"&AK148","v":"空调机组NJ-3AP(KT)7-9-水阀控制"},{"$nulls":16},{"$f":"IF(AI148=\"\",\"\",AI148)","v":"NJ-3AP(KT)7-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL148,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL148,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-9","03G09","水阀控制",{"$f":"AH148&\"-\"&AK148","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH148,List!$B$3:$D$445,2,FALSE)&AJ148&\"_\"&VLOOKUP(AK148,List!$K$2:$M$447,2,FALSE)","v":"AHU03G09_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM148&\" \"&\"AT%Q\"&B149*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J148&\"*)\",\" \")","v":"LAHU03G09_WVC AT%Q176.0 :INT ; (*空调机组NJ-3AP(KT)7-9-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN148,SEARCH(\"AT%\",AN148),,REPT(\" \",25-SEARCH(\"AT%\",AN148))),SEARCH(\":\",REPLACE(AN148,SEARCH(\"AT%\",AN148),,REPT(\" \",25-SEARCH(\"AT%\",AN148)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN148,SEARCH(\"AT%\",AN148),,REPT(\" \",25-SEARCH(\"AT%\",AN148)))))),\" \")","v":"LAHU03G09_WVC           AT%Q176.0      :INT ; (*空调机组NJ-3AP(KT)7-9-水阀控制*)"},null,{"$f":"AM148","v":"AHU03G09_WVC"},{"$f":"J148","v":"空调机组NJ-3AP(KT)7-9-水阀控制"},{"$f":"40000+($B149*8+F148-1)","v":40088}]
[null,11,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH149&AA149&\"-\"&AK149","v":"空调机组NJ-3AP(KT)7-10-水阀控制"},{"$nulls":16},{"$f":"IF(AI149=\"\",\"\",AI149)","v":"NJ-3AP(KT)7-10"},{"$f":"_xlfn.IFNA(VLOOKUP(AL149,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL149,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-10","03G10","水阀控制",{"$f":"AH149&\"-\"&AK149","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH149,List!$B$3:$D$445,2,FALSE)&AJ149&\"_\"&VLOOKUP(AK149,List!$K$2:$M$447,2,FALSE)","v":"AHU03G10_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM149&\" \"&\"AT%Q\"&B149*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J149&\"*)\",\" \")","v":"LAHU03G10_WVC AT%Q178.0 :INT ; (*空调机组NJ-3AP(KT)7-10-水阀控制*)"},"LAHU03G10_WVC           AT%Q178.0      :INT ; (*空调机组NJ-3AP(KT)7-10-水阀控制*)",null,"AHU03G10_WVC",{"$f":"J149","v":"空调机组NJ-3AP(KT)7-10-水阀控制"},{"$f":"AS148+1","v":40089}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH150&AA150&\"-\"&AK150","v":"空调机组NJ-3AP(KT)7-11-水阀控制"},{"$nulls":16},"NJ-3AP(KT)7-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL150,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL150,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-11","03G11","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH150,List!$B$3:$D$445,2,FALSE)&AJ150&\"_\"&VLOOKUP(AK150,List!$K$2:$M$447,2,FALSE)","v":"AHU03G11_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM150&\" \"&\"AT%Q\"&B149*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J150&\"*)\",\" \")","v":"LAHU03G11_WVC AT%Q180.0 :INT ; (*空调机组NJ-3AP(KT)7-11-水阀控制*)"},"LAHU03G11_WVC           AT%Q180.0      :INT ; (*空调机组NJ-3AP(KT)7-11-水阀控制*)",null,"AHU03G11_WVC","空调机组NJ-3AP(KT)7-11-水阀控制",{"$f":"AS149+1","v":40090}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH151&AA151&\"-\"&AK151","v":"空调机组NJ-3AP(KT)7-12-水阀控制"},{"$nulls":16},"NJ-3AP(KT)7-12",{"$f":"_xlfn.IFNA(VLOOKUP(AL151,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL151,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)7-12","03G12","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH151,List!$B$3:$D$445,2,FALSE)&AJ151&\"_\"&VLOOKUP(AK151,List!$K$2:$M$447,2,FALSE)","v":"AHU03G12_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM151&\" \"&\"AT%Q\"&B149*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J151&\"*)\",\" \")","v":"LAHU03G12_WVC AT%Q182.0 :INT ; (*空调机组NJ-3AP(KT)7-12-水阀控制*)"},"LAHU03G12_WVC           AT%Q182.0      :INT ; (*空调机组NJ-3AP(KT)7-12-水阀控制*)",null,"AHU03G12_WVC","空调机组NJ-3AP(KT)7-12-水阀控制",40091]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B149),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B151=20,1,IF(B151=50,10,IF(B151=125,11,IF(B151=250,100,IF(B151=500,101,IF(B151=800,110,IF(B151=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B151=20,1,IF(B151=50,10,IF(B151=125,11,IF(B151=250,100,IF(B151=500,101,IF(B151=800,110,IF(B151=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B151=20,1,IF(B151=50,10,IF(B151=125,11,IF(B151=250,100,IF(B151=500,101,IF(B151=800,110,IF(B151=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B151=20,1,IF(B151=50,10,IF(B151=125,11,IF(B151=250,100,IF(B151=500,101,IF(B151=800,110,IF(B151=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B151=20,1,IF(B151=50,10,IF(B151=125,11,IF(B151=250,100,IF(B151=500,101,IF(B151=800,110,IF(B151=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B151=20,1,IF(B151=50,10,IF(B151=125,11,IF(B151=250,100,IF(B151=500,101,IF(B151=800,110,IF(B151=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L407","index":41,"n_rows":111,"n_cols":45,"rows_kept":111,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[41,5,41,6],[41,9,41,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[92,5,92,6],[92,9,92,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[101,5,101,6],[101,9,101,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[109,5,109,6],[109,9,109,25],[110,5,110,6],[110,9,110,25],[4,1,5,1],[11,1,22,1],[28,1,39,1],[45,1,48,1],[54,1,65,1],[71,1,74,1],[80,1,83,1],[89,1,92,1],[98,1,101,1],[107,1,110,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4],[32,2,39,4],[58,2,65,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L25",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 12 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH8&AA8&\"-\"&AK8","v":"空调机组NJ-4AP(KT)7-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-4AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-1","04G01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH8,List!$B$3:$D$445,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,List!$K$2:$M$447,2,FALSE)","v":"AHU04G01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LAHU04G01_R AT%I192.0 :BOOL; (*空调机组NJ-4AP(KT)7-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LAHU04G01_R             AT%I192.0      :BOOL; (*空调机组NJ-4AP(KT)7-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L25\\L25AHU04G01_R"},{"$f":"J8","v":"空调机组NJ-4AP(KT)7-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":11536}]
[null,12,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-4AP(KT)7-1-故障状态",{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-4AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-1","04G01","故障状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU04G01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU04G01_F AT%I192.1 :BOOL; (*空调机组NJ-4AP(KT)7-1-故障状态*)"},"LAHU04G01_F             AT%I192.1      :BOOL; (*空调机组NJ-4AP(KT)7-1-故障状态*)",null,"L25\\L25AHU04G01_F",{"$f":"J9","v":"空调机组NJ-4AP(KT)7-1-故障状态"},{"$f":"AS8+1","v":11537}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},3,null,5,6,"空调机组NJ-4AP(KT)7-1-自动状态",{"$nulls":16},"NJ-4AP(KT)7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-1","04G01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU04G01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU04G01_A AT%I192.2 :BOOL; (*空调机组NJ-4AP(KT)7-1-自动状态*)"},"LAHU04G01_A             AT%I192.2      :BOOL; (*空调机组NJ-4AP(KT)7-1-自动状态*)",null,"L25\\L25AHU04G01_A","空调机组NJ-4AP(KT)7-1-自动状态",{"$f":"AS9+1","v":11538}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-4AP(KT)7-1-风机压差",{"$nulls":16},"NJ-4AP(KT)7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-1","04G01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU04G01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU04G01_FPS AT%I192.3 :BOOL; (*空调机组NJ-4AP(KT)7-1-风机压差*)"},"LAHU04G01_FPS           AT%I192.3      :BOOL; (*空调机组NJ-4AP(KT)7-1-风机压差*)",null,"L25\\L25AHU04G01_FPS","空调机组NJ-4AP(KT)7-1-风机压差",11539]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-4AP(KT)7-2-运行状态",{"$nulls":16},"NJ-4AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-2","04G02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU04G02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU04G02_R AT%I192.4 :BOOL; (*空调机组NJ-4AP(KT)7-2-运行状态*)"},"LAHU04G02_R             AT%I192.4      :BOOL; (*空调机组NJ-4AP(KT)7-2-运行状态*)",null,"L25\\L25AHU04G02_R","空调机组NJ-4AP(KT)7-2-运行状态",11540]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-4AP(KT)7-2-故障状态",{"$nulls":16},"NJ-4AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-2","04G02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU04G02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU04G02_F AT%I192.5 :BOOL; (*空调机组NJ-4AP(KT)7-2-故障状态*)"},"LAHU04G02_F             AT%I192.5      :BOOL; (*空调机组NJ-4AP(KT)7-2-故障状态*)",null,"L25\\L25AHU04G02_F","空调机组NJ-4AP(KT)7-2-故障状态",11541]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-4AP(KT)7-2-自动状态",{"$nulls":16},"NJ-4AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-2","04G02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU04G02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU04G02_A AT%I192.6 :BOOL; (*空调机组NJ-4AP(KT)7-2-自动状态*)"},"LAHU04G02_A             AT%I192.6      :BOOL; (*空调机组NJ-4AP(KT)7-2-自动状态*)",null,"L25\\L25AHU04G02_A","空调机组NJ-4AP(KT)7-2-自动状态",11542]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-4AP(KT)7-2-风机压差",{"$nulls":16},"NJ-4AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-2","04G02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU04G02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU04G02_FPS AT%I192.7 :BOOL; (*空调机组NJ-4AP(KT)7-2-风机压差*)"},"LAHU04G02_FPS           AT%I192.7      :BOOL; (*空调机组NJ-4AP(KT)7-2-风机压差*)",null,"L25\\L25AHU04G02_FPS","空调机组NJ-4AP(KT)7-2-风机压差",11543]
[{"$nulls":5},9,null,17,18,"空调机组NJ-4AP(KT)7-3-运行状态",{"$nulls":16},"NJ-4AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-3","04G03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU04G03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU04G03_R AT%I193.0 :BOOL; (*空调机组NJ-4AP(KT)7-3-运行状态*)"},"LAHU04G03_R             AT%I193.0      :BOOL; (*空调机组NJ-4AP(KT)7-3-运行状态*)",null,"L25\\L25AHU04G03_R","空调机组NJ-4AP(KT)7-3-运行状态",11544]
[{"$nulls":5},10,null,19,20,"空调机组NJ-4AP(KT)7-3-故障状态",{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-4AP(KT)7-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-3","04G03","故障状态",{"$f":"AH17&\"-\"&AK17","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU04G03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU04G03_F AT%I193.1 :BOOL; (*空调机组NJ-4AP(KT)7-3-故障状态*)"},"LAHU04G03_F             AT%I193.1      :BOOL; (*空调机组NJ-4AP(KT)7-3-故障状态*)",null,"L25\\L25AHU04G03_F","空调机组NJ-4AP(KT)7-3-故障状态",11545]
[{"$nulls":5},11,null,21,22,"空调机组NJ-4AP(KT)7-3-自动状态",{"$nulls":16},"NJ-4AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-3","04G03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU04G03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU04G03_A AT%I193.2 :BOOL; (*空调机组NJ-4AP(KT)7-3-自动状态*)"},"LAHU04G03_A             AT%I193.2      :BOOL; (*空调机组NJ-4AP(KT)7-3-自动状态*)",null,"L25\\L25AHU04G03_A","空调机组NJ-4AP(KT)7-3-自动状态",11546]
[{"$nulls":5},12,null,23,24,"空调机组NJ-4AP(KT)7-3-风机压差",{"$nulls":16},"NJ-4AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-3","04G03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU04G03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU04G03_FPS AT%I193.3 :BOOL; (*空调机组NJ-4AP(KT)7-3-风机压差*)"},"LAHU04G03_FPS           AT%I193.3      :BOOL; (*空调机组NJ-4AP(KT)7-3-风机压差*)",null,"L25\\L25AHU04G03_FPS","空调机组NJ-4AP(KT)7-3-风机压差",11547]
[{"$nulls":5},13,null,25,26,"空调机组NJ-4AP(KT)7-4-运行状态",{"$nulls":16},"NJ-4AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-4","04G04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU04G04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU04G04_R AT%I193.4 :BOOL; (*空调机组NJ-4AP(KT)7-4-运行状态*)"},"LAHU04G04_R             AT%I193.4      :BOOL; (*空调机组NJ-4AP(KT)7-4-运行状态*)",null,"L25\\L25AHU04G04_R","空调机组NJ-4AP(KT)7-4-运行状态",11548]
[{"$nulls":5},14,null,27,28,"空调机组NJ-4AP(KT)7-4-故障状态",{"$nulls":16},"NJ-4AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-4","04G04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU04G04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU04G04_F AT%I193.5 :BOOL; (*空调机组NJ-4AP(KT)7-4-故障状态*)"},"LAHU04G04_F             AT%I193.5      :BOOL; (*空调机组NJ-4AP(KT)7-4-故障状态*)",null,"L25\\L25AHU04G04_F","空调机组NJ-4AP(KT)7-4-故障状态",11549]
[{"$nulls":5},15,null,29,30,"空调机组NJ-4AP(KT)7-4-自动状态",{"$nulls":16},"NJ-4AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-4","04G04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU04G04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU04G04_A AT%I193.6 :BOOL; (*空调机组NJ-4AP(KT)7-4-自动状态*)"},"LAHU04G04_A             AT%I193.6      :BOOL; (*空调机组NJ-4AP(KT)7-4-自动状态*)",null,"L25\\L25AHU04G04_A","空调机组NJ-4AP(KT)7-4-自动状态",11550]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-4AP(KT)7-4-风机压差",{"$nulls":16},"NJ-4AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-4","04G04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU04G04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU04G04_FPS AT%I193.7 :BOOL; (*空调机组NJ-4AP(KT)7-4-风机压差*)"},"LAHU04G04_FPS           AT%I193.7      :BOOL; (*空调机组NJ-4AP(KT)7-4-风机压差*)",null,"L25\\L25AHU04G04_FPS","空调机组NJ-4AP(KT)7-4-风机压差",11551]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 1601R地址: 13 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH25&AA25&\"-\"&AK25","v":"空调机组NJ-4AP(KT)7-5-运行状态"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-4AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-5","04G05","运行状态",{"$f":"AH25&\"-\"&AK25","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"AHU04G05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LAHU04G05_R AT%I208.0 :BOOL; (*空调机组NJ-4AP(KT)7-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LAHU04G05_R             AT%I208.0      :BOOL; (*空调机组NJ-4AP(KT)7-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L25\\L25AHU04G05_R"},{"$f":"J25","v":"空调机组NJ-4AP(KT)7-5-运行状态"},{"$f":"10000+($B26*16*8+F25-1)","v":11664}]
[null,13,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-4AP(KT)7-5-故障状态",{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-4AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-5","04G05","故障状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU04G05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU04G05_F AT%I208.1 :BOOL; (*空调机组NJ-4AP(KT)7-5-故障状态*)"},"LAHU04G05_F             AT%I208.1      :BOOL; (*空调机组NJ-4AP(KT)7-5-故障状态*)",null,"L25\\L25AHU04G05_F",{"$f":"J26","v":"空调机组NJ-4AP(KT)7-5-故障状态"},{"$f":"AS25+1","v":11665}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},3,null,5,6,"空调机组NJ-4AP(KT)7-5-自动状态",{"$nulls":16},"NJ-4AP(KT)7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-5","04G05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU04G05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU04G05_A AT%I208.2 :BOOL; (*空调机组NJ-4AP(KT)7-5-自动状态*)"},"LAHU04G05_A             AT%I208.2      :BOOL; (*空调机组NJ-4AP(KT)7-5-自动状态*)",null,"L25\\L25AHU04G05_A","空调机组NJ-4AP(KT)7-5-自动状态",{"$f":"AS26+1","v":11666}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-4AP(KT)7-5-风机压差",{"$nulls":16},"NJ-4AP(KT)7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-5","04G05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU04G05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU04G05_FPS AT%I208.3 :BOOL; (*空调机组NJ-4AP(KT)7-5-风机压差*)"},"LAHU04G05_FPS           AT%I208.3      :BOOL; (*空调机组NJ-4AP(KT)7-5-风机压差*)",null,"L25\\L25AHU04G05_FPS","空调机组NJ-4AP(KT)7-5-风机压差",11667]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-4AP(KT)7-6-运行状态",{"$nulls":16},"NJ-4AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-6","04G06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU04G06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU04G06_R AT%I208.4 :BOOL; (*空调机组NJ-4AP(KT)7-6-运行状态*)"},"LAHU04G06_R             AT%I208.4      :BOOL; (*空调机组NJ-4AP(KT)7-6-运行状态*)",null,"L25\\L25AHU04G06_R","空调机组NJ-4AP(KT)7-6-运行状态",11668]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-4AP(KT)7-6-故障状态",{"$nulls":16},"NJ-4AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-6","04G06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU04G06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU04G06_F AT%I208.5 :BOOL; (*空调机组NJ-4AP(KT)7-6-故障状态*)"},"LAHU04G06_F             AT%I208.5      :BOOL; (*空调机组NJ-4AP(KT)7-6-故障状态*)",null,"L25\\L25AHU04G06_F","空调机组NJ-4AP(KT)7-6-故障状态",11669]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-4AP(KT)7-6-自动状态",{"$nulls":16},"NJ-4AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-6","04G06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU04G06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU04G06_A AT%I208.6 :BOOL; (*空调机组NJ-4AP(KT)7-6-自动状态*)"},"LAHU04G06_A             AT%I208.6      :BOOL; (*空调机组NJ-4AP(KT)7-6-自动状态*)",null,"L25\\L25AHU04G06_A","空调机组NJ-4AP(KT)7-6-自动状态",11670]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-4AP(KT)7-6-风机压差",{"$nulls":16},"NJ-4AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-6","04G06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU04G06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU04G06_FPS AT%I208.7 :BOOL; (*空调机组NJ-4AP(KT)7-6-风机压差*)"},"LAHU04G06_FPS           AT%I208.7      :BOOL; (*空调机组NJ-4AP(KT)7-6-风机压差*)",null,"L25\\L25AHU04G06_FPS","空调机组NJ-4AP(KT)7-6-风机压差",11671]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-4AL7-1-运行状态",{"$nulls":16},"NJ-4AL7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL7-1","04G01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"LCB04G01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B26*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LLCB04G01_R AT%I209.0 :BOOL; (*照明控制箱NJ-4AL7-1-运行状态*)"},"LLCB04G01_R             AT%I209.0      :BOOL; (*照明控制箱NJ-4AL7-1-运行状态*)",null,"L25\\L25LCB04G01_R","照明控制箱NJ-4AL7-1-运行状态",11672]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-4AL7-1-自动状态",{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-4AL7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL7-1","04G01","自动状态",{"$f":"AH34&\"-\"&AK34","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"LCB04G01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B26*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LLCB04G01_A AT%I209.1 :BOOL; (*照明控制箱NJ-4AL7-1-自动状态*)"},"LLCB04G01_A             AT%I209.1      :BOOL; (*照明控制箱NJ-4AL7-1-自动状态*)",null,"L25\\L25LCB04G01_A",{"$f":"J34","v":"照明控制箱NJ-4AL7-1-自动状态"},11673]
[{"$nulls":5},11,null,21,22,"照明控制箱NJ-4AL7-2-运行状态",{"$nulls":16},"NJ-4AL7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL7-2","04G02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"LCB04G02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B26*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LLCB04G02_R AT%I209.2 :BOOL; (*照明控制箱NJ-4AL7-2-运行状态*)"},"LLCB04G02_R             AT%I209.2      :BOOL; (*照明控制箱NJ-4AL7-2-运行状态*)",null,"L25\\L25LCB04G02_R","照明控制箱NJ-4AL7-2-运行状态",11674]
[{"$nulls":5},12,null,23,24,"照明控制箱NJ-4AL7-2-自动状态",{"$nulls":16},"NJ-4AL7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL7-2","04G02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"LCB04G02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B26*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LLCB04G02_A AT%I209.3 :BOOL; (*照明控制箱NJ-4AL7-2-自动状态*)"},"LLCB04G02_A             AT%I209.3      :BOOL; (*照明控制箱NJ-4AL7-2-自动状态*)",null,"L25\\L25LCB04G02_A","照明控制箱NJ-4AL7-2-自动状态",11675]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-4AL7-3-运行状态",{"$nulls":16},"NJ-4AL7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL7-3","04G03","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"LCB04G03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B26*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LLCB04G03_R AT%I209.4 :BOOL; (*照明控制箱NJ-4AL7-3-运行状态*)"},"LLCB04G03_R             AT%I209.4      :BOOL; (*照明控制箱NJ-4AL7-3-运行状态*)",null,"L25\\L25LCB04G03_R","照明控制箱NJ-4AL7-3-运行状态",11676]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-4AL7-3-自动状态",{"$nulls":16},"NJ-4AL7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL7-3","04G03","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB04G03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B26*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB04G03_A AT%I209.5 :BOOL; (*照明控制箱NJ-4AL7-3-自动状态*)"},"LLCB04G03_A             AT%I209.5      :BOOL; (*照明控制箱NJ-4AL7-3-自动状态*)",null,"L25\\L25LCB04G03_A","照明控制箱NJ-4AL7-3-自动状态",11677]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-4AL7-4-运行状态",{"$nulls":16},"NJ-4AL7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL7-4","04G04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"LCB04G04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B26*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LLCB04G04_R AT%I209.6 :BOOL; (*照明控制箱NJ-4AL7-4-运行状态*)"},"LLCB04G04_R             AT%I209.6      :BOOL; (*照明控制箱NJ-4AL7-4-运行状态*)",null,"L25\\L25LCB04G04_R","照明控制箱NJ-4AL7-4-运行状态",11678]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-4AL7-4-自动状态",{"$nulls":16},"NJ-4AL7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL7-4","04G04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"LCB04G04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B26*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LLCB04G04_A AT%I209.7 :BOOL; (*照明控制箱NJ-4AL7-4-自动状态*)"},"LLCB04G04_A             AT%I209.7      :BOOL; (*照明控制箱NJ-4AL7-4-自动状态*)",null,"L25\\L25LCB04G04_A","照明控制箱NJ-4AL7-4-自动状态",11679]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B46&\"地址: \"&B43&\" *)\"","v":"(* IOM 0801R 地址: 14 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH42&AA42&\"-\"&AK42","v":"照明控制箱NJ-4AL7-5-运行状态"},{"$nulls":16},{"$f":"IF(AI42=\"\",\"\",AI42)","v":"NJ-4AL7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL7-5","04G05","运行状态",{"$f":"AH42&\"-\"&AK42","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":"LCB04G05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%I\"&B43*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":"LLCB04G05_R AT%I224.0 :BOOL; (*照明控制箱NJ-4AL7-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42))),SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))))),\" \")","v":"LLCB04G05_R             AT%I224.0      :BOOL; (*照明控制箱NJ-4AL7-5-运行状态*)"},null,{"$f":"AM42","v":"LCB04G05_R"},{"$f":"J42","v":"照明控制箱NJ-4AL7-5-运行状态"},{"$f":"10000+($B43*16*8+F42-1)","v":11792}]
[null,14,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":1},2,null,2,"C",{"$f":"AH43&AA43&\"-\"&AK43","v":"照明控制箱NJ-4AL7-5-自动状态"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-4AL7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL7-5","04G05","自动状态",{"$f":"AH43&\"-\"&AK43","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"LCB04G05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B43*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LLCB04G05_A AT%I224.1 :BOOL; (*照明控制箱NJ-4AL7-5-自动状态*)"},"LLCB04G05_A             AT%I224.1      :BOOL; (*照明控制箱NJ-4AL7-5-自动状态*)",null,{"$f":"AM43","v":"LCB04G05_A"},{"$f":"J43","v":"照明控制箱NJ-4AL7-5-自动状态"},{"$f":"AS42+1","v":11793}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":1},3,null,3,"C",{"$f":"AH44&AA44&\"-\"&AK44","v":"排风机NJ-4AP(KT)7-1-运行状态"},{"$nulls":16},"NJ-4AP(KT)7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)7-1","04G01","运行状态","排风机-运行状态",{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"EAF04G01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B43*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LEAF04G01_R AT%I224.2 :BOOL; (*排风机NJ-4AP(KT)7-1-运行状态*)"},"LEAF04G01_R             AT%I224.2      :BOOL; (*排风机NJ-4AP(KT)7-1-运行状态*)",null,"EAF04G01_R","排风机NJ-4AP(KT)7-1-运行状态",{"$f":"AS43+1","v":11794}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},4,null,4,"C",{"$f":"AH45&AA45&\"-\"&AK45","v":"排风机NJ-4AP(KT)7-1-故障状态"},{"$nulls":16},"NJ-4AP(KT)7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)7-1","04G01","故障状态","排风机-故障状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"EAF04G01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B43*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LEAF04G01_F AT%I224.3 :BOOL; (*排风机NJ-4AP(KT)7-1-故障状态*)"},"LEAF04G01_F             AT%I224.3      :BOOL; (*排风机NJ-4AP(KT)7-1-故障状态*)",null,"EAF04G01_F","排风机NJ-4AP(KT)7-1-故障状态",11795]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},5,null,5,"C","排风机NJ-4AP(KT)7-1-自动状态",{"$nulls":16},"NJ-4AP(KT)7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)7-1","04G01","自动状态","排风机-自动状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"EAF04G01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B43*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LEAF04G01_A AT%I224.4 :BOOL; (*排风机NJ-4AP(KT)7-1-自动状态*)"},"LEAF04G01_A             AT%I224.4      :BOOL; (*排风机NJ-4AP(KT)7-1-自动状态*)",null,"EAF04G01_A","排风机NJ-4AP(KT)7-1-自动状态",11796]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","排风机NJ-4AP(KT)7-2-运行状态",{"$nulls":16},"NJ-4AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)7-2","04G02","运行状态","排风机-运行状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"EAF04G02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B43*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LEAF04G02_R AT%I224.5 :BOOL; (*排风机NJ-4AP(KT)7-2-运行状态*)"},"LEAF04G02_R             AT%I224.5      :BOOL; (*排风机NJ-4AP(KT)7-2-运行状态*)",null,"EAF04G02_R","排风机NJ-4AP(KT)7-2-运行状态",11797]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","排风机NJ-4AP(KT)7-2-故障状态",{"$nulls":16},"NJ-4AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)7-2","04G02","故障状态","排风机-故障状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"EAF04G02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B43*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LEAF04G02_F AT%I224.6 :BOOL; (*排风机NJ-4AP(KT)7-2-故障状态*)"},"LEAF04G02_F             AT%I224.6      :BOOL; (*排风机NJ-4AP(KT)7-2-故障状态*)",null,"EAF04G02_F","排风机NJ-4AP(KT)7-2-故障状态",11798]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","排风机NJ-4AP(KT)7-2-自动状态",{"$nulls":16},"NJ-4AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)7-2","04G02","自动状态","排风机-自动状态",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"EAF04G02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B43*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LEAF04G02_A AT%I224.7 :BOOL; (*排风机NJ-4AP(KT)7-2-自动状态*)"},"LEAF04G02_A             AT%I224.7      :BOOL; (*排风机NJ-4AP(KT)7-2-自动状态*)",null,"EAF04G02_A","排风机NJ-4AP(KT)7-2-自动状态",11799]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B55&\"地址: \"&B52&\" *)\"","v":"(* IOM 1601D地址: 15 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH51&AA51&\"-\"&AK51","v":"空调机组NJ-4AP(KT)7-1-启停控制"},{"$nulls":16},{"$f":"IF(AI51=\"\",\"\",AI51)","v":"NJ-4AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-1","04G01","启停控制",{"$f":"AH51&\"-\"&AK51","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"AHU04G01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%Q\"&B52*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LAHU04G01_C AT%Q240.0 :BOOL; (*空调机组NJ-4AP(KT)7-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN51,SEARCH(\"AT%\",AN51),,REPT(\" \",25-SEARCH(\"AT%\",AN51))),SEARCH(\":\",REPLACE(AN51,SEARCH(\"AT%\",AN51),,REPT(\" \",25-SEARCH(\"AT%\",AN51)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN51,SEARCH(\"AT%\",AN51),,REPT(\" \",25-SEARCH(\"AT%\",AN51)))))),\" \")","v":"LAHU04G01_C             AT%Q240.0      :BOOL; (*空调机组NJ-4AP(KT)7-1-启停控制*)"},null,{"$f":"AM51","v":"AHU04G01_C"},{"$f":"J51","v":"空调机组NJ-4AP(KT)7-1-启停控制"},{"$f":"($B52*16*8+F51-1)","v":1920}]
[null,15,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-4AP(KT)7-2-启停控制",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-4AP(KT)7-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-2","04G02","启停控制",{"$f":"AH52&\"-\"&AK52","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"AHU04G02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%Q\"&B52*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LAHU04G02_C AT%Q240.1 :BOOL; (*空调机组NJ-4AP(KT)7-2-启停控制*)"},"LAHU04G02_C             AT%Q240.1      :BOOL; (*空调机组NJ-4AP(KT)7-2-启停控制*)",null,"AHU04G02_C",{"$f":"J52","v":"空调机组NJ-4AP(KT)7-2-启停控制"},{"$f":"AS51+1","v":1921}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-4AP(KT)7-3-启停控制",{"$nulls":16},"NJ-4AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-3","04G03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"AHU04G03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%Q\"&B52*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LAHU04G03_C AT%Q240.2 :BOOL; (*空调机组NJ-4AP(KT)7-3-启停控制*)"},"LAHU04G03_C             AT%Q240.2      :BOOL; (*空调机组NJ-4AP(KT)7-3-启停控制*)",null,"AHU04G03_C","空调机组NJ-4AP(KT)7-3-启停控制",{"$f":"AS52+1","v":1922}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","空调机组NJ-4AP(KT)7-4-启停控制",{"$nulls":16},"NJ-4AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-4","04G04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"AHU04G04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%Q\"&B52*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LAHU04G04_C AT%Q240.3 :BOOL; (*空调机组NJ-4AP(KT)7-4-启停控制*)"},"LAHU04G04_C             AT%Q240.3      :BOOL; (*空调机组NJ-4AP(KT)7-4-启停控制*)",null,"AHU04G04_C","空调机组NJ-4AP(KT)7-4-启停控制",1923]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B52),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-4AP(KT)7-5-启停控制",{"$nulls":16},"NJ-4AP(KT)7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-5","04G05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"AHU04G05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%Q\"&B52*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LAHU04G05_C AT%Q240.4 :BOOL; (*空调机组NJ-4AP(KT)7-5-启停控制*)"},"LAHU04G05_C             AT%Q240.4      :BOOL; (*空调机组NJ-4AP(KT)7-5-启停控制*)",null,"AHU04G05_C","空调机组NJ-4AP(KT)7-5-启停控制",1924]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-4AP(KT)7-6-启停控制",{"$nulls":16},"NJ-4AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-6","04G06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"AHU04G06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%Q\"&B52*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LAHU04G06_C AT%Q240.5 :BOOL; (*空调机组NJ-4AP(KT)7-6-启停控制*)"},"LAHU04G06_C             AT%Q240.5      :BOOL; (*空调机组NJ-4AP(KT)7-6-启停控制*)",null,"AHU04G06_C","空调机组NJ-4AP(KT)7-6-启停控制",1925]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","照明控制箱NJ-4AL7-1-启停控制",{"$nulls":16},"NJ-4AL7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL7-1","04G01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"LCB04G01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%Q\"&B52*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LLCB04G01_C AT%Q240.6 :BOOL; (*照明控制箱NJ-4AL7-1-启停控制*)"},"LLCB04G01_C             AT%Q240.6      :BOOL; (*照明控制箱NJ-4AL7-1-启停控制*)",null,"LCB04G01_C","照明控制箱NJ-4AL7-1-启停控制",1926]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B54=20,1,IF(B54=50,10,IF(B54=125,11,IF(B54=250,100,IF(B54=500,101,IF(B54=800,110,IF(B54=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-4AL7-2-启停控制",{"$nulls":16},"NJ-4AL7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL7-2","04G02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":"LCB04G02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%Q\"&B52*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":"LLCB04G02_C AT%Q240.7 :BOOL; (*照明控制箱NJ-4AL7-2-启停控制*)"},"LLCB04G02_C             AT%Q240.7      :BOOL; (*照明控制箱NJ-4AL7-2-启停控制*)",null,"LCB04G02_C","照明控制箱NJ-4AL7-2-启停控制",1927]
[{"$nulls":5},9,null,"9+","9-","照明控制箱NJ-4AL7-3-启停控制",{"$nulls":16},"NJ-4AL7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL7-3","04G03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH59,List!$B$3:$D$445,2,FALSE)&AJ59&\"_\"&VLOOKUP(AK59,List!$K$2:$M$447,2,FALSE)","v":"LCB04G03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM59&\" \"&\"AT%Q\"&B52*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J59&\"*)\",\" \")","v":"LLCB04G03_C AT%Q241.0 :BOOL; (*照明控制箱NJ-4AL7-3-启停控制*)"},"LLCB04G03_C             AT%Q241.0      :BOOL; (*照明控制箱NJ-4AL7-3-启停控制*)",null,"LCB04G03_C","照明控制箱NJ-4AL7-3-启停控制",1928]
[{"$nulls":5},10,null,"10+","10-","照明控制箱NJ-4AL7-4-启停控制",{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-4AL7-4"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL7-4","04G04","启停控制",{"$f":"AH60&\"-\"&AK60","v":"照明控制箱-启停控制"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"LCB04G04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%Q\"&B52*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LLCB04G04_C AT%Q241.1 :BOOL; (*照明控制箱NJ-4AL7-4-启停控制*)"},"LLCB04G04_C             AT%Q241.1      :BOOL; (*照明控制箱NJ-4AL7-4-启停控制*)",null,"LCB04G04_C",{"$f":"J60","v":"照明控制箱NJ-4AL7-4-启停控制"},1929]
[{"$nulls":5},11,null,"11+","11-","照明控制箱NJ-4AL7-5-启停控制",{"$nulls":16},"NJ-4AL7-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL7-5","04G05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"LCB04G05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%Q\"&B52*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LLCB04G05_C AT%Q241.2 :BOOL; (*照明控制箱NJ-4AL7-5-启停控制*)"},"LLCB04G05_C             AT%Q241.2      :BOOL; (*照明控制箱NJ-4AL7-5-启停控制*)",null,"LCB04G05_C","照明控制箱NJ-4AL7-5-启停控制",1930]
[{"$nulls":5},12,null,"12+","12-","排风机NJ-4AP(KT)7-1-启停控制",{"$nulls":16},"NJ-4AP(KT)7-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)7-1","04G01","启停控制","排风机-启停控制",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"EAF04G01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%Q\"&B52*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LEAF04G01_C AT%Q241.3 :BOOL; (*排风机NJ-4AP(KT)7-1-启停控制*)"},"LEAF04G01_C             AT%Q241.3      :BOOL; (*排风机NJ-4AP(KT)7-1-启停控制*)",null,"EAF04G01_C","排风机NJ-4AP(KT)7-1-启停控制",1931]
[{"$nulls":5},13,null,"13+","13-","排风机NJ-4AP(KT)7-2-启停控制",{"$nulls":16},"NJ-4AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)7-2","04G02","启停控制","排风机-启停控制",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"EAF04G02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%Q\"&B52*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LEAF04G02_C AT%Q241.4 :BOOL; (*排风机NJ-4AP(KT)7-2-启停控制*)"},"LEAF04G02_C             AT%Q241.4      :BOOL; (*排风机NJ-4AP(KT)7-2-启停控制*)",null,"EAF04G02_C","排风机NJ-4AP(KT)7-2-启停控制",1932]
[{"$nulls":5},14,null,"14+","14-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%Q\"&B52*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1933]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%Q\"&B52*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1934]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%Q\"&B52*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1935]
[null,{"$f":"B72","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B72&\"地址: \"&B69&\" *)\"","v":"(* IOM 0801U地址: 16 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH68&AA68&\"-\"&AK68","v":"空调机组NJ-4AP(KT)7-1-回风温度"},{"$nulls":16},{"$f":"IF(AI68=\"\",\"\",AI68)","v":"NJ-4AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-1","04G01","回风温度",{"$f":"AH68&\"-\"&AK68","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"AHU04G01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%I\"&B69*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LAHU04G01_RT AT%I256.0 :INT ; (*空调机组NJ-4AP(KT)7-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68))),SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))))),\" \")","v":"LAHU04G01_RT            AT%I256.0      :INT ; (*空调机组NJ-4AP(KT)7-1-回风温度*)"},null,{"$f":"AM68","v":"AHU04G01_RT"},{"$f":"J68","v":"空调机组NJ-4AP(KT)7-1-回风温度"},{"$f":"30000+($B69*8+F68-1)","v":30128}]
[null,16,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-4AP(KT)7-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-4AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-1","04G01","水阀反馈",{"$f":"AH69&\"-\"&AK69","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU04G01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%I\"&B69*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU04G01_WVB AT%I258.0 :INT ; (*空调机组NJ-4AP(KT)7-1-水阀反馈*)"},"LAHU04G01_WVB           AT%I258.0      :INT ; (*空调机组NJ-4AP(KT)7-1-水阀反馈*)",null,"AHU04G01_WVB",{"$f":"J69","v":"空调机组NJ-4AP(KT)7-1-水阀反馈"},{"$f":"AS68+1","v":30129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-4AP(KT)7-2-回风温度",{"$nulls":16},"NJ-4AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-2","04G02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"AHU04G02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%I\"&B69*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LAHU04G02_RT AT%I260.0 :INT ; (*空调机组NJ-4AP(KT)7-2-回风温度*)"},"LAHU04G02_RT            AT%I260.0      :INT ; (*空调机组NJ-4AP(KT)7-2-回风温度*)",null,"AHU04G02_RT","空调机组NJ-4AP(KT)7-2-回风温度",{"$f":"AS69+1","v":30130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-4AP(KT)7-2-水阀反馈",{"$nulls":16},"NJ-4AP(KT)7-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-2","04G02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"AHU04G02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%I\"&B69*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LAHU04G02_WVB AT%I262.0 :INT ; (*空调机组NJ-4AP(KT)7-2-水阀反馈*)"},"LAHU04G02_WVB           AT%I262.0      :INT ; (*空调机组NJ-4AP(KT)7-2-水阀反馈*)",null,"AHU04G02_WVB","空调机组NJ-4AP(KT)7-2-水阀反馈",30131]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":1},5,null,5,"0V","空调机组NJ-4AP(KT)7-3-回风温度",{"$nulls":16},"NJ-4AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-3","04G03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"AHU04G03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%I\"&B69*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LAHU04G03_RT AT%I264.0 :INT ; (*空调机组NJ-4AP(KT)7-3-回风温度*)"},"LAHU04G03_RT            AT%I264.0      :INT ; (*空调机组NJ-4AP(KT)7-3-回风温度*)",null,"AHU04G03_RT","空调机组NJ-4AP(KT)7-3-回风温度",30132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-4AP(KT)7-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI73=\"\",\"\",AI73)","v":"NJ-4AP(KT)7-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-3","04G03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"AHU04G03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%I\"&B69*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LAHU04G03_WVB AT%I266.0 :INT ; (*空调机组NJ-4AP(KT)7-3-水阀反馈*)"},"LAHU04G03_WVB           AT%I266.0      :INT ; (*空调机组NJ-4AP(KT)7-3-水阀反馈*)",null,"AHU04G03_WVB",{"$f":"J73","v":"空调机组NJ-4AP(KT)7-3-水阀反馈"},30133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-4AP(KT)7-4-回风温度",{"$nulls":16},"NJ-4AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-4","04G04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":"AHU04G04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%I\"&B69*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":"LAHU04G04_RT AT%I268.0 :INT ; (*空调机组NJ-4AP(KT)7-4-回风温度*)"},"LAHU04G04_RT            AT%I268.0      :INT ; (*空调机组NJ-4AP(KT)7-4-回风温度*)",null,"AHU04G04_RT","空调机组NJ-4AP(KT)7-4-回风温度",30134]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-4AP(KT)7-4-水阀反馈",{"$nulls":16},"NJ-4AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-4","04G04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":"AHU04G04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%I\"&B69*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":"LAHU04G04_WVB AT%I270.0 :INT ; (*空调机组NJ-4AP(KT)7-4-水阀反馈*)"},"LAHU04G04_WVB           AT%I270.0      :INT ; (*空调机组NJ-4AP(KT)7-4-水阀反馈*)",null,"AHU04G04_WVB","空调机组NJ-4AP(KT)7-4-水阀反馈",30135]
[null,{"$f":"B81","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B81&\"地址: \"&B78&\" *)\"","v":"(* IOM 0801U地址: 17 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH77&AA77&\"-\"&AK77","v":"空调机组NJ-4AP(KT)7-5-回风温度"},{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-4AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-5","04G05","回风温度",{"$f":"AH77&\"-\"&AK77","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"AHU04G05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%I\"&B78*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LAHU04G05_RT AT%I272.0 :INT ; (*空调机组NJ-4AP(KT)7-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77))),SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN77,SEARCH(\"AT%\",AN77),,REPT(\" \",25-SEARCH(\"AT%\",AN77)))))),\" \")","v":"LAHU04G05_RT            AT%I272.0      :INT ; (*空调机组NJ-4AP(KT)7-5-回风温度*)"},null,{"$f":"AM77","v":"AHU04G05_RT"},{"$f":"J77","v":"空调机组NJ-4AP(KT)7-5-回风温度"},{"$f":"30000+($B78*8+F77-1)","v":30136}]
[null,17,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-4AP(KT)7-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-4AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-5","04G05","水阀反馈",{"$f":"AH78&\"-\"&AK78","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU04G05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%I\"&B78*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU04G05_WVB AT%I274.0 :INT ; (*空调机组NJ-4AP(KT)7-5-水阀反馈*)"},"LAHU04G05_WVB           AT%I274.0      :INT ; (*空调机组NJ-4AP(KT)7-5-水阀反馈*)",null,"AHU04G05_WVB",{"$f":"J78","v":"空调机组NJ-4AP(KT)7-5-水阀反馈"},{"$f":"AS77+1","v":30137}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-4AP(KT)7-6-回风温度",{"$nulls":16},"NJ-4AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-6","04G06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"AHU04G06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%I\"&B78*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LAHU04G06_RT AT%I276.0 :INT ; (*空调机组NJ-4AP(KT)7-6-回风温度*)"},"LAHU04G06_RT            AT%I276.0      :INT ; (*空调机组NJ-4AP(KT)7-6-回风温度*)",null,"AHU04G06_RT","空调机组NJ-4AP(KT)7-6-回风温度",{"$f":"AS78+1","v":30138}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-4AP(KT)7-6-水阀反馈",{"$nulls":16},"NJ-4AP(KT)7-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-6","04G06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"AHU04G06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%I\"&B78*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LAHU04G06_WVB AT%I278.0 :INT ; (*空调机组NJ-4AP(KT)7-6-水阀反馈*)"},"LAHU04G06_WVB           AT%I278.0      :INT ; (*空调机组NJ-4AP(KT)7-6-水阀反馈*)",null,"AHU04G06_WVB","空调机组NJ-4AP(KT)7-6-水阀反馈",30139]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B78),REPT(0,5))),1,1))","v":1},5,null,5,"0V","室内环境状态T-07-温度状态",{"$nulls":16},"T-07",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","T-07","04G01","温度状态","室内环境状态-温度状态",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"IES04G01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%I\"&B78*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LIES04G01_T AT%I280.0 :INT ; (*室内环境状态T-07-温度状态*)"},"LIES04G01_T             AT%I280.0      :INT ; (*室内环境状态T-07-温度状态*)",null,"IES04G01_T","室内环境状态T-07-温度状态",30140]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","室内环境状态T-08-温度状态",{"$nulls":16},{"$f":"IF(AI82=\"\",\"\",AI82)","v":"T-08"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","T-08","04G02","温度状态","室内环境状态-温度状态",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":"IES04G02_T"},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%I\"&B78*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":"LIES04G02_T AT%I282.0 :INT ; (*室内环境状态T-08-温度状态*)"},"LIES04G02_T             AT%I282.0      :INT ; (*室内环境状态T-08-温度状态*)",null,"IES04G02_T",{"$f":"J82","v":"室内环境状态T-08-温度状态"},30141]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","室内环境状态T-09-温度状态",{"$nulls":16},"T-09",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","T-09","04G03","温度状态","室内环境状态-温度状态",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":"IES04G03_T"},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%I\"&B78*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":"LIES04G03_T AT%I284.0 :INT ; (*室内环境状态T-09-温度状态*)"},"LIES04G03_T             AT%I284.0      :INT ; (*室内环境状态T-09-温度状态*)",null,"IES04G03_T","室内环境状态T-09-温度状态",30142]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B80=20,1,IF(B80=50,10,IF(B80=125,11,IF(B80=250,100,IF(B80=500,101,IF(B80=800,110,IF(B80=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","室内环境状态LUX-02-照度状态",{"$nulls":16},"LUX-02",{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","LUX-02","04G01","照度状态","室内环境状态-照度状态",{"$f":"VLOOKUP(AH84,List!$B$3:$D$445,2,FALSE)&AJ84&\"_\"&VLOOKUP(AK84,List!$K$2:$M$447,2,FALSE)","v":"IES04G01_I"},{"$f":"_xlfn.IFNA(\"L\"&AM84&\" \"&\"AT%I\"&B78*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J84&\"*)\",\" \")","v":"LIES04G01_I AT%I286.0 :INT ; (*室内环境状态LUX-02-照度状态*)"},"LIES04G01_I             AT%I286.0      :INT ; (*室内环境状态LUX-02-照度状态*)",null,"IES04G01_I","室内环境状态LUX-02-照度状态",30143]
[null,{"$f":"B90","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B90&\"地址: \"&B87&\" *)\"","v":"(* IOM 0401U地址: 18 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH86&AA86&\"-\"&AK86","v":"室内环境状态LUX-03-照度状态"},{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"LUX-03"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","LUX-03","04G02","照度状态",{"$f":"AH86&\"-\"&AK86","v":"室内环境状态-照度状态"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"IES04G02_I"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%I\"&B87*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LIES04G02_I AT%I288.0 :INT ; (*室内环境状态LUX-03-照度状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86))),SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))))),\" \")","v":"LIES04G02_I             AT%I288.0      :INT ; (*室内环境状态LUX-03-照度状态*)"},null,{"$f":"AM86","v":"IES04G02_I"},{"$f":"J86","v":"室内环境状态LUX-03-照度状态"},{"$f":"30000+($B87*8+F86-1)","v":30144}]
[null,18,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":1},2,null,2,"0V","室内环境状态LUX-04-照度状态",{"$nulls":16},{"$f":"IF(AI87=\"\",\"\",AI87)","v":"LUX-04"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","LUX-04","04G03","照度状态",{"$f":"AH87&\"-\"&AK87","v":"室内环境状态-照度状态"},{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"IES04G03_I"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%I\"&B87*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LIES04G03_I AT%I290.0 :INT ; (*室内环境状态LUX-04-照度状态*)"},"LIES04G03_I             AT%I290.0      :INT ; (*室内环境状态LUX-04-照度状态*)",null,"IES04G03_I",{"$f":"J87","v":"室内环境状态LUX-04-照度状态"},{"$f":"AS86+1","v":30145}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":0},3,null,3,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%I\"&B87*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS87+1","v":30146}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%I\"&B87*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30147]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":1}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B99","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B99&\"地址: \"&B96&\" *)\"","v":"(* IOM 0401A地址: 19 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH95&AA95&\"-\"&AK95","v":"空调机组NJ-4AP(KT)7-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-4AP(KT)7-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-1","04G01","水阀控制",{"$f":"AH95&\"-\"&AK95","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"AHU04G01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%Q\"&B96*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LAHU04G01_WVC AT%Q304.0 :INT ; (*空调机组NJ-4AP(KT)7-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95))),SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))))),\" \")","v":"LAHU04G01_WVC           AT%Q304.0      :INT ; (*空调机组NJ-4AP(KT)7-1-水阀控制*)"},null,{"$f":"AM95","v":"AHU04G01_WVC"},{"$f":"J95","v":"空调机组NJ-4AP(KT)7-1-水阀控制"},{"$f":"40000+($B96*8+F95-1)","v":40152}]
[null,19,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH96&AA96&\"-\"&AK96","v":"空调机组NJ-4AP(KT)7-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI96=\"\",\"\",AI96)","v":"NJ-4AP(KT)7-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-2","04G02","水阀控制",{"$f":"AH96&\"-\"&AK96","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"AHU04G02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%Q\"&B96*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LAHU04G02_WVC AT%Q306.0 :INT ; (*空调机组NJ-4AP(KT)7-2-水阀控制*)"},"LAHU04G02_WVC           AT%Q306.0      :INT ; (*空调机组NJ-4AP(KT)7-2-水阀控制*)",null,"AHU04G02_WVC",{"$f":"J96","v":"空调机组NJ-4AP(KT)7-2-水阀控制"},{"$f":"AS95+1","v":40153}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH97&AA97&\"-\"&AK97","v":"空调机组NJ-4AP(KT)7-3-水阀控制"},{"$nulls":16},"NJ-4AP(KT)7-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-3","04G03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":"AHU04G03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%Q\"&B96*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":"LAHU04G03_WVC AT%Q308.0 :INT ; (*空调机组NJ-4AP(KT)7-3-水阀控制*)"},"LAHU04G03_WVC           AT%Q308.0      :INT ; (*空调机组NJ-4AP(KT)7-3-水阀控制*)",null,"AHU04G03_WVC","空调机组NJ-4AP(KT)7-3-水阀控制",{"$f":"AS96+1","v":40154}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH98&AA98&\"-\"&AK98","v":"空调机组NJ-4AP(KT)7-4-水阀控制"},{"$nulls":16},"NJ-4AP(KT)7-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-4","04G04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":"AHU04G04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%Q\"&B96*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":"LAHU04G04_WVC AT%Q310.0 :INT ; (*空调机组NJ-4AP(KT)7-4-水阀控制*)"},"LAHU04G04_WVC           AT%Q310.0      :INT ; (*空调机组NJ-4AP(KT)7-4-水阀控制*)",null,"AHU04G04_WVC","空调机组NJ-4AP(KT)7-4-水阀控制",40155]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B108","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B108&\"地址: \"&B105&\" *)\"","v":"(* IOM 0401A地址: 20 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH104&AA104&\"-\"&AK104","v":"空调机组NJ-4AP(KT)7-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI104=\"\",\"\",AI104)","v":"NJ-4AP(KT)7-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-5","04G05","水阀控制",{"$f":"AH104&\"-\"&AK104","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"AHU04G05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%Q\"&B105*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LAHU04G05_WVC AT%Q320.0 :INT ; (*空调机组NJ-4AP(KT)7-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104))),SEARCH(\":\",REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104)))))),\" \")","v":"LAHU04G05_WVC           AT%Q320.0      :INT ; (*空调机组NJ-4AP(KT)7-5-水阀控制*)"},null,{"$f":"AM104","v":"AHU04G05_WVC"},{"$f":"J104","v":"空调机组NJ-4AP(KT)7-5-水阀控制"},{"$f":"40000+($B105*8+F104-1)","v":40160}]
[null,20,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH105&AA105&\"-\"&AK105","v":"空调机组NJ-4AP(KT)7-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI105=\"\",\"\",AI105)","v":"NJ-4AP(KT)7-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)7-6","04G06","水阀控制",{"$f":"AH105&\"-\"&AK105","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"AHU04G06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%Q\"&B105*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LAHU04G06_WVC AT%Q322.0 :INT ; (*空调机组NJ-4AP(KT)7-6-水阀控制*)"},"LAHU04G06_WVC           AT%Q322.0      :INT ; (*空调机组NJ-4AP(KT)7-6-水阀控制*)",null,"AHU04G06_WVC",{"$f":"J105","v":"空调机组NJ-4AP(KT)7-6-水阀控制"},{"$f":"AS104+1","v":40161}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH106&AA106&\"-\"&AK106","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},{"$f":"AH106&\"-\"&AK106","v":"-"},{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%Q\"&B105*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS105+1","v":40162}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH107&AA107&\"-\"&AK107","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},{"$f":"AH107&\"-\"&AK107","v":"-"},{"$f":"VLOOKUP(AH107,List!$B$3:$D$445,2,FALSE)&AJ107&\"_\"&VLOOKUP(AK107,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM107&\" \"&\"AT%Q\"&B105*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J107&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40163]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L502","index":42,"n_rows":50,"n_cols":45,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[4,1,5,1],[11,1,22,1],[28,1,31,1],[37,1,40,1],[46,1,49,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L01",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R D7",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 21 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":1},1,null,1,"C",{"$f":"AH8&AA8&\"-\"&AK8","v":"F新风机组NJ-5AP(KT)71-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-5AP(KT)71-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-1","05B01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"F新风机组-运行状态"},{"$f":"VLOOKUP(AH8,[1]List!$D$3:$F$527,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LFAU05B01_R AT%I336.0 :BOOL; (*F新风机组NJ-5AP(KT)71-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LFAU05B01_R             AT%I336.0      :BOOL; (*F新风机组NJ-5AP(KT)71-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L01\\L01FAU05B01_R"},{"$f":"J8","v":"F新风机组NJ-5AP(KT)71-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":12688}]
[null,21,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":0},2,null,2,"C","F新风机组NJ-5AP(KT)71-1-故障状态",{"$nulls":16},"NJ-5AP(KT)71-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-1","05B01","故障状态","F新风机组-故障状态",{"$f":"VLOOKUP(AH9,[1]List!$D$3:$F$527,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LFAU05B01_F AT%I336.1 :BOOL; (*F新风机组NJ-5AP(KT)71-1-故障状态*)"},"LFAU05B01_F             AT%I336.1      :BOOL; (*F新风机组NJ-5AP(KT)71-1-故障状态*)",null,"L01\\L01FAU05B01_F","F新风机组NJ-5AP(KT)71-1-故障状态",{"$f":"AS8+1","v":12689}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},3,null,3,"C","F新风机组NJ-5AP(KT)71-1-自动状态",{"$nulls":16},"NJ-5AP(KT)71-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-1","05B01","自动状态","F新风机组-自动状态",{"$f":"VLOOKUP(AH10,[1]List!$D$3:$F$527,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LFAU05B01_A AT%I336.2 :BOOL; (*F新风机组NJ-5AP(KT)71-1-自动状态*)"},"LFAU05B01_A             AT%I336.2      :BOOL; (*F新风机组NJ-5AP(KT)71-1-自动状态*)",null,"L01\\L01FAU05B01_A","F新风机组NJ-5AP(KT)71-1-自动状态",12690]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},4,null,4,"C","F新风机组NJ-5AP(KT)71-1-风机压差",{"$nulls":16},"NJ-5AP(KT)71-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-1","05B01","风机压差","F新风机组-风机压差",{"$f":"VLOOKUP(AH11,[1]List!$D$3:$F$527,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LFAU05B01_FPS AT%I336.3 :BOOL; (*F新风机组NJ-5AP(KT)71-1-风机压差*)"},"LFAU05B01_FPS           AT%I336.3      :BOOL; (*F新风机组NJ-5AP(KT)71-1-风机压差*)",null,"L01\\L01FAU05B01_FPS","F新风机组NJ-5AP(KT)71-1-风机压差",12691]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},5,null,5,"C","F新风机组NJ-5AP(KT)71-1-初效滤网压差",{"$nulls":16},"NJ-5AP(KT)71-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-1","05B01","初效滤网压差","F新风机组-初效滤网压差",{"$f":"VLOOKUP(AH12,[1]List!$D$3:$F$527,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B01_IPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LFAU05B01_IPS AT%I336.4 :BOOL; (*F新风机组NJ-5AP(KT)71-1-初效滤网压差*)"},"LFAU05B01_IPS           AT%I336.4      :BOOL; (*F新风机组NJ-5AP(KT)71-1-初效滤网压差*)",null,"L01\\L01FAU05B01_IPS","F新风机组NJ-5AP(KT)71-1-初效滤网压差",12692]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","F新风机组NJ-5AP(KT)71-1-低温断路开关",{"$nulls":16},"NJ-5AP(KT)71-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-1","05B01","低温断路开关","F新风机组-低温断路开关",{"$f":"VLOOKUP(AH13,[1]List!$D$3:$F$527,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B01_AFS"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LFAU05B01_AFS AT%I336.5 :BOOL; (*F新风机组NJ-5AP(KT)71-1-低温断路开关*)"},"LFAU05B01_AFS           AT%I336.5      :BOOL; (*F新风机组NJ-5AP(KT)71-1-低温断路开关*)",null,"L01\\L01FAU05B01_AFS","F新风机组NJ-5AP(KT)71-1-低温断路开关",12693]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","F新风机组NJ-5AP(KT)71-1-新风阀开状态",{"$nulls":16},"NJ-5AP(KT)71-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-1","05B01","新风阀开状态","F新风机组-新风阀开状态",{"$f":"VLOOKUP(AH14,[1]List!$D$3:$F$527,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B01_FDOB"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LFAU05B01_FDOB AT%I336.6 :BOOL; (*F新风机组NJ-5AP(KT)71-1-新风阀开状态*)"},"LFAU05B01_FDOB          AT%I336.6      :BOOL; (*F新风机组NJ-5AP(KT)71-1-新风阀开状态*)",null,"L01\\L01FAU05B01_FDOB","F新风机组NJ-5AP(KT)71-1-新风阀开状态",12694]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","F新风机组NJ-5AP(KT)71-1-新风阀关状态",{"$nulls":16},"NJ-5AP(KT)71-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-1","05B01","新风阀关状态","F新风机组-新风阀关状态",{"$f":"VLOOKUP(AH15,[1]List!$D$3:$F$527,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B01_FDSB"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LFAU05B01_FDSB AT%I336.7 :BOOL; (*F新风机组NJ-5AP(KT)71-1-新风阀关状态*)"},"LFAU05B01_FDSB          AT%I336.7      :BOOL; (*F新风机组NJ-5AP(KT)71-1-新风阀关状态*)",null,"L01\\L01FAU05B01_FDSB","F新风机组NJ-5AP(KT)71-1-新风阀关状态",12695]
[{"$nulls":5},9,null,9,"C","F新风机组NJ-5AP(KT)71-2-运行状态",{"$nulls":16},"NJ-5AP(KT)71-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-2","05B02","运行状态","F新风机组-运行状态",{"$f":"VLOOKUP(AH16,[1]List!$D$3:$F$527,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LFAU05B02_R AT%I337.0 :BOOL; (*F新风机组NJ-5AP(KT)71-2-运行状态*)"},"LFAU05B02_R             AT%I337.0      :BOOL; (*F新风机组NJ-5AP(KT)71-2-运行状态*)",null,"L01\\L01FAU05B02_R","F新风机组NJ-5AP(KT)71-2-运行状态",12696]
[{"$nulls":5},10,null,10,"C","F新风机组NJ-5AP(KT)71-2-故障状态",{"$nulls":16},"NJ-5AP(KT)71-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-2","05B02","故障状态","F新风机组-故障状态",{"$f":"VLOOKUP(AH17,[1]List!$D$3:$F$527,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LFAU05B02_F AT%I337.1 :BOOL; (*F新风机组NJ-5AP(KT)71-2-故障状态*)"},"LFAU05B02_F             AT%I337.1      :BOOL; (*F新风机组NJ-5AP(KT)71-2-故障状态*)",null,"L01\\L01FAU05B02_F","F新风机组NJ-5AP(KT)71-2-故障状态",12697]
[{"$nulls":5},11,null,11,"C","F新风机组NJ-5AP(KT)71-2-自动状态",{"$nulls":16},"NJ-5AP(KT)71-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-2","05B02","自动状态","F新风机组-自动状态",{"$f":"VLOOKUP(AH18,[1]List!$D$3:$F$527,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LFAU05B02_A AT%I337.2 :BOOL; (*F新风机组NJ-5AP(KT)71-2-自动状态*)"},"LFAU05B02_A             AT%I337.2      :BOOL; (*F新风机组NJ-5AP(KT)71-2-自动状态*)",null,"L01\\L01FAU05B02_A","F新风机组NJ-5AP(KT)71-2-自动状态",12698]
[{"$nulls":5},12,null,12,"C","F新风机组NJ-5AP(KT)71-2-风机压差",{"$nulls":16},"NJ-5AP(KT)71-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-2","05B02","风机压差","F新风机组-风机压差",{"$f":"VLOOKUP(AH19,[1]List!$D$3:$F$527,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LFAU05B02_FPS AT%I337.3 :BOOL; (*F新风机组NJ-5AP(KT)71-2-风机压差*)"},"LFAU05B02_FPS           AT%I337.3      :BOOL; (*F新风机组NJ-5AP(KT)71-2-风机压差*)",null,"L01\\L01FAU05B02_FPS","F新风机组NJ-5AP(KT)71-2-风机压差",12699]
[{"$nulls":5},13,null,13,"C","F新风机组NJ-5AP(KT)71-2-初效滤网压差",{"$nulls":16},"NJ-5AP(KT)71-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-2","05B02","初效滤网压差","F新风机组-初效滤网压差",{"$f":"VLOOKUP(AH20,[1]List!$D$3:$F$527,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B02_IPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LFAU05B02_IPS AT%I337.4 :BOOL; (*F新风机组NJ-5AP(KT)71-2-初效滤网压差*)"},"LFAU05B02_IPS           AT%I337.4      :BOOL; (*F新风机组NJ-5AP(KT)71-2-初效滤网压差*)",null,"L01\\L01FAU05B02_IPS","F新风机组NJ-5AP(KT)71-2-初效滤网压差",12700]
[{"$nulls":5},14,null,14,"C","F新风机组NJ-5AP(KT)71-2-低温断路开关",{"$nulls":16},"NJ-5AP(KT)71-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-2","05B02","低温断路开关","F新风机组-低温断路开关",{"$f":"VLOOKUP(AH21,[1]List!$D$3:$F$527,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B02_AFS"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LFAU05B02_AFS AT%I337.5 :BOOL; (*F新风机组NJ-5AP(KT)71-2-低温断路开关*)"},"LFAU05B02_AFS           AT%I337.5      :BOOL; (*F新风机组NJ-5AP(KT)71-2-低温断路开关*)",null,"L01\\L01FAU05B02_AFS","F新风机组NJ-5AP(KT)71-2-低温断路开关",12701]
[{"$nulls":5},15,null,15,"C","F新风机组NJ-5AP(KT)71-2-新风阀开状态",{"$nulls":16},"NJ-5AP(KT)71-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-2","05B02","新风阀开状态","F新风机组-新风阀开状态",{"$f":"VLOOKUP(AH22,[1]List!$D$3:$F$527,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B02_FDOB"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LFAU05B02_FDOB AT%I337.6 :BOOL; (*F新风机组NJ-5AP(KT)71-2-新风阀开状态*)"},"LFAU05B02_FDOB          AT%I337.6      :BOOL; (*F新风机组NJ-5AP(KT)71-2-新风阀开状态*)",null,"L01\\L01FAU05B02_FDOB","F新风机组NJ-5AP(KT)71-2-新风阀开状态",12702]
[".",{"$nulls":4},16,null,16,"C","F新风机组NJ-5AP(KT)71-2-新风阀关状态",{"$nulls":16},"NJ-5AP(KT)71-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-2","05B02","新风阀关状态","F新风机组-新风阀关状态",{"$f":"VLOOKUP(AH23,[1]List!$D$3:$F$527,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B02_FDSB"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LFAU05B02_FDSB AT%I337.7 :BOOL; (*F新风机组NJ-5AP(KT)71-2-新风阀关状态*)"},"LFAU05B02_FDSB          AT%I337.7      :BOOL; (*F新风机组NJ-5AP(KT)71-2-新风阀关状态*)",null,"L01\\L01FAU05B02_FDSB","F新风机组NJ-5AP(KT)71-2-新风阀关状态",12703]
[null,{"$f":"B29","v":"IOM 0801D"},{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 0801D地址: 22 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH25&AA25&\"-\"&AK25","v":"F新风机组NJ-5AP(KT)71-1-启停控制"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-5AP(KT)71-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-1","05B01","启停控制",{"$f":"AH25&\"-\"&AK25","v":"F新风机组-启停控制"},{"$f":"VLOOKUP(AH25,[1]List!$D$3:$F$527,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%Q\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LFAU05B01_C AT%Q352.0 :BOOL; (*F新风机组NJ-5AP(KT)71-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LFAU05B01_C             AT%Q352.0      :BOOL; (*F新风机组NJ-5AP(KT)71-1-启停控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L01\\L01FAU05B01_C"},{"$f":"J25","v":"F新风机组NJ-5AP(KT)71-1-启停控制"},{"$f":"($B26*16*8+F25-1)","v":2816}]
[null,22,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","F新风机组NJ-5AP(KT)71-1-新风阀开控制",{"$nulls":16},"NJ-5AP(KT)71-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-1","05B01","新风阀开控制","F新风机组-新风阀开控制",{"$f":"VLOOKUP(AH26,[1]List!$D$3:$F$527,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B01_FDOC"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%Q\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LFAU05B01_FDOC AT%Q352.1 :BOOL; (*F新风机组NJ-5AP(KT)71-1-新风阀开控制*)"},"LFAU05B01_FDOC          AT%Q352.1      :BOOL; (*F新风机组NJ-5AP(KT)71-1-新风阀开控制*)",null,"L01\\L01FAU05B01_FDOC","F新风机组NJ-5AP(KT)71-1-新风阀开控制",{"$f":"AS25+1","v":2817}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","F新风机组NJ-5AP(KT)71-1-新风阀关控制",{"$nulls":16},"NJ-5AP(KT)71-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-1","05B01","新风阀关控制","F新风机组-新风阀关控制",{"$f":"VLOOKUP(AH27,[1]List!$D$3:$F$527,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B01_FDSC"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%Q\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LFAU05B01_FDSC AT%Q352.2 :BOOL; (*F新风机组NJ-5AP(KT)71-1-新风阀关控制*)"},"LFAU05B01_FDSC          AT%Q352.2      :BOOL; (*F新风机组NJ-5AP(KT)71-1-新风阀关控制*)",null,"L01\\L01FAU05B01_FDSC","F新风机组NJ-5AP(KT)71-1-新风阀关控制",2818]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","F新风机组NJ-5AP(KT)71-2-启停控制",{"$nulls":16},"NJ-5AP(KT)71-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-2","05B02","启停控制","F新风机组-启停控制",{"$f":"VLOOKUP(AH28,[1]List!$D$3:$F$527,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%Q\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LFAU05B02_C AT%Q352.3 :BOOL; (*F新风机组NJ-5AP(KT)71-2-启停控制*)"},"LFAU05B02_C             AT%Q352.3      :BOOL; (*F新风机组NJ-5AP(KT)71-2-启停控制*)",null,"L01\\L01FAU05B02_C","F新风机组NJ-5AP(KT)71-2-启停控制",2819]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":1},5,null,"5+","5-","F新风机组NJ-5AP(KT)71-2-新风阀开控制",{"$nulls":16},"NJ-5AP(KT)71-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-2","05B02","新风阀开控制","F新风机组-新风阀开控制",{"$f":"VLOOKUP(AH29,[1]List!$D$3:$F$527,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B02_FDOC"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%Q\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LFAU05B02_FDOC AT%Q352.4 :BOOL; (*F新风机组NJ-5AP(KT)71-2-新风阀开控制*)"},"LFAU05B02_FDOC          AT%Q352.4      :BOOL; (*F新风机组NJ-5AP(KT)71-2-新风阀开控制*)",null,"L01\\L01FAU05B02_FDOC","F新风机组NJ-5AP(KT)71-2-新风阀开控制",2820]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","F新风机组NJ-5AP(KT)71-2-新风阀关控制",{"$nulls":16},"NJ-5AP(KT)71-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-2","05B02","新风阀关控制","F新风机组-新风阀关控制",{"$f":"VLOOKUP(AH30,[1]List!$D$3:$F$527,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B02_FDSC"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%Q\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LFAU05B02_FDSC AT%Q352.5 :BOOL; (*F新风机组NJ-5AP(KT)71-2-新风阀关控制*)"},"LFAU05B02_FDSC          AT%Q352.5      :BOOL; (*F新风机组NJ-5AP(KT)71-2-新风阀关控制*)",null,"L01\\L01FAU05B02_FDSC","F新风机组NJ-5AP(KT)71-2-新风阀关控制",2821]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH31,[1]List!$D$3:$F$527,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%Q\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2822]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH32,[1]List!$D$3:$F$527,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%Q\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN32,SEARCH(\"AT%\",AN32),,REPT(\" \",30-SEARCH(\"AT%\",AN32))),SEARCH(\":\",REPLACE(AN32,SEARCH(\"AT%\",AN32),,REPT(\" \",30-SEARCH(\"AT%\",AN32)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN32,SEARCH(\"AT%\",AN32),,REPT(\" \",25-SEARCH(\"AT%\",AN32)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",2823]
[null,{"$f":"B38","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B38&\"地址: \"&B35&\" *)\"","v":"(* IOM 0801U地址: 23 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH34&AA34&\"-\"&AK34","v":"F新风机组NJ-5AP(KT)71-1-送风温度"},{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-5AP(KT)71-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-1","05B01","送风温度",{"$f":"AH34&\"-\"&AK34","v":"F新风机组-送风温度"},{"$f":"VLOOKUP(AH34,[1]List!$D$3:$F$527,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B01_ST"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B35*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LFAU05B01_ST AT%I368.0 :INT; (*F新风机组NJ-5AP(KT)71-1-送风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34))),SEARCH(\":\",REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34)))))),\" \")","v":"LFAU05B01_ST            AT%I368.0      :INT; (*F新风机组NJ-5AP(KT)71-1-送风温度*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM34","v":"L01\\L01FAU05B01_ST"},{"$f":"J34","v":"F新风机组NJ-5AP(KT)71-1-送风温度"},{"$f":"30000+($B35*8+F34-1)","v":30184}]
[null,23,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),4,1))","v":1},2,null,2,"0V","F新风机组NJ-5AP(KT)71-1-水阀反馈",{"$nulls":16},"NJ-5AP(KT)71-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-1","05B01","水阀反馈","F新风机组-水阀反馈",{"$f":"VLOOKUP(AH35,[1]List!$D$3:$F$527,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B35*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LFAU05B01_WVB AT%I370.0 :INT; (*F新风机组NJ-5AP(KT)71-1-水阀反馈*)"},"LFAU05B01_WVB           AT%I370.0      :INT; (*F新风机组NJ-5AP(KT)71-1-水阀反馈*)",null,"L01\\L01FAU05B01_WVB","F新风机组NJ-5AP(KT)71-1-水阀反馈",{"$f":"AS34+1","v":30185}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),3,1))","v":1},3,null,3,"0V","F新风机组NJ-5AP(KT)71-1-变频器频率反馈",{"$nulls":16},"NJ-5AP(KT)71-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-1","05B01","变频器频率反馈","F新风机组-变频器频率反馈",{"$f":"VLOOKUP(AH36,[1]List!$D$3:$F$527,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B01_VFB"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B35*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LFAU05B01_VFB AT%I372.0 :INT; (*F新风机组NJ-5AP(KT)71-1-变频器频率反馈*)"},"LFAU05B01_VFB           AT%I372.0      :INT; (*F新风机组NJ-5AP(KT)71-1-变频器频率反馈*)",null,"L01\\L01FAU05B01_VFB","F新风机组NJ-5AP(KT)71-1-变频器频率反馈",30186]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),2,1))","v":0},4,null,4,"0V","F新风机组NJ-5AP(KT)71-2-送风温度",{"$nulls":16},"NJ-5AP(KT)71-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-2","05B02","送风温度","F新风机组-送风温度",{"$f":"VLOOKUP(AH37,[1]List!$D$3:$F$527,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B02_ST"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B35*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LFAU05B02_ST AT%I374.0 :INT; (*F新风机组NJ-5AP(KT)71-2-送风温度*)"},"LFAU05B02_ST            AT%I374.0      :INT; (*F新风机组NJ-5AP(KT)71-2-送风温度*)",null,"L01\\L01FAU05B02_ST","F新风机组NJ-5AP(KT)71-2-送风温度",30187]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),1,1))","v":1},5,null,5,"0V","F新风机组NJ-5AP(KT)71-2-水阀反馈",{"$nulls":16},"NJ-5AP(KT)71-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-2","05B02","水阀反馈","F新风机组-水阀反馈",{"$f":"VLOOKUP(AH38,[1]List!$D$3:$F$527,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B35*16+8&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LFAU05B02_WVB AT%I376.0 :INT; (*F新风机组NJ-5AP(KT)71-2-水阀反馈*)"},"LFAU05B02_WVB           AT%I376.0      :INT; (*F新风机组NJ-5AP(KT)71-2-水阀反馈*)",null,"L01\\L01FAU05B02_WVB","F新风机组NJ-5AP(KT)71-2-水阀反馈",30188]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","F新风机组NJ-5AP(KT)71-2-变频器频率反馈",{"$nulls":16},"NJ-5AP(KT)71-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-2","05B02","变频器频率反馈","F新风机组-变频器频率反馈",{"$f":"VLOOKUP(AH39,[1]List!$D$3:$F$527,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B02_VFB"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B35*16+10&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LFAU05B02_VFB AT%I378.0 :INT; (*F新风机组NJ-5AP(KT)71-2-变频器频率反馈*)"},"LFAU05B02_VFB           AT%I378.0      :INT; (*F新风机组NJ-5AP(KT)71-2-变频器频率反馈*)",null,"L01\\L01FAU05B02_VFB","F新风机组NJ-5AP(KT)71-2-变频器频率反馈",30189]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH40,[1]List!$D$3:$F$527,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B35*16+12&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30190]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH41,[1]List!$D$3:$F$527,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%I\"&B35*16+14&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN41,SEARCH(\"AT%\",AN41),,REPT(\" \",30-SEARCH(\"AT%\",AN41))),SEARCH(\":\",REPLACE(AN41,SEARCH(\"AT%\",AN41),,REPT(\" \",30-SEARCH(\"AT%\",AN41)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN41,SEARCH(\"AT%\",AN41),,REPT(\" \",25-SEARCH(\"AT%\",AN41)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",30191]
[null,{"$f":"B47","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 0401A地址: 24 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH43&AA43&\"-\"&AK43","v":"F新风机组NJ-5AP(KT)71-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-5AP(KT)71-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-1","05B01","水阀控制",{"$f":"AH43&\"-\"&AK43","v":"F新风机组-水阀控制"},{"$f":"VLOOKUP(AH43,[1]List!$D$3:$F$527,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%Q\"&B44*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LFAU05B01_WVC AT%Q384.0 :INT; (*F新风机组NJ-5AP(KT)71-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LFAU05B01_WVC           AT%Q384.0      :INT; (*F新风机组NJ-5AP(KT)71-1-水阀控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM43","v":"L01\\L01FAU05B01_WVC"},{"$f":"J43","v":"F新风机组NJ-5AP(KT)71-1-水阀控制"},{"$f":"40000+($B44*8+F43-1)","v":40192}]
[null,24,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":0},2,null,3,4,"F新风机组NJ-5AP(KT)71-1-变频器频率控制",{"$nulls":16},"NJ-5AP(KT)71-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-1","05B01","变频器频率控制","F新风机组-变频器频率控制",{"$f":"VLOOKUP(AH44,[1]List!$D$3:$F$527,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B01_VFC"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%Q\"&B44*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LFAU05B01_VFC AT%Q386.0 :INT; (*F新风机组NJ-5AP(KT)71-1-变频器频率控制*)"},"LFAU05B01_VFC           AT%Q386.0      :INT; (*F新风机组NJ-5AP(KT)71-1-变频器频率控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM44","v":"L01\\L01FAU05B01_VFC"},"F新风机组NJ-5AP(KT)71-1-变频器频率控制",{"$f":"AS43+1","v":40193}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,5,6,"F新风机组NJ-5AP(KT)71-2-水阀控制",{"$nulls":16},"NJ-5AP(KT)71-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-2","05B02","水阀控制","F新风机组-水阀控制",{"$f":"VLOOKUP(AH45,[1]List!$D$3:$F$527,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%Q\"&B44*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LFAU05B02_WVC AT%Q388.0 :INT; (*F新风机组NJ-5AP(KT)71-2-水阀控制*)"},"LFAU05B02_WVC           AT%Q388.0      :INT; (*F新风机组NJ-5AP(KT)71-2-水阀控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM45","v":"L01\\L01FAU05B02_WVC"},"F新风机组NJ-5AP(KT)71-2-水阀控制",40194]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":1},4,null,7,8,"F新风机组NJ-5AP(KT)71-2-变频器频率控制",{"$nulls":16},"NJ-5AP(KT)71-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)71-2","05B02","变频器频率控制","F新风机组-变频器频率控制",{"$f":"VLOOKUP(AH46,[1]List!$D$3:$F$527,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05B02_VFC"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%Q\"&B44*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LFAU05B02_VFC AT%Q390.0 :INT; (*F新风机组NJ-5AP(KT)71-2-变频器频率控制*)"},"LFAU05B02_VFC           AT%Q390.0      :INT; (*F新风机组NJ-5AP(KT)71-2-变频器频率控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM46","v":"L01\\L01FAU05B02_VFC"},"F新风机组NJ-5AP(KT)71-2-变频器频率控制",40195]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-",null,null," "]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L308","index":43,"n_rows":138,"n_cols":45,"rows_kept":138,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[6,1,6,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[57,5,57,6],[57,9,57,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[66,5,66,6],[66,9,66,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[75,5,75,6],[75,9,75,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[83,5,83,6],[83,9,83,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[92,5,92,6],[92,9,92,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[101,5,101,6],[101,9,101,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[109,5,109,6],[109,9,109,25],[110,5,110,6],[110,9,110,25],[112,5,112,6],[112,9,112,25],[113,5,113,6],[113,9,113,25],[114,5,114,6],[114,9,114,25],[115,5,115,6],[115,9,115,25],[116,5,116,6],[116,9,116,25],[117,5,117,6],[117,9,117,25],[118,5,118,6],[118,9,118,25],[119,5,119,6],[119,9,119,25],[121,5,121,6],[121,9,121,25],[122,5,122,6],[122,9,122,25],[123,5,123,6],[123,9,123,25],[124,5,124,6],[124,9,124,25],[125,5,125,6],[125,9,125,25],[126,5,126,6],[126,9,126,25],[127,5,127,6],[127,9,127,25],[128,5,128,6],[128,9,128,25],[130,5,130,6],[130,9,130,25],[131,5,131,6],[131,9,131,25],[132,5,132,6],[132,9,132,25],[133,5,133,6],[133,9,133,25],[134,5,134,6],[134,9,134,25],[135,5,135,6],[135,9,135,25],[136,5,136,6],[136,9,136,25],[137,5,137,6],[137,9,137,25],[4,1,5,1],[12,1,23,1],[29,1,40,1],[46,1,57,1],[63,1,66,1],[72,1,83,1],[89,1,92,1],[98,1,101,1],[107,1,110,1],[116,1,119,1],[125,1,128,1],[134,1,137,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[16,2,23,4],[33,2,40,4],[50,2,57,4],[76,2,83,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L26",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"EXC-1000"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B13&\"地址: \"&B10&\" *)\"","v":"(* IOM 1601R地址: 0 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH9&AA9&\"-\"&AK9","v":"空调机组NJ-3AP(KT)8-1-运行状态"},{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-3AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-1","03H01","运行状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU03H01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B10*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU03H01_R AT%I0.0 :BOOL; (*空调机组NJ-3AP(KT)8-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9))),SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN9,SEARCH(\"AT%\",AN9),,REPT(\" \",25-SEARCH(\"AT%\",AN9)))))),\" \")","v":"LAHU03H01_R             AT%I0.0        :BOOL; (*空调机组NJ-3AP(KT)8-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM9","v":"L26\\L26AHU03H01_R"},{"$f":"J9","v":"空调机组NJ-3AP(KT)8-1-运行状态"},{"$f":"10000+($B10*16*8+F9-1)","v":10000}]
[null,0,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-3AP(KT)8-1-故障状态",{"$nulls":16},{"$f":"IF(AI10=\"\",\"\",AI10)","v":"NJ-3AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-1","03H01","故障状态",{"$f":"AH10&\"-\"&AK10","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU03H01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B10*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU03H01_F AT%I0.1 :BOOL; (*空调机组NJ-3AP(KT)8-1-故障状态*)"},"LAHU03H01_F             AT%I0.1        :BOOL; (*空调机组NJ-3AP(KT)8-1-故障状态*)",null,"L26\\L26AHU03H01_F",{"$f":"J10","v":"空调机组NJ-3AP(KT)8-1-故障状态"},{"$f":"AS9+1","v":10001}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)8-1-自动状态",{"$nulls":16},"NJ-3AP(KT)8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-1","03H01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU03H01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B10*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU03H01_A AT%I0.2 :BOOL; (*空调机组NJ-3AP(KT)8-1-自动状态*)"},"LAHU03H01_A             AT%I0.2        :BOOL; (*空调机组NJ-3AP(KT)8-1-自动状态*)",null,"L26\\L26AHU03H01_A","空调机组NJ-3AP(KT)8-1-自动状态",{"$f":"AS10+1","v":10002}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)8-1-风机压差",{"$nulls":16},"NJ-3AP(KT)8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-1","03H01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU03H01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B10*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU03H01_FPS AT%I0.3 :BOOL; (*空调机组NJ-3AP(KT)8-1-风机压差*)"},"LAHU03H01_FPS           AT%I0.3        :BOOL; (*空调机组NJ-3AP(KT)8-1-风机压差*)",null,"L26\\L26AHU03H01_FPS","空调机组NJ-3AP(KT)8-1-风机压差",10003]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B10),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)8-2-运行状态",{"$nulls":16},"NJ-3AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-2","03H02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU03H02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B10*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU03H02_R AT%I0.4 :BOOL; (*空调机组NJ-3AP(KT)8-2-运行状态*)"},"LAHU03H02_R             AT%I0.4        :BOOL; (*空调机组NJ-3AP(KT)8-2-运行状态*)",null,"L26\\L26AHU03H02_R","空调机组NJ-3AP(KT)8-2-运行状态",10004]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)8-2-故障状态",{"$nulls":16},"NJ-3AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-2","03H02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU03H02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B10*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU03H02_F AT%I0.5 :BOOL; (*空调机组NJ-3AP(KT)8-2-故障状态*)"},"LAHU03H02_F             AT%I0.5        :BOOL; (*空调机组NJ-3AP(KT)8-2-故障状态*)",null,"L26\\L26AHU03H02_F","空调机组NJ-3AP(KT)8-2-故障状态",10005]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)8-2-自动状态",{"$nulls":16},"NJ-3AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-2","03H02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU03H02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B10*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU03H02_A AT%I0.6 :BOOL; (*空调机组NJ-3AP(KT)8-2-自动状态*)"},"LAHU03H02_A             AT%I0.6        :BOOL; (*空调机组NJ-3AP(KT)8-2-自动状态*)",null,"L26\\L26AHU03H02_A","空调机组NJ-3AP(KT)8-2-自动状态",10006]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B12=20,1,IF(B12=50,10,IF(B12=125,11,IF(B12=250,100,IF(B12=500,101,IF(B12=800,110,IF(B12=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)8-2-风机压差",{"$nulls":16},"NJ-3AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-2","03H02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU03H02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B10*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU03H02_FPS AT%I0.7 :BOOL; (*空调机组NJ-3AP(KT)8-2-风机压差*)"},"LAHU03H02_FPS           AT%I0.7        :BOOL; (*空调机组NJ-3AP(KT)8-2-风机压差*)",null,"L26\\L26AHU03H02_FPS","空调机组NJ-3AP(KT)8-2-风机压差",10007]
[{"$nulls":5},9,null,17,18,"空调机组NJ-3AP(KT)8-3-运行状态",{"$nulls":16},"NJ-3AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-3","03H03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU03H03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B10*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU03H03_R AT%I1.0 :BOOL; (*空调机组NJ-3AP(KT)8-3-运行状态*)"},"LAHU03H03_R             AT%I1.0        :BOOL; (*空调机组NJ-3AP(KT)8-3-运行状态*)",null,"L26\\L26AHU03H03_R","空调机组NJ-3AP(KT)8-3-运行状态",10008]
[{"$nulls":5},10,null,19,20,"空调机组NJ-3AP(KT)8-3-故障状态",{"$nulls":16},{"$f":"IF(AI18=\"\",\"\",AI18)","v":"NJ-3AP(KT)8-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-3","03H03","故障状态",{"$f":"AH18&\"-\"&AK18","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU03H03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B10*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU03H03_F AT%I1.1 :BOOL; (*空调机组NJ-3AP(KT)8-3-故障状态*)"},"LAHU03H03_F             AT%I1.1        :BOOL; (*空调机组NJ-3AP(KT)8-3-故障状态*)",null,"L26\\L26AHU03H03_F","空调机组NJ-3AP(KT)8-3-故障状态",10009]
[{"$nulls":5},11,null,21,22,"空调机组NJ-3AP(KT)8-3-自动状态",{"$nulls":16},"NJ-3AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-3","03H03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU03H03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B10*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU03H03_A AT%I1.2 :BOOL; (*空调机组NJ-3AP(KT)8-3-自动状态*)"},"LAHU03H03_A             AT%I1.2        :BOOL; (*空调机组NJ-3AP(KT)8-3-自动状态*)",null,"L26\\L26AHU03H03_A","空调机组NJ-3AP(KT)8-3-自动状态",10010]
[{"$nulls":5},12,null,23,24,"空调机组NJ-3AP(KT)8-3-风机压差",{"$nulls":16},"NJ-3AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-3","03H03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU03H03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B10*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU03H03_FPS AT%I1.3 :BOOL; (*空调机组NJ-3AP(KT)8-3-风机压差*)"},"LAHU03H03_FPS           AT%I1.3        :BOOL; (*空调机组NJ-3AP(KT)8-3-风机压差*)",null,"L26\\L26AHU03H03_FPS","空调机组NJ-3AP(KT)8-3-风机压差",10011]
[{"$nulls":5},13,null,25,26,"空调机组NJ-3AP(KT)8-4-运行状态",{"$nulls":16},"NJ-3AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-4","03H04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU03H04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B10*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU03H04_R AT%I1.4 :BOOL; (*空调机组NJ-3AP(KT)8-4-运行状态*)"},"LAHU03H04_R             AT%I1.4        :BOOL; (*空调机组NJ-3AP(KT)8-4-运行状态*)",null,"L26\\L26AHU03H04_R","空调机组NJ-3AP(KT)8-4-运行状态",10012]
[{"$nulls":5},14,null,27,28,"空调机组NJ-3AP(KT)8-4-故障状态",{"$nulls":16},"NJ-3AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-4","03H04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU03H04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B10*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU03H04_F AT%I1.5 :BOOL; (*空调机组NJ-3AP(KT)8-4-故障状态*)"},"LAHU03H04_F             AT%I1.5        :BOOL; (*空调机组NJ-3AP(KT)8-4-故障状态*)",null,"L26\\L26AHU03H04_F","空调机组NJ-3AP(KT)8-4-故障状态",10013]
[{"$nulls":5},15,null,29,30,"空调机组NJ-3AP(KT)8-4-自动状态",{"$nulls":16},"NJ-3AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-4","03H04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU03H04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B10*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU03H04_A AT%I1.6 :BOOL; (*空调机组NJ-3AP(KT)8-4-自动状态*)"},"LAHU03H04_A             AT%I1.6        :BOOL; (*空调机组NJ-3AP(KT)8-4-自动状态*)",null,"L26\\L26AHU03H04_A","空调机组NJ-3AP(KT)8-4-自动状态",10014]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-3AP(KT)8-4-风机压差",{"$nulls":16},"NJ-3AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-4","03H04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH24,List!$B$3:$D$445,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,List!$K$2:$M$447,2,FALSE)","v":"AHU03H04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%I\"&B10*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":"LAHU03H04_FPS AT%I1.7 :BOOL; (*空调机组NJ-3AP(KT)8-4-风机压差*)"},"LAHU03H04_FPS           AT%I1.7        :BOOL; (*空调机组NJ-3AP(KT)8-4-风机压差*)",null,"L26\\L26AHU03H04_FPS","空调机组NJ-3AP(KT)8-4-风机压差",10015]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 1601R地址: 1 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH26&AA26&\"-\"&AK26","v":"空调机组NJ-3AP(KT)8-5-运行状态"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-3AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-5","03H05","运行状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU03H05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU03H05_R AT%I16.0 :BOOL; (*空调机组NJ-3AP(KT)8-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LAHU03H05_R             AT%I16.0       :BOOL; (*空调机组NJ-3AP(KT)8-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L26\\L26AHU03H05_R"},{"$f":"J26","v":"空调机组NJ-3AP(KT)8-5-运行状态"},{"$f":"10000+($B27*16*8+F26-1)","v":10128}]
[null,1,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-3AP(KT)8-5-故障状态",{"$nulls":16},{"$f":"IF(AI27=\"\",\"\",AI27)","v":"NJ-3AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-5","03H05","故障状态",{"$f":"AH27&\"-\"&AK27","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU03H05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU03H05_F AT%I16.1 :BOOL; (*空调机组NJ-3AP(KT)8-5-故障状态*)"},"LAHU03H05_F             AT%I16.1       :BOOL; (*空调机组NJ-3AP(KT)8-5-故障状态*)",null,"L26\\L26AHU03H05_F",{"$f":"J27","v":"空调机组NJ-3AP(KT)8-5-故障状态"},{"$f":"AS26+1","v":10129}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)8-5-自动状态",{"$nulls":16},"NJ-3AP(KT)8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-5","03H05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU03H05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU03H05_A AT%I16.2 :BOOL; (*空调机组NJ-3AP(KT)8-5-自动状态*)"},"LAHU03H05_A             AT%I16.2       :BOOL; (*空调机组NJ-3AP(KT)8-5-自动状态*)",null,"L26\\L26AHU03H05_A","空调机组NJ-3AP(KT)8-5-自动状态",{"$f":"AS27+1","v":10130}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)8-5-风机压差",{"$nulls":16},"NJ-3AP(KT)8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-5","03H05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU03H05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU03H05_FPS AT%I16.3 :BOOL; (*空调机组NJ-3AP(KT)8-5-风机压差*)"},"LAHU03H05_FPS           AT%I16.3       :BOOL; (*空调机组NJ-3AP(KT)8-5-风机压差*)",null,"L26\\L26AHU03H05_FPS","空调机组NJ-3AP(KT)8-5-风机压差",10131]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)8-6-运行状态",{"$nulls":16},"NJ-3AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-6","03H06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU03H06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B27*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU03H06_R AT%I16.4 :BOOL; (*空调机组NJ-3AP(KT)8-6-运行状态*)"},"LAHU03H06_R             AT%I16.4       :BOOL; (*空调机组NJ-3AP(KT)8-6-运行状态*)",null,"L26\\L26AHU03H06_R","空调机组NJ-3AP(KT)8-6-运行状态",10132]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)8-6-故障状态",{"$nulls":16},"NJ-3AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-6","03H06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU03H06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B27*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU03H06_F AT%I16.5 :BOOL; (*空调机组NJ-3AP(KT)8-6-故障状态*)"},"LAHU03H06_F             AT%I16.5       :BOOL; (*空调机组NJ-3AP(KT)8-6-故障状态*)",null,"L26\\L26AHU03H06_F","空调机组NJ-3AP(KT)8-6-故障状态",10133]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)8-6-自动状态",{"$nulls":16},"NJ-3AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-6","03H06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU03H06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B27*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU03H06_A AT%I16.6 :BOOL; (*空调机组NJ-3AP(KT)8-6-自动状态*)"},"LAHU03H06_A             AT%I16.6       :BOOL; (*空调机组NJ-3AP(KT)8-6-自动状态*)",null,"L26\\L26AHU03H06_A","空调机组NJ-3AP(KT)8-6-自动状态",10134]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)8-6-风机压差",{"$nulls":16},"NJ-3AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-6","03H06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU03H06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B27*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU03H06_FPS AT%I16.7 :BOOL; (*空调机组NJ-3AP(KT)8-6-风机压差*)"},"LAHU03H06_FPS           AT%I16.7       :BOOL; (*空调机组NJ-3AP(KT)8-6-风机压差*)",null,"L26\\L26AHU03H06_FPS","空调机组NJ-3AP(KT)8-6-风机压差",10135]
[{"$nulls":5},9,null,17,18,"空调机组NJ-3AP(KT)8-7-运行状态",{"$nulls":16},"NJ-3AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-7","03H07","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU03H07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B27*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU03H07_R AT%I17.0 :BOOL; (*空调机组NJ-3AP(KT)8-7-运行状态*)"},"LAHU03H07_R             AT%I17.0       :BOOL; (*空调机组NJ-3AP(KT)8-7-运行状态*)",null,"L26\\L26AHU03H07_R","空调机组NJ-3AP(KT)8-7-运行状态",10136]
[{"$nulls":5},10,null,19,20,"空调机组NJ-3AP(KT)8-7-故障状态",{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-3AP(KT)8-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-7","03H07","故障状态",{"$f":"AH35&\"-\"&AK35","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU03H07_F"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B27*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU03H07_F AT%I17.1 :BOOL; (*空调机组NJ-3AP(KT)8-7-故障状态*)"},"LAHU03H07_F             AT%I17.1       :BOOL; (*空调机组NJ-3AP(KT)8-7-故障状态*)",null,"L26\\L26AHU03H07_F",{"$f":"J35","v":"空调机组NJ-3AP(KT)8-7-故障状态"},10137]
[{"$nulls":5},11,null,21,22,"空调机组NJ-3AP(KT)8-7-自动状态",{"$nulls":16},"NJ-3AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-7","03H07","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU03H07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B27*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU03H07_A AT%I17.2 :BOOL; (*空调机组NJ-3AP(KT)8-7-自动状态*)"},"LAHU03H07_A             AT%I17.2       :BOOL; (*空调机组NJ-3AP(KT)8-7-自动状态*)",null,"L26\\L26AHU03H07_A","空调机组NJ-3AP(KT)8-7-自动状态",10138]
[{"$nulls":5},12,null,23,24,"空调机组NJ-3AP(KT)8-7-风机压差",{"$nulls":16},"NJ-3AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-7","03H07","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"AHU03H07_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B27*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LAHU03H07_FPS AT%I17.3 :BOOL; (*空调机组NJ-3AP(KT)8-7-风机压差*)"},"LAHU03H07_FPS           AT%I17.3       :BOOL; (*空调机组NJ-3AP(KT)8-7-风机压差*)",null,"L26\\L26AHU03H07_FPS","空调机组NJ-3AP(KT)8-7-风机压差",10139]
[{"$nulls":5},13,null,25,26,"空调机组NJ-3AP(KT)8-8-运行状态",{"$nulls":16},"NJ-3AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-8","03H08","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"AHU03H08_R"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B27*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LAHU03H08_R AT%I17.4 :BOOL; (*空调机组NJ-3AP(KT)8-8-运行状态*)"},"LAHU03H08_R             AT%I17.4       :BOOL; (*空调机组NJ-3AP(KT)8-8-运行状态*)",null,"L26\\L26AHU03H08_R","空调机组NJ-3AP(KT)8-8-运行状态",10140]
[{"$nulls":5},14,null,27,28,"空调机组NJ-3AP(KT)8-8-故障状态",{"$nulls":16},"NJ-3AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-8","03H08","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":"AHU03H08_F"},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B27*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":"LAHU03H08_F AT%I17.5 :BOOL; (*空调机组NJ-3AP(KT)8-8-故障状态*)"},"LAHU03H08_F             AT%I17.5       :BOOL; (*空调机组NJ-3AP(KT)8-8-故障状态*)",null,"L26\\L26AHU03H08_F","空调机组NJ-3AP(KT)8-8-故障状态",10141]
[{"$nulls":5},15,null,29,30,"空调机组NJ-3AP(KT)8-8-自动状态",{"$nulls":16},"NJ-3AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-8","03H08","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":"AHU03H08_A"},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B27*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":"LAHU03H08_A AT%I17.6 :BOOL; (*空调机组NJ-3AP(KT)8-8-自动状态*)"},"LAHU03H08_A             AT%I17.6       :BOOL; (*空调机组NJ-3AP(KT)8-8-自动状态*)",null,"L26\\L26AHU03H08_A","空调机组NJ-3AP(KT)8-8-自动状态",10142]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-3AP(KT)8-8-风机压差",{"$nulls":16},"NJ-3AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL41,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-8","03H08","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH41,List!$B$3:$D$445,2,FALSE)&AJ41&\"_\"&VLOOKUP(AK41,List!$K$2:$M$447,2,FALSE)","v":"AHU03H08_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM41&\" \"&\"AT%I\"&B27*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J41&\"*)\",\" \")","v":"LAHU03H08_FPS AT%I17.7 :BOOL; (*空调机组NJ-3AP(KT)8-8-风机压差*)"},"LAHU03H08_FPS           AT%I17.7       :BOOL; (*空调机组NJ-3AP(KT)8-8-风机压差*)",null,"L26\\L26AHU03H08_FPS","空调机组NJ-3AP(KT)8-8-风机压差",10143]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 1601R地址: 2 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH43&AA43&\"-\"&AK43","v":"空调机组NJ-3AP(KT)8-9-运行状态"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-3AP(KT)8-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-9","03H09","运行状态",{"$f":"AH43&\"-\"&AK43","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"AHU03H09_R"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B44*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LAHU03H09_R AT%I32.0 :BOOL; (*空调机组NJ-3AP(KT)8-9-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LAHU03H09_R             AT%I32.0       :BOOL; (*空调机组NJ-3AP(KT)8-9-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM43","v":"L26\\L26AHU03H09_R"},{"$f":"J43","v":"空调机组NJ-3AP(KT)8-9-运行状态"},{"$f":"10000+($B44*16*8+F43-1)","v":10256}]
[null,2,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":1},2,null,3,4,"空调机组NJ-3AP(KT)8-9-故障状态",{"$nulls":16},{"$f":"IF(AI44=\"\",\"\",AI44)","v":"NJ-3AP(KT)8-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-9","03H09","故障状态",{"$f":"AH44&\"-\"&AK44","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"AHU03H09_F"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B44*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LAHU03H09_F AT%I32.1 :BOOL; (*空调机组NJ-3AP(KT)8-9-故障状态*)"},"LAHU03H09_F             AT%I32.1       :BOOL; (*空调机组NJ-3AP(KT)8-9-故障状态*)",null,"L26\\L26AHU03H09_F",{"$f":"J44","v":"空调机组NJ-3AP(KT)8-9-故障状态"},{"$f":"AS43+1","v":10257}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-3AP(KT)8-9-自动状态",{"$nulls":16},"NJ-3AP(KT)8-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-9","03H09","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"AHU03H09_A"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B44*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LAHU03H09_A AT%I32.2 :BOOL; (*空调机组NJ-3AP(KT)8-9-自动状态*)"},"LAHU03H09_A             AT%I32.2       :BOOL; (*空调机组NJ-3AP(KT)8-9-自动状态*)",null,"L26\\L26AHU03H09_A","空调机组NJ-3AP(KT)8-9-自动状态",{"$f":"AS44+1","v":10258}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":0},4,null,7,8,"空调机组NJ-3AP(KT)8-9-风机压差",{"$nulls":16},"NJ-3AP(KT)8-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-9","03H09","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"AHU03H09_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B44*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LAHU03H09_FPS AT%I32.3 :BOOL; (*空调机组NJ-3AP(KT)8-9-风机压差*)"},"LAHU03H09_FPS           AT%I32.3       :BOOL; (*空调机组NJ-3AP(KT)8-9-风机压差*)",null,"L26\\L26AHU03H09_FPS","空调机组NJ-3AP(KT)8-9-风机压差",10259]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-3AP(KT)8-10-运行状态",{"$nulls":16},"NJ-3AP(KT)8-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-10","03H10","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"AHU03H10_R"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B44*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LAHU03H10_R AT%I32.4 :BOOL; (*空调机组NJ-3AP(KT)8-10-运行状态*)"},"LAHU03H10_R             AT%I32.4       :BOOL; (*空调机组NJ-3AP(KT)8-10-运行状态*)",null,"L26\\L26AHU03H10_R","空调机组NJ-3AP(KT)8-10-运行状态",10260]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-3AP(KT)8-10-故障状态",{"$nulls":16},"NJ-3AP(KT)8-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-10","03H10","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"AHU03H10_F"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B44*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LAHU03H10_F AT%I32.5 :BOOL; (*空调机组NJ-3AP(KT)8-10-故障状态*)"},"LAHU03H10_F             AT%I32.5       :BOOL; (*空调机组NJ-3AP(KT)8-10-故障状态*)",null,"L26\\L26AHU03H10_F","空调机组NJ-3AP(KT)8-10-故障状态",10261]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-3AP(KT)8-10-自动状态",{"$nulls":16},"NJ-3AP(KT)8-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-10","03H10","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"AHU03H10_A"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B44*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LAHU03H10_A AT%I32.6 :BOOL; (*空调机组NJ-3AP(KT)8-10-自动状态*)"},"LAHU03H10_A             AT%I32.6       :BOOL; (*空调机组NJ-3AP(KT)8-10-自动状态*)",null,"L26\\L26AHU03H10_A","空调机组NJ-3AP(KT)8-10-自动状态",10262]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-3AP(KT)8-10-风机压差",{"$nulls":16},"NJ-3AP(KT)8-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-10","03H10","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"AHU03H10_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B44*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LAHU03H10_FPS AT%I32.7 :BOOL; (*空调机组NJ-3AP(KT)8-10-风机压差*)"},"LAHU03H10_FPS           AT%I32.7       :BOOL; (*空调机组NJ-3AP(KT)8-10-风机压差*)",null,"L26\\L26AHU03H10_FPS","空调机组NJ-3AP(KT)8-10-风机压差",10263]
[{"$nulls":5},9,null,17,18,"照明控制箱NJ-3AL8-1-运行状态",{"$nulls":16},"NJ-3AL8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL8-1","03H01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"LCB03H01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B44*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LLCB03H01_R AT%I33.0 :BOOL; (*照明控制箱NJ-3AL8-1-运行状态*)"},"LLCB03H01_R             AT%I33.0       :BOOL; (*照明控制箱NJ-3AL8-1-运行状态*)",null,"L26\\L26LCB03H01_R","照明控制箱NJ-3AL8-1-运行状态",10264]
[{"$nulls":5},10,null,19,20,"照明控制箱NJ-3AL8-1-自动状态",{"$nulls":16},{"$f":"IF(AI52=\"\",\"\",AI52)","v":"NJ-3AL8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL8-1","03H01","自动状态",{"$f":"AH52&\"-\"&AK52","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"LCB03H01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%I\"&B44*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LLCB03H01_A AT%I33.1 :BOOL; (*照明控制箱NJ-3AL8-1-自动状态*)"},"LLCB03H01_A             AT%I33.1       :BOOL; (*照明控制箱NJ-3AL8-1-自动状态*)",null,"L26\\L26LCB03H01_A",{"$f":"J52","v":"照明控制箱NJ-3AL8-1-自动状态"},10265]
[{"$nulls":5},11,null,21,22,"照明控制箱NJ-3AL8-2-运行状态",{"$nulls":16},"NJ-3AL8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL8-2","03H02","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"LCB03H02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%I\"&B44*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LLCB03H02_R AT%I33.2 :BOOL; (*照明控制箱NJ-3AL8-2-运行状态*)"},"LLCB03H02_R             AT%I33.2       :BOOL; (*照明控制箱NJ-3AL8-2-运行状态*)",null,"L26\\L26LCB03H02_R","照明控制箱NJ-3AL8-2-运行状态",10266]
[{"$nulls":5},12,null,23,24,"照明控制箱NJ-3AL8-2-自动状态",{"$nulls":16},"NJ-3AL8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL8-2","03H02","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"LCB03H02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%I\"&B44*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LLCB03H02_A AT%I33.3 :BOOL; (*照明控制箱NJ-3AL8-2-自动状态*)"},"LLCB03H02_A             AT%I33.3       :BOOL; (*照明控制箱NJ-3AL8-2-自动状态*)",null,"L26\\L26LCB03H02_A","照明控制箱NJ-3AL8-2-自动状态",10267]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-3AL8-3-运行状态",{"$nulls":16},"NJ-3AL8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL8-3","03H03","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"LCB03H03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%I\"&B44*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LLCB03H03_R AT%I33.4 :BOOL; (*照明控制箱NJ-3AL8-3-运行状态*)"},"LLCB03H03_R             AT%I33.4       :BOOL; (*照明控制箱NJ-3AL8-3-运行状态*)",null,"L26\\L26LCB03H03_R","照明控制箱NJ-3AL8-3-运行状态",10268]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-3AL8-3-自动状态",{"$nulls":16},"NJ-3AL8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL8-3","03H03","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"LCB03H03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%I\"&B44*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LLCB03H03_A AT%I33.5 :BOOL; (*照明控制箱NJ-3AL8-3-自动状态*)"},"LLCB03H03_A             AT%I33.5       :BOOL; (*照明控制箱NJ-3AL8-3-自动状态*)",null,"L26\\L26LCB03H03_A","照明控制箱NJ-3AL8-3-自动状态",10269]
[{"$nulls":5},15,null,29,30,"照明控制箱NJ-3AL8-4-运行状态",{"$nulls":16},"NJ-3AL8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL8-4","03H04","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":"LCB03H04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%I\"&B44*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":"LLCB03H04_R AT%I33.6 :BOOL; (*照明控制箱NJ-3AL8-4-运行状态*)"},"LLCB03H04_R             AT%I33.6       :BOOL; (*照明控制箱NJ-3AL8-4-运行状态*)",null,"L26\\L26LCB03H04_R","照明控制箱NJ-3AL8-4-运行状态",10270]
[".",{"$nulls":4},16,null,31,32,"照明控制箱NJ-3AL8-4-自动状态",{"$nulls":16},"NJ-3AL8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL58,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL8-4","03H04","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH58,List!$B$3:$D$445,2,FALSE)&AJ58&\"_\"&VLOOKUP(AK58,List!$K$2:$M$447,2,FALSE)","v":"LCB03H04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM58&\" \"&\"AT%I\"&B44*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J58&\"*)\",\" \")","v":"LLCB03H04_A AT%I33.7 :BOOL; (*照明控制箱NJ-3AL8-4-自动状态*)"},"LLCB03H04_A             AT%I33.7       :BOOL; (*照明控制箱NJ-3AL8-4-自动状态*)",null,"L26\\L26LCB03H04_A","照明控制箱NJ-3AL8-4-自动状态",10271]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B64&\"地址: \"&B61&\" *)\"","v":"(* IOM 0801R 地址: 3 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),5,1))","v":1},1,null,1,"C",{"$f":"AH60&AA60&\"-\"&AK60","v":"照明控制箱NJ-3AL8-5-运行状态"},{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-3AL8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL8-5","03H05","运行状态",{"$f":"AH60&\"-\"&AK60","v":"照明控制箱-运行状态"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"LCB03H05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%I\"&B61*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LLCB03H05_R AT%I48.0 :BOOL; (*照明控制箱NJ-3AL8-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60))),SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN60,SEARCH(\"AT%\",AN60),,REPT(\" \",25-SEARCH(\"AT%\",AN60)))))),\" \")","v":"LLCB03H05_R             AT%I48.0       :BOOL; (*照明控制箱NJ-3AL8-5-运行状态*)"},null,{"$f":"AM60","v":"LCB03H05_R"},{"$f":"J60","v":"照明控制箱NJ-3AL8-5-运行状态"},{"$f":"10000+($B61*16*8+F60-1)","v":10384}]
[null,3,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),4,1))","v":1},2,null,2,"C",{"$f":"AH61&AA61&\"-\"&AK61","v":"照明控制箱NJ-3AL8-5-自动状态"},{"$nulls":16},{"$f":"IF(AI61=\"\",\"\",AI61)","v":"NJ-3AL8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"照明控制箱","NJ-3AL8-5","03H05","自动状态",{"$f":"AH61&\"-\"&AK61","v":"照明控制箱-自动状态"},{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"LCB03H05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%I\"&B61*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LLCB03H05_A AT%I48.1 :BOOL; (*照明控制箱NJ-3AL8-5-自动状态*)"},"LLCB03H05_A             AT%I48.1       :BOOL; (*照明控制箱NJ-3AL8-5-自动状态*)",null,{"$f":"AM61","v":"LCB03H05_A"},{"$f":"J61","v":"照明控制箱NJ-3AL8-5-自动状态"},{"$f":"AS60+1","v":10385}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),3,1))","v":0},3,null,3,"C",{"$f":"AH62&AA62&\"-\"&AK62","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B61*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS61+1","v":10386}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),2,1))","v":0},4,null,4,"C",{"$f":"AH63&AA63&\"-\"&AK63","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B61*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10387]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B61),REPT(0,5))),1,1))","v":0},5,null,5,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B61*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10388]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B61*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10389]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B61*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10390]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B63=20,1,IF(B63=50,10,IF(B63=125,11,IF(B63=250,100,IF(B63=500,101,IF(B63=800,110,IF(B63=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL67,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH67,List!$B$3:$D$445,2,FALSE)&AJ67&\"_\"&VLOOKUP(AK67,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM67&\" \"&\"AT%I\"&B61*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J67&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",10391]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B73&\"地址: \"&B70&\" *)\"","v":"(* IOM 1601D地址: 4 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH69&AA69&\"-\"&AK69","v":"空调机组NJ-3AP(KT)8-1-启停控制"},{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-3AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-1","03H01","启停控制",{"$f":"AH69&\"-\"&AK69","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU03H01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%Q\"&B70*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU03H01_C AT%Q64.0 :BOOL; (*空调机组NJ-3AP(KT)8-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69))),SEARCH(\":\",REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN69,SEARCH(\"AT%\",AN69),,REPT(\" \",25-SEARCH(\"AT%\",AN69)))))),\" \")","v":"LAHU03H01_C             AT%Q64.0       :BOOL; (*空调机组NJ-3AP(KT)8-1-启停控制*)"},null,{"$f":"AM69","v":"AHU03H01_C"},{"$f":"J69","v":"空调机组NJ-3AP(KT)8-1-启停控制"},{"$f":"($B70*16*8+F69-1)","v":512}]
[null,4,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","空调机组NJ-3AP(KT)8-2-启停控制",{"$nulls":16},{"$f":"IF(AI70=\"\",\"\",AI70)","v":"NJ-3AP(KT)8-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-2","03H02","启停控制",{"$f":"AH70&\"-\"&AK70","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"AHU03H02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%Q\"&B70*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LAHU03H02_C AT%Q64.1 :BOOL; (*空调机组NJ-3AP(KT)8-2-启停控制*)"},"LAHU03H02_C             AT%Q64.1       :BOOL; (*空调机组NJ-3AP(KT)8-2-启停控制*)",null,"AHU03H02_C",{"$f":"J70","v":"空调机组NJ-3AP(KT)8-2-启停控制"},{"$f":"AS69+1","v":513}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-3AP(KT)8-3-启停控制",{"$nulls":16},"NJ-3AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-3","03H03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"AHU03H03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%Q\"&B70*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LAHU03H03_C AT%Q64.2 :BOOL; (*空调机组NJ-3AP(KT)8-3-启停控制*)"},"LAHU03H03_C             AT%Q64.2       :BOOL; (*空调机组NJ-3AP(KT)8-3-启停控制*)",null,"AHU03H03_C","空调机组NJ-3AP(KT)8-3-启停控制",{"$f":"AS70+1","v":514}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","空调机组NJ-3AP(KT)8-4-启停控制",{"$nulls":16},"NJ-3AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-4","03H04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"AHU03H04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%Q\"&B70*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LAHU03H04_C AT%Q64.3 :BOOL; (*空调机组NJ-3AP(KT)8-4-启停控制*)"},"LAHU03H04_C             AT%Q64.3       :BOOL; (*空调机组NJ-3AP(KT)8-4-启停控制*)",null,"AHU03H04_C","空调机组NJ-3AP(KT)8-4-启停控制",515]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B70),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-3AP(KT)8-5-启停控制",{"$nulls":16},"NJ-3AP(KT)8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-5","03H05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"AHU03H05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%Q\"&B70*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LAHU03H05_C AT%Q64.4 :BOOL; (*空调机组NJ-3AP(KT)8-5-启停控制*)"},"LAHU03H05_C             AT%Q64.4       :BOOL; (*空调机组NJ-3AP(KT)8-5-启停控制*)",null,"AHU03H05_C","空调机组NJ-3AP(KT)8-5-启停控制",516]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-3AP(KT)8-6-启停控制",{"$nulls":16},"NJ-3AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-6","03H06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":"AHU03H06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%Q\"&B70*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":"LAHU03H06_C AT%Q64.5 :BOOL; (*空调机组NJ-3AP(KT)8-6-启停控制*)"},"LAHU03H06_C             AT%Q64.5       :BOOL; (*空调机组NJ-3AP(KT)8-6-启停控制*)",null,"AHU03H06_C","空调机组NJ-3AP(KT)8-6-启停控制",517]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","空调机组NJ-3AP(KT)8-7-启停控制",{"$nulls":16},"NJ-3AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-7","03H07","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":"AHU03H07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%Q\"&B70*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":"LAHU03H07_C AT%Q64.6 :BOOL; (*空调机组NJ-3AP(KT)8-7-启停控制*)"},"LAHU03H07_C             AT%Q64.6       :BOOL; (*空调机组NJ-3AP(KT)8-7-启停控制*)",null,"AHU03H07_C","空调机组NJ-3AP(KT)8-7-启停控制",518]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B72=20,1,IF(B72=50,10,IF(B72=125,11,IF(B72=250,100,IF(B72=500,101,IF(B72=800,110,IF(B72=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","空调机组NJ-3AP(KT)8-8-启停控制",{"$nulls":16},"NJ-3AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-8","03H08","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH76,List!$B$3:$D$445,2,FALSE)&AJ76&\"_\"&VLOOKUP(AK76,List!$K$2:$M$447,2,FALSE)","v":"AHU03H08_C"},{"$f":"_xlfn.IFNA(\"L\"&AM76&\" \"&\"AT%Q\"&B70*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J76&\"*)\",\" \")","v":"LAHU03H08_C AT%Q64.7 :BOOL; (*空调机组NJ-3AP(KT)8-8-启停控制*)"},"LAHU03H08_C             AT%Q64.7       :BOOL; (*空调机组NJ-3AP(KT)8-8-启停控制*)",null,"AHU03H08_C","空调机组NJ-3AP(KT)8-8-启停控制",519]
[{"$nulls":5},9,null,"9+","9-","空调机组NJ-3AP(KT)8-9-启停控制",{"$nulls":16},"NJ-3AP(KT)8-9",{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-9","03H09","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"AHU03H09_C"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%Q\"&B70*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LAHU03H09_C AT%Q65.0 :BOOL; (*空调机组NJ-3AP(KT)8-9-启停控制*)"},"LAHU03H09_C             AT%Q65.0       :BOOL; (*空调机组NJ-3AP(KT)8-9-启停控制*)",null,"AHU03H09_C","空调机组NJ-3AP(KT)8-9-启停控制",520]
[{"$nulls":5},10,null,"10+","10-","空调机组NJ-3AP(KT)8-10-启停控制",{"$nulls":16},{"$f":"IF(AI78=\"\",\"\",AI78)","v":"NJ-3AP(KT)8-10"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-10","03H10","启停控制",{"$f":"AH78&\"-\"&AK78","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"AHU03H10_C"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B70*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LAHU03H10_C AT%Q65.1 :BOOL; (*空调机组NJ-3AP(KT)8-10-启停控制*)"},"LAHU03H10_C             AT%Q65.1       :BOOL; (*空调机组NJ-3AP(KT)8-10-启停控制*)",null,"AHU03H10_C",{"$f":"J78","v":"空调机组NJ-3AP(KT)8-10-启停控制"},521]
[{"$nulls":5},11,null,"11+","11-","照明控制箱NJ-3AL8-1-启停控制",{"$nulls":16},"NJ-3AL8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL8-1","03H01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"LCB03H01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B70*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LLCB03H01_C AT%Q65.2 :BOOL; (*照明控制箱NJ-3AL8-1-启停控制*)"},"LLCB03H01_C             AT%Q65.2       :BOOL; (*照明控制箱NJ-3AL8-1-启停控制*)",null,"LCB03H01_C","照明控制箱NJ-3AL8-1-启停控制",522]
[{"$nulls":5},12,null,"12+","12-","照明控制箱NJ-3AL8-2-启停控制",{"$nulls":16},"NJ-3AL8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL8-2","03H02","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"LCB03H02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B70*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LLCB03H02_C AT%Q65.3 :BOOL; (*照明控制箱NJ-3AL8-2-启停控制*)"},"LLCB03H02_C             AT%Q65.3       :BOOL; (*照明控制箱NJ-3AL8-2-启停控制*)",null,"LCB03H02_C","照明控制箱NJ-3AL8-2-启停控制",523]
[{"$nulls":5},13,null,"13+","13-","照明控制箱NJ-3AL8-3-启停控制",{"$nulls":16},"NJ-3AL8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL8-3","03H03","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":"LCB03H03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%Q\"&B70*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":"LLCB03H03_C AT%Q65.4 :BOOL; (*照明控制箱NJ-3AL8-3-启停控制*)"},"LLCB03H03_C             AT%Q65.4       :BOOL; (*照明控制箱NJ-3AL8-3-启停控制*)",null,"LCB03H03_C","照明控制箱NJ-3AL8-3-启停控制",524]
[{"$nulls":5},14,null,"14+","14-","照明控制箱NJ-3AL8-4-启停控制",{"$nulls":16},"NJ-3AL8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL8-4","03H04","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":"LCB03H04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%Q\"&B70*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":"LLCB03H04_C AT%Q65.5 :BOOL; (*照明控制箱NJ-3AL8-4-启停控制*)"},"LLCB03H04_C             AT%Q65.5       :BOOL; (*照明控制箱NJ-3AL8-4-启停控制*)",null,"LCB03H04_C","照明控制箱NJ-3AL8-4-启停控制",525]
[{"$nulls":5},15,null,"15+","15-","照明控制箱NJ-3AL8-5-启停控制",{"$nulls":16},"NJ-3AL8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-3AL8-5","03H05","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":"LCB03H05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%Q\"&B70*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":"LLCB03H05_C AT%Q65.6 :BOOL; (*照明控制箱NJ-3AL8-5-启停控制*)"},"LLCB03H05_C             AT%Q65.6       :BOOL; (*照明控制箱NJ-3AL8-5-启停控制*)",null,"LCB03H05_C","照明控制箱NJ-3AL8-5-启停控制",526]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL84,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH84,List!$B$3:$D$445,2,FALSE)&AJ84&\"_\"&VLOOKUP(AK84,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM84&\" \"&\"AT%Q\"&B70*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J84&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",527]
[null,{"$f":"B90","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B90&\"地址: \"&B87&\" *)\"","v":"(* IOM 0801U地址: 5 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH86&AA86&\"-\"&AK86","v":"空调机组NJ-3AP(KT)8-1-回风温度"},{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-3AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-1","03H01","回风温度",{"$f":"AH86&\"-\"&AK86","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"AHU03H01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%I\"&B87*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LAHU03H01_RT AT%I80.0 :INT ; (*空调机组NJ-3AP(KT)8-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86))),SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN86,SEARCH(\"AT%\",AN86),,REPT(\" \",25-SEARCH(\"AT%\",AN86)))))),\" \")","v":"LAHU03H01_RT            AT%I80.0       :INT ; (*空调机组NJ-3AP(KT)8-1-回风温度*)"},null,{"$f":"AM86","v":"AHU03H01_RT"},{"$f":"J86","v":"空调机组NJ-3AP(KT)8-1-回风温度"},{"$f":"30000+($B87*8+F86-1)","v":30040}]
[null,5,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-3AP(KT)8-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI87=\"\",\"\",AI87)","v":"NJ-3AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-1","03H01","水阀反馈",{"$f":"AH87&\"-\"&AK87","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"AHU03H01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%I\"&B87*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LAHU03H01_WVB AT%I82.0 :INT ; (*空调机组NJ-3AP(KT)8-1-水阀反馈*)"},"LAHU03H01_WVB           AT%I82.0       :INT ; (*空调机组NJ-3AP(KT)8-1-水阀反馈*)",null,"AHU03H01_WVB",{"$f":"J87","v":"空调机组NJ-3AP(KT)8-1-水阀反馈"},{"$f":"AS86+1","v":30041}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)8-2-回风温度",{"$nulls":16},"NJ-3AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-2","03H02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"AHU03H02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%I\"&B87*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LAHU03H02_RT AT%I84.0 :INT ; (*空调机组NJ-3AP(KT)8-2-回风温度*)"},"LAHU03H02_RT            AT%I84.0       :INT ; (*空调机组NJ-3AP(KT)8-2-回风温度*)",null,"AHU03H02_RT","空调机组NJ-3AP(KT)8-2-回风温度",{"$f":"AS87+1","v":30042}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-3AP(KT)8-2-水阀反馈",{"$nulls":16},"NJ-3AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-2","03H02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":"AHU03H02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%I\"&B87*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":"LAHU03H02_WVB AT%I86.0 :INT ; (*空调机组NJ-3AP(KT)8-2-水阀反馈*)"},"LAHU03H02_WVB           AT%I86.0       :INT ; (*空调机组NJ-3AP(KT)8-2-水阀反馈*)",null,"AHU03H02_WVB","空调机组NJ-3AP(KT)8-2-水阀反馈",30043]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B87),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-3AP(KT)8-3-回风温度",{"$nulls":16},"NJ-3AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-3","03H03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":"AHU03H03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%I\"&B87*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":"LAHU03H03_RT AT%I88.0 :INT ; (*空调机组NJ-3AP(KT)8-3-回风温度*)"},"LAHU03H03_RT            AT%I88.0       :INT ; (*空调机组NJ-3AP(KT)8-3-回风温度*)",null,"AHU03H03_RT","空调机组NJ-3AP(KT)8-3-回风温度",30044]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-3AP(KT)8-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI91=\"\",\"\",AI91)","v":"NJ-3AP(KT)8-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-3","03H03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH91,List!$B$3:$D$445,2,FALSE)&AJ91&\"_\"&VLOOKUP(AK91,List!$K$2:$M$447,2,FALSE)","v":"AHU03H03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM91&\" \"&\"AT%I\"&B87*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J91&\"*)\",\" \")","v":"LAHU03H03_WVB AT%I90.0 :INT ; (*空调机组NJ-3AP(KT)8-3-水阀反馈*)"},"LAHU03H03_WVB           AT%I90.0       :INT ; (*空调机组NJ-3AP(KT)8-3-水阀反馈*)",null,"AHU03H03_WVB",{"$f":"J91","v":"空调机组NJ-3AP(KT)8-3-水阀反馈"},30045]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-3AP(KT)8-4-回风温度",{"$nulls":16},"NJ-3AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-4","03H04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH92,List!$B$3:$D$445,2,FALSE)&AJ92&\"_\"&VLOOKUP(AK92,List!$K$2:$M$447,2,FALSE)","v":"AHU03H04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM92&\" \"&\"AT%I\"&B87*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J92&\"*)\",\" \")","v":"LAHU03H04_RT AT%I92.0 :INT ; (*空调机组NJ-3AP(KT)8-4-回风温度*)"},"LAHU03H04_RT            AT%I92.0       :INT ; (*空调机组NJ-3AP(KT)8-4-回风温度*)",null,"AHU03H04_RT","空调机组NJ-3AP(KT)8-4-回风温度",30046]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B89=20,1,IF(B89=50,10,IF(B89=125,11,IF(B89=250,100,IF(B89=500,101,IF(B89=800,110,IF(B89=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-3AP(KT)8-4-水阀反馈",{"$nulls":16},"NJ-3AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL93,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL93,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-4","03H04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH93,List!$B$3:$D$445,2,FALSE)&AJ93&\"_\"&VLOOKUP(AK93,List!$K$2:$M$447,2,FALSE)","v":"AHU03H04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM93&\" \"&\"AT%I\"&B87*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J93&\"*)\",\" \")","v":"LAHU03H04_WVB AT%I94.0 :INT ; (*空调机组NJ-3AP(KT)8-4-水阀反馈*)"},"LAHU03H04_WVB           AT%I94.0       :INT ; (*空调机组NJ-3AP(KT)8-4-水阀反馈*)",null,"AHU03H04_WVB","空调机组NJ-3AP(KT)8-4-水阀反馈",30047]
[null,{"$f":"B99","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B99&\"地址: \"&B96&\" *)\"","v":"(* IOM 0801U地址: 6 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH95&AA95&\"-\"&AK95","v":"空调机组NJ-3AP(KT)8-5-回风温度"},{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-3AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-5","03H05","回风温度",{"$f":"AH95&\"-\"&AK95","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"AHU03H05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%I\"&B96*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LAHU03H05_RT AT%I96.0 :INT ; (*空调机组NJ-3AP(KT)8-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95))),SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN95,SEARCH(\"AT%\",AN95),,REPT(\" \",25-SEARCH(\"AT%\",AN95)))))),\" \")","v":"LAHU03H05_RT            AT%I96.0       :INT ; (*空调机组NJ-3AP(KT)8-5-回风温度*)"},null,{"$f":"AM95","v":"AHU03H05_RT"},{"$f":"J95","v":"空调机组NJ-3AP(KT)8-5-回风温度"},{"$f":"30000+($B96*8+F95-1)","v":30048}]
[null,6,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-3AP(KT)8-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI96=\"\",\"\",AI96)","v":"NJ-3AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-5","03H05","水阀反馈",{"$f":"AH96&\"-\"&AK96","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"AHU03H05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%I\"&B96*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LAHU03H05_WVB AT%I98.0 :INT ; (*空调机组NJ-3AP(KT)8-5-水阀反馈*)"},"LAHU03H05_WVB           AT%I98.0       :INT ; (*空调机组NJ-3AP(KT)8-5-水阀反馈*)",null,"AHU03H05_WVB",{"$f":"J96","v":"空调机组NJ-3AP(KT)8-5-水阀反馈"},{"$f":"AS95+1","v":30049}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)8-6-回风温度",{"$nulls":16},"NJ-3AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-6","03H06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":"AHU03H06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%I\"&B96*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":"LAHU03H06_RT AT%I100.0 :INT ; (*空调机组NJ-3AP(KT)8-6-回风温度*)"},"LAHU03H06_RT            AT%I100.0      :INT ; (*空调机组NJ-3AP(KT)8-6-回风温度*)",null,"AHU03H06_RT","空调机组NJ-3AP(KT)8-6-回风温度",{"$f":"AS96+1","v":30050}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-3AP(KT)8-6-水阀反馈",{"$nulls":16},"NJ-3AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-6","03H06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":"AHU03H06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%I\"&B96*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":"LAHU03H06_WVB AT%I102.0 :INT ; (*空调机组NJ-3AP(KT)8-6-水阀反馈*)"},"LAHU03H06_WVB           AT%I102.0      :INT ; (*空调机组NJ-3AP(KT)8-6-水阀反馈*)",null,"AHU03H06_WVB","空调机组NJ-3AP(KT)8-6-水阀反馈",30051]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B96),REPT(0,5))),1,1))","v":0},5,null,5,"0V","空调机组NJ-3AP(KT)8-7-回风温度",{"$nulls":16},"NJ-3AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-7","03H07","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH99,List!$B$3:$D$445,2,FALSE)&AJ99&\"_\"&VLOOKUP(AK99,List!$K$2:$M$447,2,FALSE)","v":"AHU03H07_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM99&\" \"&\"AT%I\"&B96*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J99&\"*)\",\" \")","v":"LAHU03H07_RT AT%I104.0 :INT ; (*空调机组NJ-3AP(KT)8-7-回风温度*)"},"LAHU03H07_RT            AT%I104.0      :INT ; (*空调机组NJ-3AP(KT)8-7-回风温度*)",null,"AHU03H07_RT","空调机组NJ-3AP(KT)8-7-回风温度",30052]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-3AP(KT)8-7-水阀反馈",{"$nulls":16},"NJ-3AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-7","03H07","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH100,List!$B$3:$D$445,2,FALSE)&AJ100&\"_\"&VLOOKUP(AK100,List!$K$2:$M$447,2,FALSE)","v":"AHU03H07_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM100&\" \"&\"AT%I\"&B96*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J100&\"*)\",\" \")","v":"LAHU03H07_WVB AT%I106.0 :INT ; (*空调机组NJ-3AP(KT)8-7-水阀反馈*)"},"LAHU03H07_WVB           AT%I106.0      :INT ; (*空调机组NJ-3AP(KT)8-7-水阀反馈*)",null,"AHU03H07_WVB",{"$f":"J100","v":"空调机组NJ-3AP(KT)8-7-水阀反馈"},30053]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-3AP(KT)8-8-回风温度",{"$nulls":16},"NJ-3AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-8","03H08","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH101,List!$B$3:$D$445,2,FALSE)&AJ101&\"_\"&VLOOKUP(AK101,List!$K$2:$M$447,2,FALSE)","v":"AHU03H08_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM101&\" \"&\"AT%I\"&B96*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J101&\"*)\",\" \")","v":"LAHU03H08_RT AT%I108.0 :INT ; (*空调机组NJ-3AP(KT)8-8-回风温度*)"},"LAHU03H08_RT            AT%I108.0      :INT ; (*空调机组NJ-3AP(KT)8-8-回风温度*)",null,"AHU03H08_RT","空调机组NJ-3AP(KT)8-8-回风温度",30054]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B98=20,1,IF(B98=50,10,IF(B98=125,11,IF(B98=250,100,IF(B98=500,101,IF(B98=800,110,IF(B98=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-3AP(KT)8-8-水阀反馈",{"$nulls":16},{"$f":"IF(AI102=\"\",\"\",AI102)","v":"NJ-3AP(KT)8-8"},{"$f":"_xlfn.IFNA(VLOOKUP(AL102,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL102,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-8","03H08","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH102,List!$B$3:$D$445,2,FALSE)&AJ102&\"_\"&VLOOKUP(AK102,List!$K$2:$M$447,2,FALSE)","v":"AHU03H08_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM102&\" \"&\"AT%I\"&B96*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J102&\"*)\",\" \")","v":"LAHU03H08_WVB AT%I110.0 :INT ; (*空调机组NJ-3AP(KT)8-8-水阀反馈*)"},"LAHU03H08_WVB           AT%I110.0      :INT ; (*空调机组NJ-3AP(KT)8-8-水阀反馈*)",null,"AHU03H08_WVB","空调机组NJ-3AP(KT)8-8-水阀反馈",30055]
[null,{"$f":"B108","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B108&\"地址: \"&B105&\" *)\"","v":"(* IOM 0401U地址: 7 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH104&AA104&\"-\"&AK104","v":"空调机组NJ-3AP(KT)8-9-回风温度"},{"$nulls":16},{"$f":"IF(AI104=\"\",\"\",AI104)","v":"NJ-3AP(KT)8-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-9","03H09","回风温度",{"$f":"AH104&\"-\"&AK104","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"AHU03H09_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%I\"&B105*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LAHU03H09_RT AT%I112.0 :INT ; (*空调机组NJ-3AP(KT)8-9-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104))),SEARCH(\":\",REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN104,SEARCH(\"AT%\",AN104),,REPT(\" \",25-SEARCH(\"AT%\",AN104)))))),\" \")","v":"LAHU03H09_RT            AT%I112.0      :INT ; (*空调机组NJ-3AP(KT)8-9-回风温度*)"},null,{"$f":"AM104","v":"AHU03H09_RT"},{"$f":"J104","v":"空调机组NJ-3AP(KT)8-9-回风温度"},{"$f":"30000+($B105*8+F104-1)","v":30056}]
[null,7,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-3AP(KT)8-9-水阀反馈",{"$nulls":16},{"$f":"IF(AI105=\"\",\"\",AI105)","v":"NJ-3AP(KT)8-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-9","03H09","水阀反馈",{"$f":"AH105&\"-\"&AK105","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"AHU03H09_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%I\"&B105*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LAHU03H09_WVB AT%I114.0 :INT ; (*空调机组NJ-3AP(KT)8-9-水阀反馈*)"},"LAHU03H09_WVB           AT%I114.0      :INT ; (*空调机组NJ-3AP(KT)8-9-水阀反馈*)",null,"AHU03H09_WVB",{"$f":"J105","v":"空调机组NJ-3AP(KT)8-9-水阀反馈"},{"$f":"AS104+1","v":30057}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),3,1))","v":1},3,null,3,"0V","空调机组NJ-3AP(KT)8-10-回风温度",{"$nulls":16},"NJ-3AP(KT)8-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-10","03H10","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":"AHU03H10_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%I\"&B105*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":"LAHU03H10_RT AT%I116.0 :INT ; (*空调机组NJ-3AP(KT)8-10-回风温度*)"},"LAHU03H10_RT            AT%I116.0      :INT ; (*空调机组NJ-3AP(KT)8-10-回风温度*)",null,"AHU03H10_RT","空调机组NJ-3AP(KT)8-10-回风温度",{"$f":"AS105+1","v":30058}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-3AP(KT)8-10-水阀反馈",{"$nulls":16},"NJ-3AP(KT)8-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-10","03H10","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH107,List!$B$3:$D$445,2,FALSE)&AJ107&\"_\"&VLOOKUP(AK107,List!$K$2:$M$447,2,FALSE)","v":"AHU03H10_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM107&\" \"&\"AT%I\"&B105*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J107&\"*)\",\" \")","v":"LAHU03H10_WVB AT%I118.0 :INT ; (*空调机组NJ-3AP(KT)8-10-水阀反馈*)"},"LAHU03H10_WVB           AT%I118.0      :INT ; (*空调机组NJ-3AP(KT)8-10-水阀反馈*)",null,"AHU03H10_WVB","空调机组NJ-3AP(KT)8-10-水阀反馈",30059]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B105),REPT(0,5))),1,1))","v":0}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B107=20,1,IF(B107=50,10,IF(B107=125,11,IF(B107=250,100,IF(B107=500,101,IF(B107=800,110,IF(B107=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B117","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B117&\"地址: \"&B114&\" *)\"","v":"(* IOM 0401A地址: 8 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH113&AA113&\"-\"&AK113","v":"空调机组NJ-3AP(KT)8-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI113=\"\",\"\",AI113)","v":"NJ-3AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-1","03H01","水阀控制",{"$f":"AH113&\"-\"&AK113","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH113,List!$B$3:$D$445,2,FALSE)&AJ113&\"_\"&VLOOKUP(AK113,List!$K$2:$M$447,2,FALSE)","v":"AHU03H01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM113&\" \"&\"AT%Q\"&B114*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J113&\"*)\",\" \")","v":"LAHU03H01_WVC AT%Q128.0 :INT ; (*空调机组NJ-3AP(KT)8-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN113,SEARCH(\"AT%\",AN113),,REPT(\" \",25-SEARCH(\"AT%\",AN113))),SEARCH(\":\",REPLACE(AN113,SEARCH(\"AT%\",AN113),,REPT(\" \",25-SEARCH(\"AT%\",AN113)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN113,SEARCH(\"AT%\",AN113),,REPT(\" \",25-SEARCH(\"AT%\",AN113)))))),\" \")","v":"LAHU03H01_WVC           AT%Q128.0      :INT ; (*空调机组NJ-3AP(KT)8-1-水阀控制*)"},null,{"$f":"AM113","v":"AHU03H01_WVC"},{"$f":"J113","v":"空调机组NJ-3AP(KT)8-1-水阀控制"},{"$f":"40000+($B114*8+F113-1)","v":40064}]
[null,8,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH114&AA114&\"-\"&AK114","v":"空调机组NJ-3AP(KT)8-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI114=\"\",\"\",AI114)","v":"NJ-3AP(KT)8-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-2","03H02","水阀控制",{"$f":"AH114&\"-\"&AK114","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH114,List!$B$3:$D$445,2,FALSE)&AJ114&\"_\"&VLOOKUP(AK114,List!$K$2:$M$447,2,FALSE)","v":"AHU03H02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM114&\" \"&\"AT%Q\"&B114*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J114&\"*)\",\" \")","v":"LAHU03H02_WVC AT%Q130.0 :INT ; (*空调机组NJ-3AP(KT)8-2-水阀控制*)"},"LAHU03H02_WVC           AT%Q130.0      :INT ; (*空调机组NJ-3AP(KT)8-2-水阀控制*)",null,"AHU03H02_WVC",{"$f":"J114","v":"空调机组NJ-3AP(KT)8-2-水阀控制"},{"$f":"AS113+1","v":40065}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH115&AA115&\"-\"&AK115","v":"空调机组NJ-3AP(KT)8-3-水阀控制"},{"$nulls":16},"NJ-3AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-3","03H03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH115,List!$B$3:$D$445,2,FALSE)&AJ115&\"_\"&VLOOKUP(AK115,List!$K$2:$M$447,2,FALSE)","v":"AHU03H03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM115&\" \"&\"AT%Q\"&B114*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J115&\"*)\",\" \")","v":"LAHU03H03_WVC AT%Q132.0 :INT ; (*空调机组NJ-3AP(KT)8-3-水阀控制*)"},"LAHU03H03_WVC           AT%Q132.0      :INT ; (*空调机组NJ-3AP(KT)8-3-水阀控制*)",null,"AHU03H03_WVC","空调机组NJ-3AP(KT)8-3-水阀控制",{"$f":"AS114+1","v":40066}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH116&AA116&\"-\"&AK116","v":"空调机组NJ-3AP(KT)8-4-水阀控制"},{"$nulls":16},"NJ-3AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-4","03H04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH116,List!$B$3:$D$445,2,FALSE)&AJ116&\"_\"&VLOOKUP(AK116,List!$K$2:$M$447,2,FALSE)","v":"AHU03H04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM116&\" \"&\"AT%Q\"&B114*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J116&\"*)\",\" \")","v":"LAHU03H04_WVC AT%Q134.0 :INT ; (*空调机组NJ-3AP(KT)8-4-水阀控制*)"},"LAHU03H04_WVC           AT%Q134.0      :INT ; (*空调机组NJ-3AP(KT)8-4-水阀控制*)",null,"AHU03H04_WVC","空调机组NJ-3AP(KT)8-4-水阀控制",40067]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B114),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B116=20,1,IF(B116=50,10,IF(B116=125,11,IF(B116=250,100,IF(B116=500,101,IF(B116=800,110,IF(B116=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B126","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B126&\"地址: \"&B123&\" *)\"","v":"(* IOM 0401A地址: 9 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH122&AA122&\"-\"&AK122","v":"空调机组NJ-3AP(KT)8-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI122=\"\",\"\",AI122)","v":"NJ-3AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-5","03H05","水阀控制",{"$f":"AH122&\"-\"&AK122","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH122,List!$B$3:$D$445,2,FALSE)&AJ122&\"_\"&VLOOKUP(AK122,List!$K$2:$M$447,2,FALSE)","v":"AHU03H05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM122&\" \"&\"AT%Q\"&B123*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J122&\"*)\",\" \")","v":"LAHU03H05_WVC AT%Q144.0 :INT ; (*空调机组NJ-3AP(KT)8-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN122,SEARCH(\"AT%\",AN122),,REPT(\" \",25-SEARCH(\"AT%\",AN122))),SEARCH(\":\",REPLACE(AN122,SEARCH(\"AT%\",AN122),,REPT(\" \",25-SEARCH(\"AT%\",AN122)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN122,SEARCH(\"AT%\",AN122),,REPT(\" \",25-SEARCH(\"AT%\",AN122)))))),\" \")","v":"LAHU03H05_WVC           AT%Q144.0      :INT ; (*空调机组NJ-3AP(KT)8-5-水阀控制*)"},null,{"$f":"AM122","v":"AHU03H05_WVC"},{"$f":"J122","v":"空调机组NJ-3AP(KT)8-5-水阀控制"},{"$f":"40000+($B123*8+F122-1)","v":40072}]
[null,9,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH123&AA123&\"-\"&AK123","v":"空调机组NJ-3AP(KT)8-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI123=\"\",\"\",AI123)","v":"NJ-3AP(KT)8-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-6","03H06","水阀控制",{"$f":"AH123&\"-\"&AK123","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH123,List!$B$3:$D$445,2,FALSE)&AJ123&\"_\"&VLOOKUP(AK123,List!$K$2:$M$447,2,FALSE)","v":"AHU03H06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM123&\" \"&\"AT%Q\"&B123*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J123&\"*)\",\" \")","v":"LAHU03H06_WVC AT%Q146.0 :INT ; (*空调机组NJ-3AP(KT)8-6-水阀控制*)"},"LAHU03H06_WVC           AT%Q146.0      :INT ; (*空调机组NJ-3AP(KT)8-6-水阀控制*)",null,"AHU03H06_WVC",{"$f":"J123","v":"空调机组NJ-3AP(KT)8-6-水阀控制"},{"$f":"AS122+1","v":40073}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH124&AA124&\"-\"&AK124","v":"空调机组NJ-3AP(KT)8-7-水阀控制"},{"$nulls":16},"NJ-3AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-7","03H07","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH124,List!$B$3:$D$445,2,FALSE)&AJ124&\"_\"&VLOOKUP(AK124,List!$K$2:$M$447,2,FALSE)","v":"AHU03H07_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM124&\" \"&\"AT%Q\"&B123*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J124&\"*)\",\" \")","v":"LAHU03H07_WVC AT%Q148.0 :INT ; (*空调机组NJ-3AP(KT)8-7-水阀控制*)"},"LAHU03H07_WVC           AT%Q148.0      :INT ; (*空调机组NJ-3AP(KT)8-7-水阀控制*)",null,"AHU03H07_WVC","空调机组NJ-3AP(KT)8-7-水阀控制",{"$f":"AS123+1","v":40074}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH125&AA125&\"-\"&AK125","v":"空调机组NJ-3AP(KT)8-8-水阀控制"},{"$nulls":16},"NJ-3AP(KT)8-8",{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL125,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-8","03H08","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH125,List!$B$3:$D$445,2,FALSE)&AJ125&\"_\"&VLOOKUP(AK125,List!$K$2:$M$447,2,FALSE)","v":"AHU03H08_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM125&\" \"&\"AT%Q\"&B123*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J125&\"*)\",\" \")","v":"LAHU03H08_WVC AT%Q150.0 :INT ; (*空调机组NJ-3AP(KT)8-8-水阀控制*)"},"LAHU03H08_WVC           AT%Q150.0      :INT ; (*空调机组NJ-3AP(KT)8-8-水阀控制*)",null,"AHU03H08_WVC","空调机组NJ-3AP(KT)8-8-水阀控制",40075]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B123),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B125=20,1,IF(B125=50,10,IF(B125=125,11,IF(B125=250,100,IF(B125=500,101,IF(B125=800,110,IF(B125=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B135","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B135&\"地址: \"&B132&\" *)\"","v":"(* IOM 0401A地址: 10 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B132),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B132),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH131&AA131&\"-\"&AK131","v":"空调机组NJ-3AP(KT)8-9-水阀控制"},{"$nulls":16},{"$f":"IF(AI131=\"\",\"\",AI131)","v":"NJ-3AP(KT)8-9"},{"$f":"_xlfn.IFNA(VLOOKUP(AL131,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL131,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-9","03H09","水阀控制",{"$f":"AH131&\"-\"&AK131","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH131,List!$B$3:$D$445,2,FALSE)&AJ131&\"_\"&VLOOKUP(AK131,List!$K$2:$M$447,2,FALSE)","v":"AHU03H09_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM131&\" \"&\"AT%Q\"&B132*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J131&\"*)\",\" \")","v":"LAHU03H09_WVC AT%Q160.0 :INT ; (*空调机组NJ-3AP(KT)8-9-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN131,SEARCH(\"AT%\",AN131),,REPT(\" \",25-SEARCH(\"AT%\",AN131))),SEARCH(\":\",REPLACE(AN131,SEARCH(\"AT%\",AN131),,REPT(\" \",25-SEARCH(\"AT%\",AN131)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN131,SEARCH(\"AT%\",AN131),,REPT(\" \",25-SEARCH(\"AT%\",AN131)))))),\" \")","v":"LAHU03H09_WVC           AT%Q160.0      :INT ; (*空调机组NJ-3AP(KT)8-9-水阀控制*)"},null,{"$f":"AM131","v":"AHU03H09_WVC"},{"$f":"J131","v":"空调机组NJ-3AP(KT)8-9-水阀控制"},{"$f":"40000+($B132*8+F131-1)","v":40080}]
[null,10,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B132),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B132),REPT(0,5))),4,1))","v":1},2,null,3,4,{"$f":"AH132&AA132&\"-\"&AK132","v":"空调机组NJ-3AP(KT)8-10-水阀控制"},{"$nulls":16},{"$f":"IF(AI132=\"\",\"\",AI132)","v":"NJ-3AP(KT)8-10"},{"$f":"_xlfn.IFNA(VLOOKUP(AL132,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL132,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-3AP(KT)8-10","03H10","水阀控制",{"$f":"AH132&\"-\"&AK132","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH132,List!$B$3:$D$445,2,FALSE)&AJ132&\"_\"&VLOOKUP(AK132,List!$K$2:$M$447,2,FALSE)","v":"AHU03H10_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM132&\" \"&\"AT%Q\"&B132*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J132&\"*)\",\" \")","v":"LAHU03H10_WVC AT%Q162.0 :INT ; (*空调机组NJ-3AP(KT)8-10-水阀控制*)"},"LAHU03H10_WVC           AT%Q162.0      :INT ; (*空调机组NJ-3AP(KT)8-10-水阀控制*)",null,"AHU03H10_WVC",{"$f":"J132","v":"空调机组NJ-3AP(KT)8-10-水阀控制"},{"$f":"AS131+1","v":40081}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B132),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B132),REPT(0,5))),3,1))","v":0},3,null,5,6,{"$f":"AH133&AA133&\"-\"&AK133","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL133,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL133,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH133,List!$B$3:$D$445,2,FALSE)&AJ133&\"_\"&VLOOKUP(AK133,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM133&\" \"&\"AT%Q\"&B132*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J133&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",{"$f":"AS132+1","v":40082}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B132),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B132),REPT(0,5))),2,1))","v":1},4,null,7,8,{"$f":"AH134&AA134&\"-\"&AK134","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL134,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL134,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH134,List!$B$3:$D$445,2,FALSE)&AJ134&\"_\"&VLOOKUP(AK134,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM134&\" \"&\"AT%Q\"&B132*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J134&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40083]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B132),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B132),REPT(0,5))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B134=20,1,IF(B134=50,10,IF(B134=125,11,IF(B134=250,100,IF(B134=500,101,IF(B134=800,110,IF(B134=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B134=20,1,IF(B134=50,10,IF(B134=125,11,IF(B134=250,100,IF(B134=500,101,IF(B134=800,110,IF(B134=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B134=20,1,IF(B134=50,10,IF(B134=125,11,IF(B134=250,100,IF(B134=500,101,IF(B134=800,110,IF(B134=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B134=20,1,IF(B134=50,10,IF(B134=125,11,IF(B134=250,100,IF(B134=500,101,IF(B134=800,110,IF(B134=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B134=20,1,IF(B134=50,10,IF(B134=125,11,IF(B134=250,100,IF(B134=500,101,IF(B134=800,110,IF(B134=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B134=20,1,IF(B134=50,10,IF(B134=125,11,IF(B134=250,100,IF(B134=500,101,IF(B134=800,110,IF(B134=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L408","index":44,"n_rows":137,"n_cols":45,"rows_kept":137,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[41,5,41,6],[41,9,41,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[50,5,50,6],[50,9,50,25],[51,5,51,6],[51,9,51,25],[52,5,52,6],[52,9,52,25],[53,5,53,6],[53,9,53,25],[54,5,54,6],[54,9,54,25],[55,5,55,6],[55,9,55,25],[56,5,56,6],[56,9,56,25],[58,5,58,6],[58,9,58,25],[59,5,59,6],[59,9,59,25],[60,5,60,6],[60,9,60,25],[61,5,61,6],[61,9,61,25],[62,5,62,6],[62,9,62,25],[63,5,63,6],[63,9,63,25],[64,5,64,6],[64,9,64,25],[65,5,65,6],[65,9,65,25],[67,5,67,6],[67,9,67,25],[68,5,68,6],[68,9,68,25],[69,5,69,6],[69,9,69,25],[70,5,70,6],[70,9,70,25],[71,5,71,6],[71,9,71,25],[72,5,72,6],[72,9,72,25],[73,5,73,6],[73,9,73,25],[74,5,74,6],[74,9,74,25],[75,5,75,6],[75,9,75,25],[76,5,76,6],[76,9,76,25],[77,5,77,6],[77,9,77,25],[78,5,78,6],[78,9,78,25],[79,5,79,6],[79,9,79,25],[80,5,80,6],[80,9,80,25],[81,5,81,6],[81,9,81,25],[82,5,82,6],[82,9,82,25],[84,5,84,6],[84,9,84,25],[85,5,85,6],[85,9,85,25],[86,5,86,6],[86,9,86,25],[87,5,87,6],[87,9,87,25],[88,5,88,6],[88,9,88,25],[89,5,89,6],[89,9,89,25],[90,5,90,6],[90,9,90,25],[91,5,91,6],[91,9,91,25],[93,5,93,6],[93,9,93,25],[94,5,94,6],[94,9,94,25],[95,5,95,6],[95,9,95,25],[96,5,96,6],[96,9,96,25],[97,5,97,6],[97,9,97,25],[98,5,98,6],[98,9,98,25],[99,5,99,6],[99,9,99,25],[100,5,100,6],[100,9,100,25],[102,5,102,6],[102,9,102,25],[103,5,103,6],[103,9,103,25],[104,5,104,6],[104,9,104,25],[105,5,105,6],[105,9,105,25],[106,5,106,6],[106,9,106,25],[107,5,107,6],[107,9,107,25],[108,5,108,6],[108,9,108,25],[109,5,109,6],[109,9,109,25],[111,5,111,6],[111,9,111,25],[112,5,112,6],[112,9,112,25],[113,5,113,6],[113,9,113,25],[114,5,114,6],[114,9,114,25],[115,5,115,6],[115,9,115,25],[116,5,116,6],[116,9,116,25],[117,5,117,6],[117,9,117,25],[118,5,118,6],[118,9,118,25],[120,5,120,6],[120,9,120,25],[121,5,121,6],[121,9,121,25],[122,5,122,6],[122,9,122,25],[123,5,123,6],[123,9,123,25],[124,5,124,6],[124,9,124,25],[125,5,125,6],[125,9,125,25],[126,5,126,6],[126,9,126,25],[127,5,127,6],[127,9,127,25],[129,5,129,6],[129,9,129,25],[130,5,130,6],[130,9,130,25],[131,5,131,6],[131,9,131,25],[132,5,132,6],[132,9,132,25],[133,5,133,6],[133,9,133,25],[134,5,134,6],[134,9,134,25],[135,5,135,6],[135,9,135,25],[136,5,136,6],[136,9,136,25],[4,1,5,1],[11,1,22,1],[28,1,39,1],[45,1,56,1],[62,1,65,1],[71,1,82,1],[88,1,91,1],[97,1,100,1],[106,1,109,1],[115,1,118,1],[124,1,127,1],[133,1,136,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4],[32,2,39,4],[75,2,82,4],[49,2,56,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L26",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 11 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH8&AA8&\"-\"&AK8","v":"空调机组NJ-4AP(KT)8-1-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-4AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-1","04H01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH8,List!$B$3:$D$445,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,List!$K$2:$M$447,2,FALSE)","v":"AHU04H01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LAHU04H01_R AT%I176.0 :BOOL; (*空调机组NJ-4AP(KT)8-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LAHU04H01_R             AT%I176.0      :BOOL; (*空调机组NJ-4AP(KT)8-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L26\\L26AHU04H01_R"},{"$f":"J8","v":"空调机组NJ-4AP(KT)8-1-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":11408}]
[null,11,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},2,null,3,4,"空调机组NJ-4AP(KT)8-1-故障状态",{"$nulls":16},{"$f":"IF(AI9=\"\",\"\",AI9)","v":"NJ-4AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-1","04H01","故障状态",{"$f":"AH9&\"-\"&AK9","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH9,List!$B$3:$D$445,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,List!$K$2:$M$447,2,FALSE)","v":"AHU04H01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LAHU04H01_F AT%I176.1 :BOOL; (*空调机组NJ-4AP(KT)8-1-故障状态*)"},"LAHU04H01_F             AT%I176.1      :BOOL; (*空调机组NJ-4AP(KT)8-1-故障状态*)",null,"L26\\L26AHU04H01_F",{"$f":"J9","v":"空调机组NJ-4AP(KT)8-1-故障状态"},{"$f":"AS8+1","v":11409}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},3,null,5,6,"空调机组NJ-4AP(KT)8-1-自动状态",{"$nulls":16},"NJ-4AP(KT)8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-1","04H01","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH10,List!$B$3:$D$445,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,List!$K$2:$M$447,2,FALSE)","v":"AHU04H01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LAHU04H01_A AT%I176.2 :BOOL; (*空调机组NJ-4AP(KT)8-1-自动状态*)"},"LAHU04H01_A             AT%I176.2      :BOOL; (*空调机组NJ-4AP(KT)8-1-自动状态*)",null,"L26\\L26AHU04H01_A","空调机组NJ-4AP(KT)8-1-自动状态",{"$f":"AS9+1","v":11410}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-4AP(KT)8-1-风机压差",{"$nulls":16},"NJ-4AP(KT)8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-1","04H01","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH11,List!$B$3:$D$445,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,List!$K$2:$M$447,2,FALSE)","v":"AHU04H01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LAHU04H01_FPS AT%I176.3 :BOOL; (*空调机组NJ-4AP(KT)8-1-风机压差*)"},"LAHU04H01_FPS           AT%I176.3      :BOOL; (*空调机组NJ-4AP(KT)8-1-风机压差*)",null,"L26\\L26AHU04H01_FPS","空调机组NJ-4AP(KT)8-1-风机压差",11411]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-4AP(KT)8-2-运行状态",{"$nulls":16},"NJ-4AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-2","04H02","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH12,List!$B$3:$D$445,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,List!$K$2:$M$447,2,FALSE)","v":"AHU04H02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LAHU04H02_R AT%I176.4 :BOOL; (*空调机组NJ-4AP(KT)8-2-运行状态*)"},"LAHU04H02_R             AT%I176.4      :BOOL; (*空调机组NJ-4AP(KT)8-2-运行状态*)",null,"L26\\L26AHU04H02_R","空调机组NJ-4AP(KT)8-2-运行状态",11412]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-4AP(KT)8-2-故障状态",{"$nulls":16},"NJ-4AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-2","04H02","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH13,List!$B$3:$D$445,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,List!$K$2:$M$447,2,FALSE)","v":"AHU04H02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LAHU04H02_F AT%I176.5 :BOOL; (*空调机组NJ-4AP(KT)8-2-故障状态*)"},"LAHU04H02_F             AT%I176.5      :BOOL; (*空调机组NJ-4AP(KT)8-2-故障状态*)",null,"L26\\L26AHU04H02_F","空调机组NJ-4AP(KT)8-2-故障状态",11413]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-4AP(KT)8-2-自动状态",{"$nulls":16},"NJ-4AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-2","04H02","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH14,List!$B$3:$D$445,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,List!$K$2:$M$447,2,FALSE)","v":"AHU04H02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LAHU04H02_A AT%I176.6 :BOOL; (*空调机组NJ-4AP(KT)8-2-自动状态*)"},"LAHU04H02_A             AT%I176.6      :BOOL; (*空调机组NJ-4AP(KT)8-2-自动状态*)",null,"L26\\L26AHU04H02_A","空调机组NJ-4AP(KT)8-2-自动状态",11414]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-4AP(KT)8-2-风机压差",{"$nulls":16},"NJ-4AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-2","04H02","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH15,List!$B$3:$D$445,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,List!$K$2:$M$447,2,FALSE)","v":"AHU04H02_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LAHU04H02_FPS AT%I176.7 :BOOL; (*空调机组NJ-4AP(KT)8-2-风机压差*)"},"LAHU04H02_FPS           AT%I176.7      :BOOL; (*空调机组NJ-4AP(KT)8-2-风机压差*)",null,"L26\\L26AHU04H02_FPS","空调机组NJ-4AP(KT)8-2-风机压差",11415]
[{"$nulls":5},9,null,17,18,"空调机组NJ-4AP(KT)8-3-运行状态",{"$nulls":16},"NJ-4AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-3","04H03","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH16,List!$B$3:$D$445,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,List!$K$2:$M$447,2,FALSE)","v":"AHU04H03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LAHU04H03_R AT%I177.0 :BOOL; (*空调机组NJ-4AP(KT)8-3-运行状态*)"},"LAHU04H03_R             AT%I177.0      :BOOL; (*空调机组NJ-4AP(KT)8-3-运行状态*)",null,"L26\\L26AHU04H03_R","空调机组NJ-4AP(KT)8-3-运行状态",11416]
[{"$nulls":5},10,null,19,20,"空调机组NJ-4AP(KT)8-3-故障状态",{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-4AP(KT)8-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-3","04H03","故障状态",{"$f":"AH17&\"-\"&AK17","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH17,List!$B$3:$D$445,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,List!$K$2:$M$447,2,FALSE)","v":"AHU04H03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LAHU04H03_F AT%I177.1 :BOOL; (*空调机组NJ-4AP(KT)8-3-故障状态*)"},"LAHU04H03_F             AT%I177.1      :BOOL; (*空调机组NJ-4AP(KT)8-3-故障状态*)",null,"L26\\L26AHU04H03_F","空调机组NJ-4AP(KT)8-3-故障状态",11417]
[{"$nulls":5},11,null,21,22,"空调机组NJ-4AP(KT)8-3-自动状态",{"$nulls":16},"NJ-4AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-3","04H03","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH18,List!$B$3:$D$445,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,List!$K$2:$M$447,2,FALSE)","v":"AHU04H03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LAHU04H03_A AT%I177.2 :BOOL; (*空调机组NJ-4AP(KT)8-3-自动状态*)"},"LAHU04H03_A             AT%I177.2      :BOOL; (*空调机组NJ-4AP(KT)8-3-自动状态*)",null,"L26\\L26AHU04H03_A","空调机组NJ-4AP(KT)8-3-自动状态",11418]
[{"$nulls":5},12,null,23,24,"空调机组NJ-4AP(KT)8-3-风机压差",{"$nulls":16},"NJ-4AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-3","04H03","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH19,List!$B$3:$D$445,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,List!$K$2:$M$447,2,FALSE)","v":"AHU04H03_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LAHU04H03_FPS AT%I177.3 :BOOL; (*空调机组NJ-4AP(KT)8-3-风机压差*)"},"LAHU04H03_FPS           AT%I177.3      :BOOL; (*空调机组NJ-4AP(KT)8-3-风机压差*)",null,"L26\\L26AHU04H03_FPS","空调机组NJ-4AP(KT)8-3-风机压差",11419]
[{"$nulls":5},13,null,25,26,"空调机组NJ-4AP(KT)8-4-运行状态",{"$nulls":16},"NJ-4AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-4","04H04","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH20,List!$B$3:$D$445,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,List!$K$2:$M$447,2,FALSE)","v":"AHU04H04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":"LAHU04H04_R AT%I177.4 :BOOL; (*空调机组NJ-4AP(KT)8-4-运行状态*)"},"LAHU04H04_R             AT%I177.4      :BOOL; (*空调机组NJ-4AP(KT)8-4-运行状态*)",null,"L26\\L26AHU04H04_R","空调机组NJ-4AP(KT)8-4-运行状态",11420]
[{"$nulls":5},14,null,27,28,"空调机组NJ-4AP(KT)8-4-故障状态",{"$nulls":16},"NJ-4AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-4","04H04","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH21,List!$B$3:$D$445,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,List!$K$2:$M$447,2,FALSE)","v":"AHU04H04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":"LAHU04H04_F AT%I177.5 :BOOL; (*空调机组NJ-4AP(KT)8-4-故障状态*)"},"LAHU04H04_F             AT%I177.5      :BOOL; (*空调机组NJ-4AP(KT)8-4-故障状态*)",null,"L26\\L26AHU04H04_F","空调机组NJ-4AP(KT)8-4-故障状态",11421]
[{"$nulls":5},15,null,29,30,"空调机组NJ-4AP(KT)8-4-自动状态",{"$nulls":16},"NJ-4AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-4","04H04","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH22,List!$B$3:$D$445,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,List!$K$2:$M$447,2,FALSE)","v":"AHU04H04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":"LAHU04H04_A AT%I177.6 :BOOL; (*空调机组NJ-4AP(KT)8-4-自动状态*)"},"LAHU04H04_A             AT%I177.6      :BOOL; (*空调机组NJ-4AP(KT)8-4-自动状态*)",null,"L26\\L26AHU04H04_A","空调机组NJ-4AP(KT)8-4-自动状态",11422]
[".",{"$nulls":4},16,null,31,32,"空调机组NJ-4AP(KT)8-4-风机压差",{"$nulls":16},"NJ-4AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-4","04H04","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH23,List!$B$3:$D$445,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,List!$K$2:$M$447,2,FALSE)","v":"AHU04H04_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":"LAHU04H04_FPS AT%I177.7 :BOOL; (*空调机组NJ-4AP(KT)8-4-风机压差*)"},"LAHU04H04_FPS           AT%I177.7      :BOOL; (*空调机组NJ-4AP(KT)8-4-风机压差*)",null,"L26\\L26AHU04H04_FPS","空调机组NJ-4AP(KT)8-4-风机压差",11423]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 1601R地址: 12 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH25&AA25&\"-\"&AK25","v":"空调机组NJ-4AP(KT)8-5-运行状态"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-4AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-5","04H05","运行状态",{"$f":"AH25&\"-\"&AK25","v":"空调机组-运行状态"},{"$f":"VLOOKUP(AH25,List!$B$3:$D$445,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,List!$K$2:$M$447,2,FALSE)","v":"AHU04H05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%I\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LAHU04H05_R AT%I192.0 :BOOL; (*空调机组NJ-4AP(KT)8-5-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LAHU04H05_R             AT%I192.0      :BOOL; (*空调机组NJ-4AP(KT)8-5-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L26\\L26AHU04H05_R"},{"$f":"J25","v":"空调机组NJ-4AP(KT)8-5-运行状态"},{"$f":"10000+($B26*16*8+F25-1)","v":11536}]
[null,12,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":0},2,null,3,4,"空调机组NJ-4AP(KT)8-5-故障状态",{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-4AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-5","04H05","故障状态",{"$f":"AH26&\"-\"&AK26","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH26,List!$B$3:$D$445,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,List!$K$2:$M$447,2,FALSE)","v":"AHU04H05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LAHU04H05_F AT%I192.1 :BOOL; (*空调机组NJ-4AP(KT)8-5-故障状态*)"},"LAHU04H05_F             AT%I192.1      :BOOL; (*空调机组NJ-4AP(KT)8-5-故障状态*)",null,"L26\\L26AHU04H05_F",{"$f":"J26","v":"空调机组NJ-4AP(KT)8-5-故障状态"},{"$f":"AS25+1","v":11537}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},3,null,5,6,"空调机组NJ-4AP(KT)8-5-自动状态",{"$nulls":16},"NJ-4AP(KT)8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-5","04H05","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH27,List!$B$3:$D$445,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,List!$K$2:$M$447,2,FALSE)","v":"AHU04H05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LAHU04H05_A AT%I192.2 :BOOL; (*空调机组NJ-4AP(KT)8-5-自动状态*)"},"LAHU04H05_A             AT%I192.2      :BOOL; (*空调机组NJ-4AP(KT)8-5-自动状态*)",null,"L26\\L26AHU04H05_A","空调机组NJ-4AP(KT)8-5-自动状态",{"$f":"AS26+1","v":11538}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":1},4,null,7,8,"空调机组NJ-4AP(KT)8-5-风机压差",{"$nulls":16},"NJ-4AP(KT)8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-5","04H05","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH28,List!$B$3:$D$445,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,List!$K$2:$M$447,2,FALSE)","v":"AHU04H05_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LAHU04H05_FPS AT%I192.3 :BOOL; (*空调机组NJ-4AP(KT)8-5-风机压差*)"},"LAHU04H05_FPS           AT%I192.3      :BOOL; (*空调机组NJ-4AP(KT)8-5-风机压差*)",null,"L26\\L26AHU04H05_FPS","空调机组NJ-4AP(KT)8-5-风机压差",11539]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":0},5,null,9,10,"空调机组NJ-4AP(KT)8-6-运行状态",{"$nulls":16},"NJ-4AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-6","04H06","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH29,List!$B$3:$D$445,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,List!$K$2:$M$447,2,FALSE)","v":"AHU04H06_R"},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":"LAHU04H06_R AT%I192.4 :BOOL; (*空调机组NJ-4AP(KT)8-6-运行状态*)"},"LAHU04H06_R             AT%I192.4      :BOOL; (*空调机组NJ-4AP(KT)8-6-运行状态*)",null,"L26\\L26AHU04H06_R","空调机组NJ-4AP(KT)8-6-运行状态",11540]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"空调机组NJ-4AP(KT)8-6-故障状态",{"$nulls":16},"NJ-4AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-6","04H06","故障状态","空调机组-故障状态",{"$f":"VLOOKUP(AH30,List!$B$3:$D$445,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,List!$K$2:$M$447,2,FALSE)","v":"AHU04H06_F"},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%I\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":"LAHU04H06_F AT%I192.5 :BOOL; (*空调机组NJ-4AP(KT)8-6-故障状态*)"},"LAHU04H06_F             AT%I192.5      :BOOL; (*空调机组NJ-4AP(KT)8-6-故障状态*)",null,"L26\\L26AHU04H06_F","空调机组NJ-4AP(KT)8-6-故障状态",11541]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"空调机组NJ-4AP(KT)8-6-自动状态",{"$nulls":16},"NJ-4AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-6","04H06","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH31,List!$B$3:$D$445,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,List!$K$2:$M$447,2,FALSE)","v":"AHU04H06_A"},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%I\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":"LAHU04H06_A AT%I192.6 :BOOL; (*空调机组NJ-4AP(KT)8-6-自动状态*)"},"LAHU04H06_A             AT%I192.6      :BOOL; (*空调机组NJ-4AP(KT)8-6-自动状态*)",null,"L26\\L26AHU04H06_A","空调机组NJ-4AP(KT)8-6-自动状态",11542]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"空调机组NJ-4AP(KT)8-6-风机压差",{"$nulls":16},"NJ-4AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-6","04H06","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH32,List!$B$3:$D$445,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,List!$K$2:$M$447,2,FALSE)","v":"AHU04H06_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%I\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":"LAHU04H06_FPS AT%I192.7 :BOOL; (*空调机组NJ-4AP(KT)8-6-风机压差*)"},"LAHU04H06_FPS           AT%I192.7      :BOOL; (*空调机组NJ-4AP(KT)8-6-风机压差*)",null,"L26\\L26AHU04H06_FPS","空调机组NJ-4AP(KT)8-6-风机压差",11543]
[{"$nulls":5},9,null,17,18,"空调机组NJ-4AP(KT)8-7-运行状态",{"$nulls":16},"NJ-4AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL33,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-7","04H07","运行状态","空调机组-运行状态",{"$f":"VLOOKUP(AH33,List!$B$3:$D$445,2,FALSE)&AJ33&\"_\"&VLOOKUP(AK33,List!$K$2:$M$447,2,FALSE)","v":"AHU04H07_R"},{"$f":"_xlfn.IFNA(\"L\"&AM33&\" \"&\"AT%I\"&B26*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J33&\"*)\",\" \")","v":"LAHU04H07_R AT%I193.0 :BOOL; (*空调机组NJ-4AP(KT)8-7-运行状态*)"},"LAHU04H07_R             AT%I193.0      :BOOL; (*空调机组NJ-4AP(KT)8-7-运行状态*)",null,"L26\\L26AHU04H07_R","空调机组NJ-4AP(KT)8-7-运行状态",11544]
[{"$nulls":5},10,null,19,20,"空调机组NJ-4AP(KT)8-7-故障状态",{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-4AP(KT)8-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-7","04H07","故障状态",{"$f":"AH34&\"-\"&AK34","v":"空调机组-故障状态"},{"$f":"VLOOKUP(AH34,List!$B$3:$D$445,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,List!$K$2:$M$447,2,FALSE)","v":"AHU04H07_F"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B26*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LAHU04H07_F AT%I193.1 :BOOL; (*空调机组NJ-4AP(KT)8-7-故障状态*)"},"LAHU04H07_F             AT%I193.1      :BOOL; (*空调机组NJ-4AP(KT)8-7-故障状态*)",null,"L26\\L26AHU04H07_F",{"$f":"J34","v":"空调机组NJ-4AP(KT)8-7-故障状态"},11545]
[{"$nulls":5},11,null,21,22,"空调机组NJ-4AP(KT)8-7-自动状态",{"$nulls":16},"NJ-4AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-7","04H07","自动状态","空调机组-自动状态",{"$f":"VLOOKUP(AH35,List!$B$3:$D$445,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,List!$K$2:$M$447,2,FALSE)","v":"AHU04H07_A"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B26*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LAHU04H07_A AT%I193.2 :BOOL; (*空调机组NJ-4AP(KT)8-7-自动状态*)"},"LAHU04H07_A             AT%I193.2      :BOOL; (*空调机组NJ-4AP(KT)8-7-自动状态*)",null,"L26\\L26AHU04H07_A","空调机组NJ-4AP(KT)8-7-自动状态",11546]
[{"$nulls":5},12,null,23,24,"空调机组NJ-4AP(KT)8-7-风机压差",{"$nulls":16},"NJ-4AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-7","04H07","风机压差","空调机组-风机压差",{"$f":"VLOOKUP(AH36,List!$B$3:$D$445,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,List!$K$2:$M$447,2,FALSE)","v":"AHU04H07_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B26*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LAHU04H07_FPS AT%I193.3 :BOOL; (*空调机组NJ-4AP(KT)8-7-风机压差*)"},"LAHU04H07_FPS           AT%I193.3      :BOOL; (*空调机组NJ-4AP(KT)8-7-风机压差*)",null,"L26\\L26AHU04H07_FPS","空调机组NJ-4AP(KT)8-7-风机压差",11547]
[{"$nulls":5},13,null,25,26,"照明控制箱NJ-4AL8-1-运行状态",{"$nulls":16},"NJ-4AL8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL8-1","04H01","运行状态","照明控制箱-运行状态",{"$f":"VLOOKUP(AH37,List!$B$3:$D$445,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,List!$K$2:$M$447,2,FALSE)","v":"LCB04H01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B26*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":"LLCB04H01_R AT%I193.4 :BOOL; (*照明控制箱NJ-4AL8-1-运行状态*)"},"LLCB04H01_R             AT%I193.4      :BOOL; (*照明控制箱NJ-4AL8-1-运行状态*)",null,"L26\\L26LCB04H01_R","照明控制箱NJ-4AL8-1-运行状态",11548]
[{"$nulls":5},14,null,27,28,"照明控制箱NJ-4AL8-1-自动状态",{"$nulls":16},"NJ-4AL8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL8-1","04H01","自动状态","照明控制箱-自动状态",{"$f":"VLOOKUP(AH38,List!$B$3:$D$445,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,List!$K$2:$M$447,2,FALSE)","v":"LCB04H01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%I\"&B26*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":"LLCB04H01_A AT%I193.5 :BOOL; (*照明控制箱NJ-4AL8-1-自动状态*)"},"LLCB04H01_A             AT%I193.5      :BOOL; (*照明控制箱NJ-4AL8-1-自动状态*)",null,"L26\\L26LCB04H01_A","照明控制箱NJ-4AL8-1-自动状态",11549]
[{"$nulls":5},15,null,29,30,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL39,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH39,List!$B$3:$D$445,2,FALSE)&AJ39&\"_\"&VLOOKUP(AK39,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM39&\" \"&\"AT%I\"&B26*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J39&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",11550]
[".",{"$nulls":4},16,null,31,32,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL40,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH40,List!$B$3:$D$445,2,FALSE)&AJ40&\"_\"&VLOOKUP(AK40,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM40&\" \"&\"AT%I\"&B26*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J40&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN40,SEARCH(\"AT%\",AN40),,REPT(\" \",30-SEARCH(\"AT%\",AN40))),SEARCH(\":\",REPLACE(AN40,SEARCH(\"AT%\",AN40),,REPT(\" \",30-SEARCH(\"AT%\",AN40)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN40,SEARCH(\"AT%\",AN40),,REPT(\" \",25-SEARCH(\"AT%\",AN40)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",11551]
[null,"IOM.1601R",{"$nulls":38},{"$f":"\"(* \"&B46&\"地址: \"&B43&\" *)\"","v":"(* IOM 1601R地址: 13 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH42&AA42&\"-\"&AK42","v":"排风机NJ-4AP(KT)8-1-运行状态"},{"$nulls":16},{"$f":"IF(AI42=\"\",\"\",AI42)","v":"NJ-4AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL42,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-1","04H01","运行状态",{"$f":"AH42&\"-\"&AK42","v":"排风机-运行状态"},{"$f":"VLOOKUP(AH42,List!$B$3:$D$445,2,FALSE)&AJ42&\"_\"&VLOOKUP(AK42,List!$K$2:$M$447,2,FALSE)","v":"EAF04H01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM42&\" \"&\"AT%I\"&B43*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J42&\"*)\",\" \")","v":"LEAF04H01_R AT%I208.0 :BOOL; (*排风机NJ-4AP(KT)8-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42))),SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN42,SEARCH(\"AT%\",AN42),,REPT(\" \",25-SEARCH(\"AT%\",AN42)))))),\" \")","v":"LEAF04H01_R             AT%I208.0      :BOOL; (*排风机NJ-4AP(KT)8-1-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM42","v":"L26\\L26EAF04H01_R"},{"$f":"J42","v":"排风机NJ-4AP(KT)8-1-运行状态"},{"$f":"10000+($B43*16*8+F42-1)","v":11664}]
[null,13,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),4,1))","v":0},2,null,3,4,"排风机NJ-4AP(KT)8-1-故障状态",{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-4AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-1","04H01","故障状态",{"$f":"AH43&\"-\"&AK43","v":"排风机-故障状态"},{"$f":"VLOOKUP(AH43,List!$B$3:$D$445,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,List!$K$2:$M$447,2,FALSE)","v":"EAF04H01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%I\"&B43*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LEAF04H01_F AT%I208.1 :BOOL; (*排风机NJ-4AP(KT)8-1-故障状态*)"},"LEAF04H01_F             AT%I208.1      :BOOL; (*排风机NJ-4AP(KT)8-1-故障状态*)",null,"L26\\L26EAF04H01_F",{"$f":"J43","v":"排风机NJ-4AP(KT)8-1-故障状态"},{"$f":"AS42+1","v":11665}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),3,1))","v":1},3,null,5,6,"排风机NJ-4AP(KT)8-1-自动状态",{"$nulls":16},"NJ-4AP(KT)8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-1","04H01","自动状态","排风机-自动状态",{"$f":"VLOOKUP(AH44,List!$B$3:$D$445,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,List!$K$2:$M$447,2,FALSE)","v":"EAF04H01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%I\"&B43*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LEAF04H01_A AT%I208.2 :BOOL; (*排风机NJ-4AP(KT)8-1-自动状态*)"},"LEAF04H01_A             AT%I208.2      :BOOL; (*排风机NJ-4AP(KT)8-1-自动状态*)",null,"L26\\L26EAF04H01_A","排风机NJ-4AP(KT)8-1-自动状态",{"$f":"AS43+1","v":11666}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),2,1))","v":1},4,null,7,8,"排风机NJ-4AP(KT)8-2-运行状态",{"$nulls":16},"NJ-4AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-2","04H02","运行状态","排风机-运行状态",{"$f":"VLOOKUP(AH45,List!$B$3:$D$445,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,List!$K$2:$M$447,2,FALSE)","v":"EAF04H02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%I\"&B43*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":"LEAF04H02_R AT%I208.3 :BOOL; (*排风机NJ-4AP(KT)8-2-运行状态*)"},"LEAF04H02_R             AT%I208.3      :BOOL; (*排风机NJ-4AP(KT)8-2-运行状态*)",null,"L26\\L26EAF04H02_R","排风机NJ-4AP(KT)8-2-运行状态",11667]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B43),REPT(0,5))),1,1))","v":0},5,null,9,10,"排风机NJ-4AP(KT)8-2-故障状态",{"$nulls":16},"NJ-4AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-2","04H02","故障状态","排风机-故障状态",{"$f":"VLOOKUP(AH46,List!$B$3:$D$445,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,List!$K$2:$M$447,2,FALSE)","v":"EAF04H02_F"},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%I\"&B43*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":"LEAF04H02_F AT%I208.4 :BOOL; (*排风机NJ-4AP(KT)8-2-故障状态*)"},"LEAF04H02_F             AT%I208.4      :BOOL; (*排风机NJ-4AP(KT)8-2-故障状态*)",null,"L26\\L26EAF04H02_F","排风机NJ-4AP(KT)8-2-故障状态",11668]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,11,12,"排风机NJ-4AP(KT)8-2-自动状态",{"$nulls":16},"NJ-4AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL47,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-2","04H02","自动状态","排风机-自动状态",{"$f":"VLOOKUP(AH47,List!$B$3:$D$445,2,FALSE)&AJ47&\"_\"&VLOOKUP(AK47,List!$K$2:$M$447,2,FALSE)","v":"EAF04H02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM47&\" \"&\"AT%I\"&B43*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J47&\"*)\",\" \")","v":"LEAF04H02_A AT%I208.5 :BOOL; (*排风机NJ-4AP(KT)8-2-自动状态*)"},"LEAF04H02_A             AT%I208.5      :BOOL; (*排风机NJ-4AP(KT)8-2-自动状态*)",null,"L26\\L26EAF04H02_A","排风机NJ-4AP(KT)8-2-自动状态",11669]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,13,14,"排风机NJ-4AP(KT)8-3-运行状态",{"$nulls":16},"NJ-4AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL48,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-3","04H03","运行状态","排风机-运行状态",{"$f":"VLOOKUP(AH48,List!$B$3:$D$445,2,FALSE)&AJ48&\"_\"&VLOOKUP(AK48,List!$K$2:$M$447,2,FALSE)","v":"EAF04H03_R"},{"$f":"_xlfn.IFNA(\"L\"&AM48&\" \"&\"AT%I\"&B43*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J48&\"*)\",\" \")","v":"LEAF04H03_R AT%I208.6 :BOOL; (*排风机NJ-4AP(KT)8-3-运行状态*)"},"LEAF04H03_R             AT%I208.6      :BOOL; (*排风机NJ-4AP(KT)8-3-运行状态*)",null,"L26\\L26EAF04H03_R","排风机NJ-4AP(KT)8-3-运行状态",11670]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B45=20,1,IF(B45=50,10,IF(B45=125,11,IF(B45=250,100,IF(B45=500,101,IF(B45=800,110,IF(B45=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,15,16,"排风机NJ-4AP(KT)8-3-故障状态",{"$nulls":16},{"$f":"IF(AI49=\"\",\"\",AI49)","v":"NJ-4AP(KT)8-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL49,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-3","04H03","故障状态","排风机-故障状态",{"$f":"VLOOKUP(AH49,List!$B$3:$D$445,2,FALSE)&AJ49&\"_\"&VLOOKUP(AK49,List!$K$2:$M$447,2,FALSE)","v":"EAF04H03_F"},{"$f":"_xlfn.IFNA(\"L\"&AM49&\" \"&\"AT%I\"&B43*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J49&\"*)\",\" \")","v":"LEAF04H03_F AT%I208.7 :BOOL; (*排风机NJ-4AP(KT)8-3-故障状态*)"},"LEAF04H03_F             AT%I208.7      :BOOL; (*排风机NJ-4AP(KT)8-3-故障状态*)",null,"L26\\L26EAF04H03_F","排风机NJ-4AP(KT)8-3-故障状态",11671]
[{"$nulls":5},9,null,17,18,"排风机NJ-4AP(KT)8-3-自动状态",{"$nulls":16},"NJ-4AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL50,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-3","04H03","自动状态","排风机-自动状态",{"$f":"VLOOKUP(AH50,List!$B$3:$D$445,2,FALSE)&AJ50&\"_\"&VLOOKUP(AK50,List!$K$2:$M$447,2,FALSE)","v":"EAF04H03_A"},{"$f":"_xlfn.IFNA(\"L\"&AM50&\" \"&\"AT%I\"&B43*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J50&\"*)\",\" \")","v":"LEAF04H03_A AT%I209.0 :BOOL; (*排风机NJ-4AP(KT)8-3-自动状态*)"},"LEAF04H03_A             AT%I209.0      :BOOL; (*排风机NJ-4AP(KT)8-3-自动状态*)",null,"L26\\L26EAF04H03_A","排风机NJ-4AP(KT)8-3-自动状态",11672]
[{"$nulls":5},10,null,19,20,"排风机NJ-4AP(KT)8-4-运行状态",{"$nulls":16},{"$f":"IF(AI51=\"\",\"\",AI51)","v":"NJ-4AP(KT)8-4"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL51,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-4","04H04","运行状态",{"$f":"AH51&\"-\"&AK51","v":"排风机-运行状态"},{"$f":"VLOOKUP(AH51,List!$B$3:$D$445,2,FALSE)&AJ51&\"_\"&VLOOKUP(AK51,List!$K$2:$M$447,2,FALSE)","v":"EAF04H04_R"},{"$f":"_xlfn.IFNA(\"L\"&AM51&\" \"&\"AT%I\"&B43*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J51&\"*)\",\" \")","v":"LEAF04H04_R AT%I209.1 :BOOL; (*排风机NJ-4AP(KT)8-4-运行状态*)"},"LEAF04H04_R             AT%I209.1      :BOOL; (*排风机NJ-4AP(KT)8-4-运行状态*)",null,"L26\\L26EAF04H04_R",{"$f":"J51","v":"排风机NJ-4AP(KT)8-4-运行状态"},11673]
[{"$nulls":5},11,null,21,22,"排风机NJ-4AP(KT)8-4-故障状态",{"$nulls":16},"NJ-4AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL52,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-4","04H04","故障状态","排风机-故障状态",{"$f":"VLOOKUP(AH52,List!$B$3:$D$445,2,FALSE)&AJ52&\"_\"&VLOOKUP(AK52,List!$K$2:$M$447,2,FALSE)","v":"EAF04H04_F"},{"$f":"_xlfn.IFNA(\"L\"&AM52&\" \"&\"AT%I\"&B43*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J52&\"*)\",\" \")","v":"LEAF04H04_F AT%I209.2 :BOOL; (*排风机NJ-4AP(KT)8-4-故障状态*)"},"LEAF04H04_F             AT%I209.2      :BOOL; (*排风机NJ-4AP(KT)8-4-故障状态*)",null,"L26\\L26EAF04H04_F","排风机NJ-4AP(KT)8-4-故障状态",11674]
[{"$nulls":5},12,null,23,24,"排风机NJ-4AP(KT)8-4-自动状态",{"$nulls":16},"NJ-4AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL53,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-4","04H04","自动状态","排风机-自动状态",{"$f":"VLOOKUP(AH53,List!$B$3:$D$445,2,FALSE)&AJ53&\"_\"&VLOOKUP(AK53,List!$K$2:$M$447,2,FALSE)","v":"EAF04H04_A"},{"$f":"_xlfn.IFNA(\"L\"&AM53&\" \"&\"AT%I\"&B43*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J53&\"*)\",\" \")","v":"LEAF04H04_A AT%I209.3 :BOOL; (*排风机NJ-4AP(KT)8-4-自动状态*)"},"LEAF04H04_A             AT%I209.3      :BOOL; (*排风机NJ-4AP(KT)8-4-自动状态*)",null,"L26\\L26EAF04H04_A","排风机NJ-4AP(KT)8-4-自动状态",11675]
[{"$nulls":5},13,null,25,26,"排风机NJ-4AP(KT)8-5-运行状态",{"$nulls":16},"NJ-4AP(KT)8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL54,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-5","04H05","运行状态","排风机-运行状态",{"$f":"VLOOKUP(AH54,List!$B$3:$D$445,2,FALSE)&AJ54&\"_\"&VLOOKUP(AK54,List!$K$2:$M$447,2,FALSE)","v":"EAF04H05_R"},{"$f":"_xlfn.IFNA(\"L\"&AM54&\" \"&\"AT%I\"&B43*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J54&\"*)\",\" \")","v":"LEAF04H05_R AT%I209.4 :BOOL; (*排风机NJ-4AP(KT)8-5-运行状态*)"},"LEAF04H05_R             AT%I209.4      :BOOL; (*排风机NJ-4AP(KT)8-5-运行状态*)",null,"L26\\L26EAF04H05_R","排风机NJ-4AP(KT)8-5-运行状态",11676]
[{"$nulls":5},14,null,27,28,"排风机NJ-4AP(KT)8-5-故障状态",{"$nulls":16},"NJ-4AP(KT)8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL55,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-5","04H05","故障状态","排风机-故障状态",{"$f":"VLOOKUP(AH55,List!$B$3:$D$445,2,FALSE)&AJ55&\"_\"&VLOOKUP(AK55,List!$K$2:$M$447,2,FALSE)","v":"EAF04H05_F"},{"$f":"_xlfn.IFNA(\"L\"&AM55&\" \"&\"AT%I\"&B43*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J55&\"*)\",\" \")","v":"LEAF04H05_F AT%I209.5 :BOOL; (*排风机NJ-4AP(KT)8-5-故障状态*)"},"LEAF04H05_F             AT%I209.5      :BOOL; (*排风机NJ-4AP(KT)8-5-故障状态*)",null,"L26\\L26EAF04H05_F","排风机NJ-4AP(KT)8-5-故障状态",11677]
[{"$nulls":5},15,null,29,30,"排风机NJ-4AP(KT)8-5-自动状态",{"$nulls":16},"NJ-4AP(KT)8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL56,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-5","04H05","自动状态","排风机-自动状态",{"$f":"VLOOKUP(AH56,List!$B$3:$D$445,2,FALSE)&AJ56&\"_\"&VLOOKUP(AK56,List!$K$2:$M$447,2,FALSE)","v":"EAF04H05_A"},{"$f":"_xlfn.IFNA(\"L\"&AM56&\" \"&\"AT%I\"&B43*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J56&\"*)\",\" \")","v":"LEAF04H05_A AT%I209.6 :BOOL; (*排风机NJ-4AP(KT)8-5-自动状态*)"},"LEAF04H05_A             AT%I209.6      :BOOL; (*排风机NJ-4AP(KT)8-5-自动状态*)",null,"L26\\L26EAF04H05_A","排风机NJ-4AP(KT)8-5-自动状态",11678]
[".",{"$nulls":4},16,null,31,32,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL57,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH57,List!$B$3:$D$445,2,FALSE)&AJ57&\"_\"&VLOOKUP(AK57,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM57&\" \"&\"AT%I\"&B43*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J57&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN57,SEARCH(\"AT%\",AN57),,REPT(\" \",30-SEARCH(\"AT%\",AN57))),SEARCH(\":\",REPLACE(AN57,SEARCH(\"AT%\",AN57),,REPT(\" \",30-SEARCH(\"AT%\",AN57)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN57,SEARCH(\"AT%\",AN57),,REPT(\" \",25-SEARCH(\"AT%\",AN57)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",11679]
[null,"IOM.0801R",{"$nulls":38},{"$f":"\"(* \"&B63&\"地址: \"&B60&\" *)\"","v":"(* IOM 0801R 地址: 14 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH59&AA59&\"-\"&AK59","v":"风机盘管NJ-4AP(KT)8-1-运行状态"},{"$nulls":16},{"$f":"IF(AI59=\"\",\"\",AI59)","v":"NJ-4AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL59,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)8-1","04H01","运行状态",{"$f":"AH59&\"-\"&AK59","v":"风机盘管-运行状态"},{"$f":"VLOOKUP(AH59,List!$B$3:$D$445,2,FALSE)&AJ59&\"_\"&VLOOKUP(AK59,List!$K$2:$M$447,2,FALSE)","v":"FCU04H01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM59&\" \"&\"AT%I\"&B60*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J59&\"*)\",\" \")","v":"LFCU04H01_R AT%I224.0 :BOOL; (*风机盘管NJ-4AP(KT)8-1-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59))),SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN59,SEARCH(\"AT%\",AN59),,REPT(\" \",25-SEARCH(\"AT%\",AN59)))))),\" \")","v":"LFCU04H01_R             AT%I224.0      :BOOL; (*风机盘管NJ-4AP(KT)8-1-运行状态*)"},null,{"$f":"AM59","v":"FCU04H01_R"},{"$f":"J59","v":"风机盘管NJ-4AP(KT)8-1-运行状态"},{"$f":"10000+($B60*16*8+F59-1)","v":11792}]
[null,14,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),4,1))","v":1},2,null,2,"C",{"$f":"AH60&AA60&\"-\"&AK60","v":"风机盘管NJ-4AP(KT)8-1-自动状态"},{"$nulls":16},{"$f":"IF(AI60=\"\",\"\",AI60)","v":"NJ-4AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL60,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)8-1","04H01","自动状态",{"$f":"AH60&\"-\"&AK60","v":"风机盘管-自动状态"},{"$f":"VLOOKUP(AH60,List!$B$3:$D$445,2,FALSE)&AJ60&\"_\"&VLOOKUP(AK60,List!$K$2:$M$447,2,FALSE)","v":"FCU04H01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM60&\" \"&\"AT%I\"&B60*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J60&\"*)\",\" \")","v":"LFCU04H01_A AT%I224.1 :BOOL; (*风机盘管NJ-4AP(KT)8-1-自动状态*)"},"LFCU04H01_A             AT%I224.1      :BOOL; (*风机盘管NJ-4AP(KT)8-1-自动状态*)",null,{"$f":"AM60","v":"FCU04H01_A"},{"$f":"J60","v":"风机盘管NJ-4AP(KT)8-1-自动状态"},{"$f":"AS59+1","v":11793}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),3,1))","v":1},3,null,3,"C",{"$f":"AH61&AA61&\"-\"&AK61","v":"风机盘管NJ-4AP(KT)8-1-电磁阀开启状态"},{"$nulls":16},"NJ-4AP(KT)8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL61,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)8-1","04H01","电磁阀开启状态","风机盘管-电磁阀开启状态",{"$f":"VLOOKUP(AH61,List!$B$3:$D$445,2,FALSE)&AJ61&\"_\"&VLOOKUP(AK61,List!$K$2:$M$447,2,FALSE)","v":"FCU04H01_EVR"},{"$f":"_xlfn.IFNA(\"L\"&AM61&\" \"&\"AT%I\"&B60*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J61&\"*)\",\" \")","v":"LFCU04H01_EVR AT%I224.2 :BOOL; (*风机盘管NJ-4AP(KT)8-1-电磁阀开启状态*)"},"LFCU04H01_EVR           AT%I224.2      :BOOL; (*风机盘管NJ-4AP(KT)8-1-电磁阀开启状态*)",null,"FCU04H01_EVR","风机盘管NJ-4AP(KT)8-1-电磁阀开启状态",{"$f":"AS60+1","v":11794}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),2,1))","v":1},4,null,4,"C",{"$f":"AH62&AA62&\"-\"&AK62","v":"风机盘管NJ-4AP(KT)8-1-电磁阀自动状态"},{"$nulls":16},"NJ-4AP(KT)8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL62,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)8-1","04H01","电磁阀自动状态","风机盘管-电磁阀自动状态",{"$f":"VLOOKUP(AH62,List!$B$3:$D$445,2,FALSE)&AJ62&\"_\"&VLOOKUP(AK62,List!$K$2:$M$447,2,FALSE)","v":"FCU04H01_EVA"},{"$f":"_xlfn.IFNA(\"L\"&AM62&\" \"&\"AT%I\"&B60*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J62&\"*)\",\" \")","v":"LFCU04H01_EVA AT%I224.3 :BOOL; (*风机盘管NJ-4AP(KT)8-1-电磁阀自动状态*)"},"LFCU04H01_EVA           AT%I224.3      :BOOL; (*风机盘管NJ-4AP(KT)8-1-电磁阀自动状态*)",null,"FCU04H01_EVA","风机盘管NJ-4AP(KT)8-1-电磁阀自动状态",11795]
[null,"IOM 0801R ",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B60),REPT(0,5))),1,1))","v":0},5,null,5,"C","遮阳帘-运行状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL63,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04H01","运行状态","遮阳帘-运行状态",{"$f":"VLOOKUP(AH63,List!$B$3:$D$445,2,FALSE)&AJ63&\"_\"&VLOOKUP(AK63,List!$K$2:$M$447,2,FALSE)","v":"SSC04H01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM63&\" \"&\"AT%I\"&B60*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J63&\"*)\",\" \")","v":"LSSC04H01_R AT%I224.4 :BOOL; (*遮阳帘-运行状态*)"},"LSSC04H01_R             AT%I224.4      :BOOL; (*遮阳帘-运行状态*)",null,"SSC04H01_R","遮阳帘-运行状态",11796]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","遮阳帘-自动状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL64,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04H01","自动状态","遮阳帘-自动状态",{"$f":"VLOOKUP(AH64,List!$B$3:$D$445,2,FALSE)&AJ64&\"_\"&VLOOKUP(AK64,List!$K$2:$M$447,2,FALSE)","v":"SSC04H01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM64&\" \"&\"AT%I\"&B60*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J64&\"*)\",\" \")","v":"LSSC04H01_A AT%I224.5 :BOOL; (*遮阳帘-自动状态*)"},"LSSC04H01_A             AT%I224.5      :BOOL; (*遮阳帘-自动状态*)",null,"SSC04H01_A","遮阳帘-自动状态",11797]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","遮阳帘-运行状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL65,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04H02","运行状态","遮阳帘-运行状态",{"$f":"VLOOKUP(AH65,List!$B$3:$D$445,2,FALSE)&AJ65&\"_\"&VLOOKUP(AK65,List!$K$2:$M$447,2,FALSE)","v":"SSC04H02_R"},{"$f":"_xlfn.IFNA(\"L\"&AM65&\" \"&\"AT%I\"&B60*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J65&\"*)\",\" \")","v":"LSSC04H02_R AT%I224.6 :BOOL; (*遮阳帘-运行状态*)"},"LSSC04H02_R             AT%I224.6      :BOOL; (*遮阳帘-运行状态*)",null,"SSC04H02_R","遮阳帘-运行状态",11798]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B62=20,1,IF(B62=50,10,IF(B62=125,11,IF(B62=250,100,IF(B62=500,101,IF(B62=800,110,IF(B62=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","遮阳帘-自动状态",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL66,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04H02","自动状态","遮阳帘-自动状态",{"$f":"VLOOKUP(AH66,List!$B$3:$D$445,2,FALSE)&AJ66&\"_\"&VLOOKUP(AK66,List!$K$2:$M$447,2,FALSE)","v":"SSC04H02_A"},{"$f":"_xlfn.IFNA(\"L\"&AM66&\" \"&\"AT%I\"&B60*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J66&\"*)\",\" \")","v":"LSSC04H02_A AT%I224.7 :BOOL; (*遮阳帘-自动状态*)"},"LSSC04H02_A             AT%I224.7      :BOOL; (*遮阳帘-自动状态*)",null,"SSC04H02_A","遮阳帘-自动状态",11799]
[null,"IOM 1601D",{"$nulls":38},{"$f":"\"(* \"&B72&\"地址: \"&B69&\" *)\"","v":"(* IOM 1601D地址: 15 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH68&AA68&\"-\"&AK68","v":"空调机组NJ-4AP(KT)8-1-启停控制"},{"$nulls":16},{"$f":"IF(AI68=\"\",\"\",AI68)","v":"NJ-4AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL68,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-1","04H01","启停控制",{"$f":"AH68&\"-\"&AK68","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH68,List!$B$3:$D$445,2,FALSE)&AJ68&\"_\"&VLOOKUP(AK68,List!$K$2:$M$447,2,FALSE)","v":"AHU04H01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM68&\" \"&\"AT%Q\"&B69*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J68&\"*)\",\" \")","v":"LAHU04H01_C AT%Q240.0 :BOOL; (*空调机组NJ-4AP(KT)8-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68))),SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN68,SEARCH(\"AT%\",AN68),,REPT(\" \",25-SEARCH(\"AT%\",AN68)))))),\" \")","v":"LAHU04H01_C             AT%Q240.0      :BOOL; (*空调机组NJ-4AP(KT)8-1-启停控制*)"},null,{"$f":"AM68","v":"AHU04H01_C"},{"$f":"J68","v":"空调机组NJ-4AP(KT)8-1-启停控制"},{"$f":"($B69*16*8+F68-1)","v":1920}]
[null,15,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","空调机组NJ-4AP(KT)8-2-启停控制",{"$nulls":16},{"$f":"IF(AI69=\"\",\"\",AI69)","v":"NJ-4AP(KT)8-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL69,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-2","04H02","启停控制",{"$f":"AH69&\"-\"&AK69","v":"空调机组-启停控制"},{"$f":"VLOOKUP(AH69,List!$B$3:$D$445,2,FALSE)&AJ69&\"_\"&VLOOKUP(AK69,List!$K$2:$M$447,2,FALSE)","v":"AHU04H02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM69&\" \"&\"AT%Q\"&B69*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J69&\"*)\",\" \")","v":"LAHU04H02_C AT%Q240.1 :BOOL; (*空调机组NJ-4AP(KT)8-2-启停控制*)"},"LAHU04H02_C             AT%Q240.1      :BOOL; (*空调机组NJ-4AP(KT)8-2-启停控制*)",null,"AHU04H02_C",{"$f":"J69","v":"空调机组NJ-4AP(KT)8-2-启停控制"},{"$f":"AS68+1","v":1921}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","空调机组NJ-4AP(KT)8-3-启停控制",{"$nulls":16},"NJ-4AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL70,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-3","04H03","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH70,List!$B$3:$D$445,2,FALSE)&AJ70&\"_\"&VLOOKUP(AK70,List!$K$2:$M$447,2,FALSE)","v":"AHU04H03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM70&\" \"&\"AT%Q\"&B69*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J70&\"*)\",\" \")","v":"LAHU04H03_C AT%Q240.2 :BOOL; (*空调机组NJ-4AP(KT)8-3-启停控制*)"},"LAHU04H03_C             AT%Q240.2      :BOOL; (*空调机组NJ-4AP(KT)8-3-启停控制*)",null,"AHU04H03_C","空调机组NJ-4AP(KT)8-3-启停控制",{"$f":"AS69+1","v":1922}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","空调机组NJ-4AP(KT)8-4-启停控制",{"$nulls":16},"NJ-4AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL71,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-4","04H04","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH71,List!$B$3:$D$445,2,FALSE)&AJ71&\"_\"&VLOOKUP(AK71,List!$K$2:$M$447,2,FALSE)","v":"AHU04H04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM71&\" \"&\"AT%Q\"&B69*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J71&\"*)\",\" \")","v":"LAHU04H04_C AT%Q240.3 :BOOL; (*空调机组NJ-4AP(KT)8-4-启停控制*)"},"LAHU04H04_C             AT%Q240.3      :BOOL; (*空调机组NJ-4AP(KT)8-4-启停控制*)",null,"AHU04H04_C","空调机组NJ-4AP(KT)8-4-启停控制",1923]
[null,"IOM 1601D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B69),REPT(0,5))),1,1))","v":0},5,null,"5+","5-","空调机组NJ-4AP(KT)8-5-启停控制",{"$nulls":16},"NJ-4AP(KT)8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL72,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-5","04H05","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH72,List!$B$3:$D$445,2,FALSE)&AJ72&\"_\"&VLOOKUP(AK72,List!$K$2:$M$447,2,FALSE)","v":"AHU04H05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM72&\" \"&\"AT%Q\"&B69*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J72&\"*)\",\" \")","v":"LAHU04H05_C AT%Q240.4 :BOOL; (*空调机组NJ-4AP(KT)8-5-启停控制*)"},"LAHU04H05_C             AT%Q240.4      :BOOL; (*空调机组NJ-4AP(KT)8-5-启停控制*)",null,"AHU04H05_C","空调机组NJ-4AP(KT)8-5-启停控制",1924]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","空调机组NJ-4AP(KT)8-6-启停控制",{"$nulls":16},"NJ-4AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL73,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-6","04H06","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH73,List!$B$3:$D$445,2,FALSE)&AJ73&\"_\"&VLOOKUP(AK73,List!$K$2:$M$447,2,FALSE)","v":"AHU04H06_C"},{"$f":"_xlfn.IFNA(\"L\"&AM73&\" \"&\"AT%Q\"&B69*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J73&\"*)\",\" \")","v":"LAHU04H06_C AT%Q240.5 :BOOL; (*空调机组NJ-4AP(KT)8-6-启停控制*)"},"LAHU04H06_C             AT%Q240.5      :BOOL; (*空调机组NJ-4AP(KT)8-6-启停控制*)",null,"AHU04H06_C","空调机组NJ-4AP(KT)8-6-启停控制",1925]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","空调机组NJ-4AP(KT)8-7-启停控制",{"$nulls":16},"NJ-4AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL74,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-7","04H07","启停控制","空调机组-启停控制",{"$f":"VLOOKUP(AH74,List!$B$3:$D$445,2,FALSE)&AJ74&\"_\"&VLOOKUP(AK74,List!$K$2:$M$447,2,FALSE)","v":"AHU04H07_C"},{"$f":"_xlfn.IFNA(\"L\"&AM74&\" \"&\"AT%Q\"&B69*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J74&\"*)\",\" \")","v":"LAHU04H07_C AT%Q240.6 :BOOL; (*空调机组NJ-4AP(KT)8-7-启停控制*)"},"LAHU04H07_C             AT%Q240.6      :BOOL; (*空调机组NJ-4AP(KT)8-7-启停控制*)",null,"AHU04H07_C","空调机组NJ-4AP(KT)8-7-启停控制",1926]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B71=20,1,IF(B71=50,10,IF(B71=125,11,IF(B71=250,100,IF(B71=500,101,IF(B71=800,110,IF(B71=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","照明控制箱NJ-4AL8-1-启停控制",{"$nulls":16},"NJ-4AL8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL75,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},null,"通过",null,null,"照明控制箱","NJ-4AL8-1","04H01","启停控制","照明控制箱-启停控制",{"$f":"VLOOKUP(AH75,List!$B$3:$D$445,2,FALSE)&AJ75&\"_\"&VLOOKUP(AK75,List!$K$2:$M$447,2,FALSE)","v":"LCB04H01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM75&\" \"&\"AT%Q\"&B69*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J75&\"*)\",\" \")","v":"LLCB04H01_C AT%Q240.7 :BOOL; (*照明控制箱NJ-4AL8-1-启停控制*)"},"LLCB04H01_C             AT%Q240.7      :BOOL; (*照明控制箱NJ-4AL8-1-启停控制*)",null,"LCB04H01_C","照明控制箱NJ-4AL8-1-启停控制",1927]
[{"$nulls":5},9,null,"9+","9-","排风机NJ-4AP(KT)8-1-启停控制",{"$nulls":16},"NJ-4AP(KT)8-1",{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL76,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-1","04H01","启停控制","排风机-启停控制",{"$f":"VLOOKUP(AH76,List!$B$3:$D$445,2,FALSE)&AJ76&\"_\"&VLOOKUP(AK76,List!$K$2:$M$447,2,FALSE)","v":"EAF04H01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM76&\" \"&\"AT%Q\"&B69*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J76&\"*)\",\" \")","v":"LEAF04H01_C AT%Q241.0 :BOOL; (*排风机NJ-4AP(KT)8-1-启停控制*)"},"LEAF04H01_C             AT%Q241.0      :BOOL; (*排风机NJ-4AP(KT)8-1-启停控制*)",null,"EAF04H01_C","排风机NJ-4AP(KT)8-1-启停控制",1928]
[{"$nulls":5},10,null,"10+","10-","排风机NJ-4AP(KT)8-2-启停控制",{"$nulls":16},{"$f":"IF(AI77=\"\",\"\",AI77)","v":"NJ-4AP(KT)8-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL77,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-2","04H02","启停控制",{"$f":"AH77&\"-\"&AK77","v":"排风机-启停控制"},{"$f":"VLOOKUP(AH77,List!$B$3:$D$445,2,FALSE)&AJ77&\"_\"&VLOOKUP(AK77,List!$K$2:$M$447,2,FALSE)","v":"EAF04H02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM77&\" \"&\"AT%Q\"&B69*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J77&\"*)\",\" \")","v":"LEAF04H02_C AT%Q241.1 :BOOL; (*排风机NJ-4AP(KT)8-2-启停控制*)"},"LEAF04H02_C             AT%Q241.1      :BOOL; (*排风机NJ-4AP(KT)8-2-启停控制*)",null,"EAF04H02_C",{"$f":"J77","v":"排风机NJ-4AP(KT)8-2-启停控制"},1929]
[{"$nulls":5},11,null,"11+","11-","排风机NJ-4AP(KT)8-3-启停控制",{"$nulls":16},"NJ-4AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL78,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-3","04H03","启停控制","排风机-启停控制",{"$f":"VLOOKUP(AH78,List!$B$3:$D$445,2,FALSE)&AJ78&\"_\"&VLOOKUP(AK78,List!$K$2:$M$447,2,FALSE)","v":"EAF04H03_C"},{"$f":"_xlfn.IFNA(\"L\"&AM78&\" \"&\"AT%Q\"&B69*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J78&\"*)\",\" \")","v":"LEAF04H03_C AT%Q241.2 :BOOL; (*排风机NJ-4AP(KT)8-3-启停控制*)"},"LEAF04H03_C             AT%Q241.2      :BOOL; (*排风机NJ-4AP(KT)8-3-启停控制*)",null,"EAF04H03_C","排风机NJ-4AP(KT)8-3-启停控制",1930]
[{"$nulls":5},12,null,"12+","12-","排风机NJ-4AP(KT)8-4-启停控制",{"$nulls":16},"NJ-4AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL79,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-4","04H04","启停控制","排风机-启停控制",{"$f":"VLOOKUP(AH79,List!$B$3:$D$445,2,FALSE)&AJ79&\"_\"&VLOOKUP(AK79,List!$K$2:$M$447,2,FALSE)","v":"EAF04H04_C"},{"$f":"_xlfn.IFNA(\"L\"&AM79&\" \"&\"AT%Q\"&B69*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J79&\"*)\",\" \")","v":"LEAF04H04_C AT%Q241.3 :BOOL; (*排风机NJ-4AP(KT)8-4-启停控制*)"},"LEAF04H04_C             AT%Q241.3      :BOOL; (*排风机NJ-4AP(KT)8-4-启停控制*)",null,"EAF04H04_C","排风机NJ-4AP(KT)8-4-启停控制",1931]
[{"$nulls":5},13,null,"13+","13-","排风机NJ-4AP(KT)8-5-启停控制",{"$nulls":16},"NJ-4AP(KT)8-5",{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL80,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排风机","NJ-4AP(KT)8-5","04H05","启停控制","排风机-启停控制",{"$f":"VLOOKUP(AH80,List!$B$3:$D$445,2,FALSE)&AJ80&\"_\"&VLOOKUP(AK80,List!$K$2:$M$447,2,FALSE)","v":"EAF04H05_C"},{"$f":"_xlfn.IFNA(\"L\"&AM80&\" \"&\"AT%Q\"&B69*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J80&\"*)\",\" \")","v":"LEAF04H05_C AT%Q241.4 :BOOL; (*排风机NJ-4AP(KT)8-5-启停控制*)"},"LEAF04H05_C             AT%Q241.4      :BOOL; (*排风机NJ-4AP(KT)8-5-启停控制*)",null,"EAF04H05_C","排风机NJ-4AP(KT)8-5-启停控制",1932]
[{"$nulls":5},14,null,"14+","14-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL81,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH81,List!$B$3:$D$445,2,FALSE)&AJ81&\"_\"&VLOOKUP(AK81,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM81&\" \"&\"AT%Q\"&B69*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J81&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1933]
[{"$nulls":5},15,null,"15+","15-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL82,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH82,List!$B$3:$D$445,2,FALSE)&AJ82&\"_\"&VLOOKUP(AK82,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM82&\" \"&\"AT%Q\"&B69*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J82&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1934]
[".",{"$nulls":4},16,null,"16+","16-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL83,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH83,List!$B$3:$D$445,2,FALSE)&AJ83&\"_\"&VLOOKUP(AK83,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM83&\" \"&\"AT%Q\"&B69*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J83&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",1935]
[null,"IOM 0801D",{"$nulls":38},{"$f":"\"(* \"&B89&\"地址: \"&B86&\" *)\"","v":"(* IOM 0801D地址: 16 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),5,1))","v":0},1,null,"1+","1-",{"$f":"AH85&AA85&\"-\"&AK85","v":"风机盘管NJ-4AP(KT)8-1-启停控制"},{"$nulls":16},{"$f":"IF(AI85=\"\",\"\",AI85)","v":"NJ-4AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL85,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)8-1","04H01","启停控制",{"$f":"AH85&\"-\"&AK85","v":"风机盘管-启停控制"},{"$f":"VLOOKUP(AH85,List!$B$3:$D$445,2,FALSE)&AJ85&\"_\"&VLOOKUP(AK85,List!$K$2:$M$447,2,FALSE)","v":"FCU04H01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM85&\" \"&\"AT%Q\"&B86*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J85&\"*)\",\" \")","v":"LFCU04H01_C AT%Q256.0 :BOOL; (*风机盘管NJ-4AP(KT)8-1-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN85,SEARCH(\"AT%\",AN85),,REPT(\" \",25-SEARCH(\"AT%\",AN85))),SEARCH(\":\",REPLACE(AN85,SEARCH(\"AT%\",AN85),,REPT(\" \",25-SEARCH(\"AT%\",AN85)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN85,SEARCH(\"AT%\",AN85),,REPT(\" \",25-SEARCH(\"AT%\",AN85)))))),\" \")","v":"LFCU04H01_C             AT%Q256.0      :BOOL; (*风机盘管NJ-4AP(KT)8-1-启停控制*)"},null,{"$f":"AM85","v":"FCU04H01_C"},{"$f":"J85","v":"风机盘管NJ-4AP(KT)8-1-启停控制"},{"$f":"($B86*16*8+F85-1)","v":2048}]
[null,16,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),4,1))","v":0},2,null,"2+","2-","风机盘管NJ-4AP(KT)8-1-电磁阀开关控制",{"$nulls":16},{"$f":"IF(AI86=\"\",\"\",AI86)","v":"NJ-4AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL86,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管","NJ-4AP(KT)8-1","04H01","电磁阀开关控制",{"$f":"AH86&\"-\"&AK86","v":"风机盘管-电磁阀开关控制"},{"$f":"VLOOKUP(AH86,List!$B$3:$D$445,2,FALSE)&AJ86&\"_\"&VLOOKUP(AK86,List!$K$2:$M$447,2,FALSE)","v":"FCU04H01_EVC"},{"$f":"_xlfn.IFNA(\"L\"&AM86&\" \"&\"AT%Q\"&B86*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J86&\"*)\",\" \")","v":"LFCU04H01_EVC AT%Q256.1 :BOOL; (*风机盘管NJ-4AP(KT)8-1-电磁阀开关控制*)"},"LFCU04H01_EVC           AT%Q256.1      :BOOL; (*风机盘管NJ-4AP(KT)8-1-电磁阀开关控制*)",null,"FCU04H01_EVC",{"$f":"J86","v":"风机盘管NJ-4AP(KT)8-1-电磁阀开关控制"},{"$f":"AS85+1","v":2049}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","遮阳帘-启停控制",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL87,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04H01","启停控制","遮阳帘-启停控制",{"$f":"VLOOKUP(AH87,List!$B$3:$D$445,2,FALSE)&AJ87&\"_\"&VLOOKUP(AK87,List!$K$2:$M$447,2,FALSE)","v":"SSC04H01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM87&\" \"&\"AT%Q\"&B86*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J87&\"*)\",\" \")","v":"LSSC04H01_C AT%Q256.2 :BOOL; (*遮阳帘-启停控制*)"},"LSSC04H01_C             AT%Q256.2      :BOOL; (*遮阳帘-启停控制*)",null,"SSC04H01_C","遮阳帘-启停控制",{"$f":"AS86+1","v":2050}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","遮阳帘-启停控制",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL88,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"遮阳帘",null,"04H02","启停控制","遮阳帘-启停控制",{"$f":"VLOOKUP(AH88,List!$B$3:$D$445,2,FALSE)&AJ88&\"_\"&VLOOKUP(AK88,List!$K$2:$M$447,2,FALSE)","v":"SSC04H02_C"},{"$f":"_xlfn.IFNA(\"L\"&AM88&\" \"&\"AT%Q\"&B86*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J88&\"*)\",\" \")","v":"LSSC04H02_C AT%Q256.3 :BOOL; (*遮阳帘-启停控制*)"},"LSSC04H02_C             AT%Q256.3      :BOOL; (*遮阳帘-启停控制*)",null,"SSC04H02_C","遮阳帘-启停控制",2051]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B86),REPT(0,5))),1,1))","v":1},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL89,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH89,List!$B$3:$D$445,2,FALSE)&AJ89&\"_\"&VLOOKUP(AK89,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM89&\" \"&\"AT%Q\"&B86*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J89&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2052]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL90,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH90,List!$B$3:$D$445,2,FALSE)&AJ90&\"_\"&VLOOKUP(AK90,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM90&\" \"&\"AT%Q\"&B86*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J90&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2053]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL91,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH91,List!$B$3:$D$445,2,FALSE)&AJ91&\"_\"&VLOOKUP(AK91,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM91&\" \"&\"AT%Q\"&B86*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J91&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2054]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B88=20,1,IF(B88=50,10,IF(B88=125,11,IF(B88=250,100,IF(B88=500,101,IF(B88=800,110,IF(B88=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL92,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH92,List!$B$3:$D$445,2,FALSE)&AJ92&\"_\"&VLOOKUP(AK92,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM92&\" \"&\"AT%Q\"&B86*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J92&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2055]
[null,{"$f":"B98","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B98&\"地址: \"&B95&\" *)\"","v":"(* IOM 0801U地址: 17 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH94&AA94&\"-\"&AK94","v":"空调机组NJ-4AP(KT)8-1-回风温度"},{"$nulls":16},{"$f":"IF(AI94=\"\",\"\",AI94)","v":"NJ-4AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL94,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-1","04H01","回风温度",{"$f":"AH94&\"-\"&AK94","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH94,List!$B$3:$D$445,2,FALSE)&AJ94&\"_\"&VLOOKUP(AK94,List!$K$2:$M$447,2,FALSE)","v":"AHU04H01_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM94&\" \"&\"AT%I\"&B95*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J94&\"*)\",\" \")","v":"LAHU04H01_RT AT%I272.0 :INT ; (*空调机组NJ-4AP(KT)8-1-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94))),SEARCH(\":\",REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN94,SEARCH(\"AT%\",AN94),,REPT(\" \",25-SEARCH(\"AT%\",AN94)))))),\" \")","v":"LAHU04H01_RT            AT%I272.0      :INT ; (*空调机组NJ-4AP(KT)8-1-回风温度*)"},null,{"$f":"AM94","v":"AHU04H01_RT"},{"$f":"J94","v":"空调机组NJ-4AP(KT)8-1-回风温度"},{"$f":"30000+($B95*8+F94-1)","v":30136}]
[null,17,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),4,1))","v":0},2,null,2,"0V","空调机组NJ-4AP(KT)8-1-水阀反馈",{"$nulls":16},{"$f":"IF(AI95=\"\",\"\",AI95)","v":"NJ-4AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL95,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-1","04H01","水阀反馈",{"$f":"AH95&\"-\"&AK95","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH95,List!$B$3:$D$445,2,FALSE)&AJ95&\"_\"&VLOOKUP(AK95,List!$K$2:$M$447,2,FALSE)","v":"AHU04H01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM95&\" \"&\"AT%I\"&B95*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J95&\"*)\",\" \")","v":"LAHU04H01_WVB AT%I274.0 :INT ; (*空调机组NJ-4AP(KT)8-1-水阀反馈*)"},"LAHU04H01_WVB           AT%I274.0      :INT ; (*空调机组NJ-4AP(KT)8-1-水阀反馈*)",null,"AHU04H01_WVB",{"$f":"J95","v":"空调机组NJ-4AP(KT)8-1-水阀反馈"},{"$f":"AS94+1","v":30137}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-4AP(KT)8-2-回风温度",{"$nulls":16},"NJ-4AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL96,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-2","04H02","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH96,List!$B$3:$D$445,2,FALSE)&AJ96&\"_\"&VLOOKUP(AK96,List!$K$2:$M$447,2,FALSE)","v":"AHU04H02_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM96&\" \"&\"AT%I\"&B95*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J96&\"*)\",\" \")","v":"LAHU04H02_RT AT%I276.0 :INT ; (*空调机组NJ-4AP(KT)8-2-回风温度*)"},"LAHU04H02_RT            AT%I276.0      :INT ; (*空调机组NJ-4AP(KT)8-2-回风温度*)",null,"AHU04H02_RT","空调机组NJ-4AP(KT)8-2-回风温度",{"$f":"AS95+1","v":30138}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-4AP(KT)8-2-水阀反馈",{"$nulls":16},"NJ-4AP(KT)8-2",{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL97,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-2","04H02","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH97,List!$B$3:$D$445,2,FALSE)&AJ97&\"_\"&VLOOKUP(AK97,List!$K$2:$M$447,2,FALSE)","v":"AHU04H02_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM97&\" \"&\"AT%I\"&B95*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J97&\"*)\",\" \")","v":"LAHU04H02_WVB AT%I278.0 :INT ; (*空调机组NJ-4AP(KT)8-2-水阀反馈*)"},"LAHU04H02_WVB           AT%I278.0      :INT ; (*空调机组NJ-4AP(KT)8-2-水阀反馈*)",null,"AHU04H02_WVB","空调机组NJ-4AP(KT)8-2-水阀反馈",30139]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B95),REPT(0,5))),1,1))","v":1},5,null,5,"0V","空调机组NJ-4AP(KT)8-3-回风温度",{"$nulls":16},"NJ-4AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL98,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-3","04H03","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH98,List!$B$3:$D$445,2,FALSE)&AJ98&\"_\"&VLOOKUP(AK98,List!$K$2:$M$447,2,FALSE)","v":"AHU04H03_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM98&\" \"&\"AT%I\"&B95*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J98&\"*)\",\" \")","v":"LAHU04H03_RT AT%I280.0 :INT ; (*空调机组NJ-4AP(KT)8-3-回风温度*)"},"LAHU04H03_RT            AT%I280.0      :INT ; (*空调机组NJ-4AP(KT)8-3-回风温度*)",null,"AHU04H03_RT","空调机组NJ-4AP(KT)8-3-回风温度",30140]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-4AP(KT)8-3-水阀反馈",{"$nulls":16},{"$f":"IF(AI99=\"\",\"\",AI99)","v":"NJ-4AP(KT)8-3"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL99,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-3","04H03","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH99,List!$B$3:$D$445,2,FALSE)&AJ99&\"_\"&VLOOKUP(AK99,List!$K$2:$M$447,2,FALSE)","v":"AHU04H03_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM99&\" \"&\"AT%I\"&B95*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J99&\"*)\",\" \")","v":"LAHU04H03_WVB AT%I282.0 :INT ; (*空调机组NJ-4AP(KT)8-3-水阀反馈*)"},"LAHU04H03_WVB           AT%I282.0      :INT ; (*空调机组NJ-4AP(KT)8-3-水阀反馈*)",null,"AHU04H03_WVB",{"$f":"J99","v":"空调机组NJ-4AP(KT)8-3-水阀反馈"},30141]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","空调机组NJ-4AP(KT)8-4-回风温度",{"$nulls":16},"NJ-4AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL100,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-4","04H04","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH100,List!$B$3:$D$445,2,FALSE)&AJ100&\"_\"&VLOOKUP(AK100,List!$K$2:$M$447,2,FALSE)","v":"AHU04H04_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM100&\" \"&\"AT%I\"&B95*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J100&\"*)\",\" \")","v":"LAHU04H04_RT AT%I284.0 :INT ; (*空调机组NJ-4AP(KT)8-4-回风温度*)"},"LAHU04H04_RT            AT%I284.0      :INT ; (*空调机组NJ-4AP(KT)8-4-回风温度*)",null,"AHU04H04_RT","空调机组NJ-4AP(KT)8-4-回风温度",30142]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B97=20,1,IF(B97=50,10,IF(B97=125,11,IF(B97=250,100,IF(B97=500,101,IF(B97=800,110,IF(B97=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","空调机组NJ-4AP(KT)8-4-水阀反馈",{"$nulls":16},"NJ-4AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL101,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-4","04H04","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH101,List!$B$3:$D$445,2,FALSE)&AJ101&\"_\"&VLOOKUP(AK101,List!$K$2:$M$447,2,FALSE)","v":"AHU04H04_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM101&\" \"&\"AT%I\"&B95*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J101&\"*)\",\" \")","v":"LAHU04H04_WVB AT%I286.0 :INT ; (*空调机组NJ-4AP(KT)8-4-水阀反馈*)"},"LAHU04H04_WVB           AT%I286.0      :INT ; (*空调机组NJ-4AP(KT)8-4-水阀反馈*)",null,"AHU04H04_WVB","空调机组NJ-4AP(KT)8-4-水阀反馈",30143]
[null,{"$f":"B107","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B107&\"地址: \"&B104&\" *)\"","v":"(* IOM 0801U地址: 18 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH103&AA103&\"-\"&AK103","v":"空调机组NJ-4AP(KT)8-5-回风温度"},{"$nulls":16},{"$f":"IF(AI103=\"\",\"\",AI103)","v":"NJ-4AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL103,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-5","04H05","回风温度",{"$f":"AH103&\"-\"&AK103","v":"空调机组-回风温度"},{"$f":"VLOOKUP(AH103,List!$B$3:$D$445,2,FALSE)&AJ103&\"_\"&VLOOKUP(AK103,List!$K$2:$M$447,2,FALSE)","v":"AHU04H05_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM103&\" \"&\"AT%I\"&B104*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J103&\"*)\",\" \")","v":"LAHU04H05_RT AT%I288.0 :INT ; (*空调机组NJ-4AP(KT)8-5-回风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103))),SEARCH(\":\",REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN103,SEARCH(\"AT%\",AN103),,REPT(\" \",25-SEARCH(\"AT%\",AN103)))))),\" \")","v":"LAHU04H05_RT            AT%I288.0      :INT ; (*空调机组NJ-4AP(KT)8-5-回风温度*)"},null,{"$f":"AM103","v":"AHU04H05_RT"},{"$f":"J103","v":"空调机组NJ-4AP(KT)8-5-回风温度"},{"$f":"30000+($B104*8+F103-1)","v":30144}]
[null,18,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),4,1))","v":1},2,null,2,"0V","空调机组NJ-4AP(KT)8-5-水阀反馈",{"$nulls":16},{"$f":"IF(AI104=\"\",\"\",AI104)","v":"NJ-4AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL104,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-5","04H05","水阀反馈",{"$f":"AH104&\"-\"&AK104","v":"空调机组-水阀反馈"},{"$f":"VLOOKUP(AH104,List!$B$3:$D$445,2,FALSE)&AJ104&\"_\"&VLOOKUP(AK104,List!$K$2:$M$447,2,FALSE)","v":"AHU04H05_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM104&\" \"&\"AT%I\"&B104*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J104&\"*)\",\" \")","v":"LAHU04H05_WVB AT%I290.0 :INT ; (*空调机组NJ-4AP(KT)8-5-水阀反馈*)"},"LAHU04H05_WVB           AT%I290.0      :INT ; (*空调机组NJ-4AP(KT)8-5-水阀反馈*)",null,"AHU04H05_WVB",{"$f":"J104","v":"空调机组NJ-4AP(KT)8-5-水阀反馈"},{"$f":"AS103+1","v":30145}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),3,1))","v":0},3,null,3,"0V","空调机组NJ-4AP(KT)8-6-回风温度",{"$nulls":16},"NJ-4AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL105,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-6","04H06","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH105,List!$B$3:$D$445,2,FALSE)&AJ105&\"_\"&VLOOKUP(AK105,List!$K$2:$M$447,2,FALSE)","v":"AHU04H06_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM105&\" \"&\"AT%I\"&B104*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J105&\"*)\",\" \")","v":"LAHU04H06_RT AT%I292.0 :INT ; (*空调机组NJ-4AP(KT)8-6-回风温度*)"},"LAHU04H06_RT            AT%I292.0      :INT ; (*空调机组NJ-4AP(KT)8-6-回风温度*)",null,"AHU04H06_RT","空调机组NJ-4AP(KT)8-6-回风温度",{"$f":"AS104+1","v":30146}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),2,1))","v":0},4,null,4,"0V","空调机组NJ-4AP(KT)8-6-水阀反馈",{"$nulls":16},"NJ-4AP(KT)8-6",{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL106,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-6","04H06","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH106,List!$B$3:$D$445,2,FALSE)&AJ106&\"_\"&VLOOKUP(AK106,List!$K$2:$M$447,2,FALSE)","v":"AHU04H06_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM106&\" \"&\"AT%I\"&B104*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J106&\"*)\",\" \")","v":"LAHU04H06_WVB AT%I294.0 :INT ; (*空调机组NJ-4AP(KT)8-6-水阀反馈*)"},"LAHU04H06_WVB           AT%I294.0      :INT ; (*空调机组NJ-4AP(KT)8-6-水阀反馈*)",null,"AHU04H06_WVB","空调机组NJ-4AP(KT)8-6-水阀反馈",30147]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B104),REPT(0,5))),1,1))","v":1},5,null,5,"0V","空调机组NJ-4AP(KT)8-7-回风温度",{"$nulls":16},"NJ-4AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL107,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-7","04H07","回风温度","空调机组-回风温度",{"$f":"VLOOKUP(AH107,List!$B$3:$D$445,2,FALSE)&AJ107&\"_\"&VLOOKUP(AK107,List!$K$2:$M$447,2,FALSE)","v":"AHU04H07_RT"},{"$f":"_xlfn.IFNA(\"L\"&AM107&\" \"&\"AT%I\"&B104*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J107&\"*)\",\" \")","v":"LAHU04H07_RT AT%I296.0 :INT ; (*空调机组NJ-4AP(KT)8-7-回风温度*)"},"LAHU04H07_RT            AT%I296.0      :INT ; (*空调机组NJ-4AP(KT)8-7-回风温度*)",null,"AHU04H07_RT","空调机组NJ-4AP(KT)8-7-回风温度",30148]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","空调机组NJ-4AP(KT)8-7-水阀反馈",{"$nulls":16},{"$f":"IF(AI108=\"\",\"\",AI108)","v":"NJ-4AP(KT)8-7"},{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL108,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-7","04H07","水阀反馈","空调机组-水阀反馈",{"$f":"VLOOKUP(AH108,List!$B$3:$D$445,2,FALSE)&AJ108&\"_\"&VLOOKUP(AK108,List!$K$2:$M$447,2,FALSE)","v":"AHU04H07_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM108&\" \"&\"AT%I\"&B104*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J108&\"*)\",\" \")","v":"LAHU04H07_WVB AT%I298.0 :INT ; (*空调机组NJ-4AP(KT)8-7-水阀反馈*)"},"LAHU04H07_WVB           AT%I298.0      :INT ; (*空调机组NJ-4AP(KT)8-7-水阀反馈*)",null,"AHU04H07_WVB",{"$f":"J108","v":"空调机组NJ-4AP(KT)8-7-水阀反馈"},30149]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","室内环境状态T-10-温度状态",{"$nulls":16},"T-10",{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL109,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","T-10","04H01","温度状态","室内环境状态-温度状态",{"$f":"VLOOKUP(AH109,List!$B$3:$D$445,2,FALSE)&AJ109&\"_\"&VLOOKUP(AK109,List!$K$2:$M$447,2,FALSE)","v":"IES04H01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM109&\" \"&\"AT%I\"&B104*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J109&\"*)\",\" \")","v":"LIES04H01_T AT%I300.0 :INT ; (*室内环境状态T-10-温度状态*)"},"LIES04H01_T             AT%I300.0      :INT ; (*室内环境状态T-10-温度状态*)",null,"IES04H01_T","室内环境状态T-10-温度状态",30150]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B106=20,1,IF(B106=50,10,IF(B106=125,11,IF(B106=250,100,IF(B106=500,101,IF(B106=800,110,IF(B106=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","室内环境状态T-11-温度状态",{"$nulls":16},"T-11",{"$f":"_xlfn.IFNA(VLOOKUP(AL110,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL110,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","T-11","04H02","温度状态","室内环境状态-温度状态",{"$f":"VLOOKUP(AH110,List!$B$3:$D$445,2,FALSE)&AJ110&\"_\"&VLOOKUP(AK110,List!$K$2:$M$447,2,FALSE)","v":"IES04H02_T"},{"$f":"_xlfn.IFNA(\"L\"&AM110&\" \"&\"AT%I\"&B104*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J110&\"*)\",\" \")","v":"LIES04H02_T AT%I302.0 :INT ; (*室内环境状态T-11-温度状态*)"},"LIES04H02_T             AT%I302.0      :INT ; (*室内环境状态T-11-温度状态*)",null,"IES04H02_T","室内环境状态T-11-温度状态",30151]
[null,{"$f":"B116","v":"IOM 0801U"},{"$nulls":38},{"$f":"\"(* \"&B116&\"地址: \"&B113&\" *)\"","v":"(* IOM 0801U地址: 19 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),5,1))","v":1},1,null,1,"0V",{"$f":"AH112&AA112&\"-\"&AK112","v":"室内环境状态T-12-温度状态"},{"$nulls":16},{"$f":"IF(AI112=\"\",\"\",AI112)","v":"T-12"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL112,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","T-12","04H03","温度状态",{"$f":"AH112&\"-\"&AK112","v":"室内环境状态-温度状态"},{"$f":"VLOOKUP(AH112,List!$B$3:$D$445,2,FALSE)&AJ112&\"_\"&VLOOKUP(AK112,List!$K$2:$M$447,2,FALSE)","v":"IES04H03_T"},{"$f":"_xlfn.IFNA(\"L\"&AM112&\" \"&\"AT%I\"&B113*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J112&\"*)\",\" \")","v":"LIES04H03_T AT%I304.0 :INT ; (*室内环境状态T-12-温度状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112))),SEARCH(\":\",REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN112,SEARCH(\"AT%\",AN112),,REPT(\" \",25-SEARCH(\"AT%\",AN112)))))),\" \")","v":"LIES04H03_T             AT%I304.0      :INT ; (*室内环境状态T-12-温度状态*)"},null,{"$f":"AM112","v":"IES04H03_T"},{"$f":"J112","v":"室内环境状态T-12-温度状态"},{"$f":"30000+($B113*8+F112-1)","v":30152}]
[null,19,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),4,1))","v":1},2,null,2,"0V","风机盘管-温度状态",{"$nulls":16},{"$f":"IF(AI113=\"\",\"\",AI113)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL113,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"风机盘管",null,"04H01","温度状态",{"$f":"AH113&\"-\"&AK113","v":"风机盘管-温度状态"},{"$f":"VLOOKUP(AH113,List!$B$3:$D$445,2,FALSE)&AJ113&\"_\"&VLOOKUP(AK113,List!$K$2:$M$447,2,FALSE)","v":"FCU04H01_T"},{"$f":"_xlfn.IFNA(\"L\"&AM113&\" \"&\"AT%I\"&B113*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J113&\"*)\",\" \")","v":"LFCU04H01_T AT%I306.0 :INT ; (*风机盘管-温度状态*)"},"LFCU04H01_T             AT%I306.0      :INT ; (*风机盘管-温度状态*)",null,"FCU04H01_T",{"$f":"J113","v":"风机盘管-温度状态"},{"$f":"AS112+1","v":30153}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),3,1))","v":0},3,null,3,"0V","室内环境状态LUX-05-照度",{"$nulls":16},"LUX-05",{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL114,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","LUX-05","04H01","照度","室内环境状态-照度",{"$f":"VLOOKUP(AH114,List!$B$3:$D$445,2,FALSE)&AJ114&\"_\"&VLOOKUP(AK114,List!$K$2:$M$447,2,FALSE)","v":"IES04H01_I"},{"$f":"_xlfn.IFNA(\"L\"&AM114&\" \"&\"AT%I\"&B113*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J114&\"*)\",\" \")","v":"LIES04H01_I AT%I308.0 :INT ; (*室内环境状态LUX-05-照度*)"},"LIES04H01_I             AT%I308.0      :INT ; (*室内环境状态LUX-05-照度*)",null,"IES04H01_I","室内环境状态LUX-05-照度",{"$f":"AS113+1","v":30154}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),2,1))","v":0},4,null,4,"0V","室内环境状态LUX-06-照度",{"$nulls":16},"LUX-06",{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL115,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","LUX-06","04H02","照度","室内环境状态-照度",{"$f":"VLOOKUP(AH115,List!$B$3:$D$445,2,FALSE)&AJ115&\"_\"&VLOOKUP(AK115,List!$K$2:$M$447,2,FALSE)","v":"IES04H02_I"},{"$f":"_xlfn.IFNA(\"L\"&AM115&\" \"&\"AT%I\"&B113*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J115&\"*)\",\" \")","v":"LIES04H02_I AT%I310.0 :INT ; (*室内环境状态LUX-06-照度*)"},"LIES04H02_I             AT%I310.0      :INT ; (*室内环境状态LUX-06-照度*)",null,"IES04H02_I","室内环境状态LUX-06-照度",30155]
[null,"IOM 0801U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B113),REPT(0,5))),1,1))","v":1},5,null,5,"0V","室内环境状态CO2-05-二氧化碳浓度状态",{"$nulls":16},"CO2-05",{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL116,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"室内环境状态","CO2-05","04H01","二氧化碳浓度状态","室内环境状态-二氧化碳浓度状态",{"$f":"VLOOKUP(AH116,List!$B$3:$D$445,2,FALSE)&AJ116&\"_\"&VLOOKUP(AK116,List!$K$2:$M$447,2,FALSE)","v":"IES04H01_CO2"},{"$f":"_xlfn.IFNA(\"L\"&AM116&\" \"&\"AT%I\"&B113*16+8&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J116&\"*)\",\" \")","v":"LIES04H01_CO2 AT%I312.0 :INT ; (*室内环境状态CO2-05-二氧化碳浓度状态*)"},"LIES04H01_CO2           AT%I312.0      :INT ; (*室内环境状态CO2-05-二氧化碳浓度状态*)",null,"IES04H01_CO2","室内环境状态CO2-05-二氧化碳浓度状态",30156]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"0V","-",{"$nulls":16},{"$f":"IF(AI117=\"\",\"\",AI117)","v":""},{"$f":"_xlfn.IFNA(VLOOKUP(AL117,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL117,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH117,List!$B$3:$D$445,2,FALSE)&AJ117&\"_\"&VLOOKUP(AK117,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM117&\" \"&\"AT%I\"&B113*16+10&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J117&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},{"$f":"J117","v":"-"},30157]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL118,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL118,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH118,List!$B$3:$D$445,2,FALSE)&AJ118&\"_\"&VLOOKUP(AK118,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM118&\" \"&\"AT%I\"&B113*16+12&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J118&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30158]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B115=20,1,IF(B115=50,10,IF(B115=125,11,IF(B115=250,100,IF(B115=500,101,IF(B115=800,110,IF(B115=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL119,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL119,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH119,List!$B$3:$D$445,2,FALSE)&AJ119&\"_\"&VLOOKUP(AK119,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM119&\" \"&\"AT%I\"&B113*16+14&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J119&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",30159]
[null,{"$f":"B50","v":0},{"$nulls":38},{"$f":"\"(* \"&B125&\"地址: \"&B122&\" *)\"","v":"(* IOM 0401A地址: 20 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),5,1))","v":0},1,null,1,2,{"$f":"AH121&AA121&\"-\"&AK121","v":"空调机组NJ-4AP(KT)8-1-水阀控制"},{"$nulls":16},{"$f":"IF(AI121=\"\",\"\",AI121)","v":"NJ-4AP(KT)8-1"},{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL121,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-1","04H01","水阀控制",{"$f":"AH121&\"-\"&AK121","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH121,List!$B$3:$D$445,2,FALSE)&AJ121&\"_\"&VLOOKUP(AK121,List!$K$2:$M$447,2,FALSE)","v":"AHU04H01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM121&\" \"&\"AT%Q\"&B122*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J121&\"*)\",\" \")","v":"LAHU04H01_WVC AT%Q320.0 :INT ; (*空调机组NJ-4AP(KT)8-1-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121))),SEARCH(\":\",REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN121,SEARCH(\"AT%\",AN121),,REPT(\" \",25-SEARCH(\"AT%\",AN121)))))),\" \")","v":"LAHU04H01_WVC           AT%Q320.0      :INT ; (*空调机组NJ-4AP(KT)8-1-水阀控制*)"},null,{"$f":"AM121","v":"AHU04H01_WVC"},{"$f":"J121","v":"空调机组NJ-4AP(KT)8-1-水阀控制"},{"$f":"40000+($B122*8+F121-1)","v":40160}]
[null,20,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH122&AA122&\"-\"&AK122","v":"空调机组NJ-4AP(KT)8-2-水阀控制"},{"$nulls":16},{"$f":"IF(AI122=\"\",\"\",AI122)","v":"NJ-4AP(KT)8-2"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL122,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-2","04H02","水阀控制",{"$f":"AH122&\"-\"&AK122","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH122,List!$B$3:$D$445,2,FALSE)&AJ122&\"_\"&VLOOKUP(AK122,List!$K$2:$M$447,2,FALSE)","v":"AHU04H02_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM122&\" \"&\"AT%Q\"&B122*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J122&\"*)\",\" \")","v":"LAHU04H02_WVC AT%Q322.0 :INT ; (*空调机组NJ-4AP(KT)8-2-水阀控制*)"},"LAHU04H02_WVC           AT%Q322.0      :INT ; (*空调机组NJ-4AP(KT)8-2-水阀控制*)",null,"AHU04H02_WVC",{"$f":"J122","v":"空调机组NJ-4AP(KT)8-2-水阀控制"},{"$f":"AS121+1","v":40161}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH123&AA123&\"-\"&AK123","v":"空调机组NJ-4AP(KT)8-3-水阀控制"},{"$nulls":16},"NJ-4AP(KT)8-3",{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL123,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-3","04H03","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH123,List!$B$3:$D$445,2,FALSE)&AJ123&\"_\"&VLOOKUP(AK123,List!$K$2:$M$447,2,FALSE)","v":"AHU04H03_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM123&\" \"&\"AT%Q\"&B122*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J123&\"*)\",\" \")","v":"LAHU04H03_WVC AT%Q324.0 :INT ; (*空调机组NJ-4AP(KT)8-3-水阀控制*)"},"LAHU04H03_WVC           AT%Q324.0      :INT ; (*空调机组NJ-4AP(KT)8-3-水阀控制*)",null,"AHU04H03_WVC","空调机组NJ-4AP(KT)8-3-水阀控制",{"$f":"AS122+1","v":40162}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH124&AA124&\"-\"&AK124","v":"空调机组NJ-4AP(KT)8-4-水阀控制"},{"$nulls":16},"NJ-4AP(KT)8-4",{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL124,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-4","04H04","水阀控制","空调机组-水阀控制",{"$f":"VLOOKUP(AH124,List!$B$3:$D$445,2,FALSE)&AJ124&\"_\"&VLOOKUP(AK124,List!$K$2:$M$447,2,FALSE)","v":"AHU04H04_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM124&\" \"&\"AT%Q\"&B122*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J124&\"*)\",\" \")","v":"LAHU04H04_WVC AT%Q326.0 :INT ; (*空调机组NJ-4AP(KT)8-4-水阀控制*)"},"LAHU04H04_WVC           AT%Q326.0      :INT ; (*空调机组NJ-4AP(KT)8-4-水阀控制*)",null,"AHU04H04_WVC","空调机组NJ-4AP(KT)8-4-水阀控制",40163]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B122),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B124=20,1,IF(B124=50,10,IF(B124=125,11,IF(B124=250,100,IF(B124=500,101,IF(B124=800,110,IF(B124=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,{"$f":"B134","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B134&\"地址: \"&B131&\" *)\"","v":"(* IOM 0401A地址: 21 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH130&AA130&\"-\"&AK130","v":"空调机组NJ-4AP(KT)8-5-水阀控制"},{"$nulls":16},{"$f":"IF(AI130=\"\",\"\",AI130)","v":"NJ-4AP(KT)8-5"},{"$f":"_xlfn.IFNA(VLOOKUP(AL130,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL130,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-5","04H05","水阀控制",{"$f":"AH130&\"-\"&AK130","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH130,List!$B$3:$D$445,2,FALSE)&AJ130&\"_\"&VLOOKUP(AK130,List!$K$2:$M$447,2,FALSE)","v":"AHU04H05_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM130&\" \"&\"AT%Q\"&B131*16&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J130&\"*)\",\" \")","v":"LAHU04H05_WVC AT%Q336.0 :INT ; (*空调机组NJ-4AP(KT)8-5-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN130,SEARCH(\"AT%\",AN130),,REPT(\" \",25-SEARCH(\"AT%\",AN130))),SEARCH(\":\",REPLACE(AN130,SEARCH(\"AT%\",AN130),,REPT(\" \",25-SEARCH(\"AT%\",AN130)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN130,SEARCH(\"AT%\",AN130),,REPT(\" \",25-SEARCH(\"AT%\",AN130)))))),\" \")","v":"LAHU04H05_WVC           AT%Q336.0      :INT ; (*空调机组NJ-4AP(KT)8-5-水阀控制*)"},null,{"$f":"AM130","v":"AHU04H05_WVC"},{"$f":"J130","v":"空调机组NJ-4AP(KT)8-5-水阀控制"},{"$f":"40000+($B131*8+F130-1)","v":40168}]
[null,21,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),4,1))","v":0},2,null,3,4,{"$f":"AH131&AA131&\"-\"&AK131","v":"空调机组NJ-4AP(KT)8-6-水阀控制"},{"$nulls":16},{"$f":"IF(AI131=\"\",\"\",AI131)","v":"NJ-4AP(KT)8-6"},{"$f":"_xlfn.IFNA(VLOOKUP(AL131,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL131,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-6","04H06","水阀控制",{"$f":"AH131&\"-\"&AK131","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH131,List!$B$3:$D$445,2,FALSE)&AJ131&\"_\"&VLOOKUP(AK131,List!$K$2:$M$447,2,FALSE)","v":"AHU04H06_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM131&\" \"&\"AT%Q\"&B131*16+2&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J131&\"*)\",\" \")","v":"LAHU04H06_WVC AT%Q338.0 :INT ; (*空调机组NJ-4AP(KT)8-6-水阀控制*)"},"LAHU04H06_WVC           AT%Q338.0      :INT ; (*空调机组NJ-4AP(KT)8-6-水阀控制*)",null,"AHU04H06_WVC",{"$f":"J131","v":"空调机组NJ-4AP(KT)8-6-水阀控制"},{"$f":"AS130+1","v":40169}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),3,1))","v":1},3,null,5,6,{"$f":"AH132&AA132&\"-\"&AK132","v":"空调机组NJ-4AP(KT)8-7-水阀控制"},{"$nulls":16},"NJ-4AP(KT)8-7",{"$f":"_xlfn.IFNA(VLOOKUP(AL132,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL132,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"空调机组","NJ-4AP(KT)8-7","04H07","水阀控制",{"$f":"AH132&\"-\"&AK132","v":"空调机组-水阀控制"},{"$f":"VLOOKUP(AH132,List!$B$3:$D$445,2,FALSE)&AJ132&\"_\"&VLOOKUP(AK132,List!$K$2:$M$447,2,FALSE)","v":"AHU04H07_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM132&\" \"&\"AT%Q\"&B131*16+4&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J132&\"*)\",\" \")","v":"LAHU04H07_WVC AT%Q340.0 :INT ; (*空调机组NJ-4AP(KT)8-7-水阀控制*)"},"LAHU04H07_WVC           AT%Q340.0      :INT ; (*空调机组NJ-4AP(KT)8-7-水阀控制*)",null,"AHU04H07_WVC","空调机组NJ-4AP(KT)8-7-水阀控制",{"$f":"AS131+1","v":40170}]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),2,1))","v":0},4,null,7,8,{"$f":"AH133&AA133&\"-\"&AK133","v":"-"},{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL133,List!$O$3:$P$444,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL133,List!$O$3:$Q$444,3,FALSE),\"-\")","v":"-"},{"$nulls":8},{"$f":"AH133&\"-\"&AK133","v":"-"},{"$f":"VLOOKUP(AH133,List!$B$3:$D$445,2,FALSE)&AJ133&\"_\"&VLOOKUP(AK133,List!$K$2:$M$447,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM133&\" \"&\"AT%Q\"&B131*16+6&\".0\"&\" \"&\":INT ;\"&\" \"&\"(*\"&J133&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",40171]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B131),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B133=20,1,IF(B133=50,10,IF(B133=125,11,IF(B133=250,100,IF(B133=500,101,IF(B133=800,110,IF(B133=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L505","index":45,"n_rows":50,"n_cols":45,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[15,5,15,6],[15,9,15,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[24,5,24,6],[24,9,24,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[33,5,33,6],[33,9,33,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[42,5,42,6],[42,9,42,25],[43,5,43,6],[43,9,43,25],[44,5,44,6],[44,9,44,25],[45,5,45,6],[45,9,45,25],[46,5,46,6],[46,9,46,25],[47,5,47,6],[47,9,47,25],[48,5,48,6],[48,9,48,25],[49,5,49,6],[49,9,49,25],[4,1,5,1],[11,1,22,1],[28,1,31,1],[37,1,40,1],[46,1,49,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25],[15,2,22,4]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L01",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.1601R D7",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 1601R地址: 22 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH8&AA8&\"-\"&AK8","v":"F新风机组NJ-5AP(KT)81-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-5AP(KT)81"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)81","05E01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"F新风机组-运行状态"},{"$f":"VLOOKUP(AH8,[1]List!$D$3:$F$527,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05E01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LFAU05E01_R AT%I352.0 :BOOL; (*F新风机组NJ-5AP(KT)81-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LFAU05E01_R             AT%I352.0      :BOOL; (*F新风机组NJ-5AP(KT)81-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L01\\L01FAU05E01_R"},{"$f":"J8","v":"F新风机组NJ-5AP(KT)81-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":12816}]
[null,22,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},2,null,2,"C","F新风机组NJ-5AP(KT)81-故障状态",{"$nulls":16},"NJ-5AP(KT)81",{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)81","05E01","故障状态","F新风机组-故障状态",{"$f":"VLOOKUP(AH9,[1]List!$D$3:$F$527,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05E01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LFAU05E01_F AT%I352.1 :BOOL; (*F新风机组NJ-5AP(KT)81-故障状态*)"},"LFAU05E01_F             AT%I352.1      :BOOL; (*F新风机组NJ-5AP(KT)81-故障状态*)",null,"L01\\L01FAU05E01_F","F新风机组NJ-5AP(KT)81-故障状态",{"$f":"AS8+1","v":12817}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":1},3,null,3,"C","F新风机组NJ-5AP(KT)81-自动状态",{"$nulls":16},"NJ-5AP(KT)81",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)81","05E01","自动状态","F新风机组-自动状态",{"$f":"VLOOKUP(AH10,[1]List!$D$3:$F$527,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05E01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LFAU05E01_A AT%I352.2 :BOOL; (*F新风机组NJ-5AP(KT)81-自动状态*)"},"LFAU05E01_A             AT%I352.2      :BOOL; (*F新风机组NJ-5AP(KT)81-自动状态*)",null,"L01\\L01FAU05E01_A","F新风机组NJ-5AP(KT)81-自动状态",12818]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":0},4,null,4,"C","F新风机组NJ-5AP(KT)81-风机压差",{"$nulls":16},"NJ-5AP(KT)81",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)81","05E01","风机压差","F新风机组-风机压差",{"$f":"VLOOKUP(AH11,[1]List!$D$3:$F$527,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05E01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LFAU05E01_FPS AT%I352.3 :BOOL; (*F新风机组NJ-5AP(KT)81-风机压差*)"},"LFAU05E01_FPS           AT%I352.3      :BOOL; (*F新风机组NJ-5AP(KT)81-风机压差*)",null,"L01\\L01FAU05E01_FPS","F新风机组NJ-5AP(KT)81-风机压差",12819]
[null,"IOM 1601R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},5,null,5,"C","F新风机组NJ-5AP(KT)81-初效滤网压差",{"$nulls":16},"NJ-5AP(KT)81",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)81","05E01","初效滤网压差","F新风机组-初效滤网压差",{"$f":"VLOOKUP(AH12,[1]List!$D$3:$F$527,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05E01_IPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LFAU05E01_IPS AT%I352.4 :BOOL; (*F新风机组NJ-5AP(KT)81-初效滤网压差*)"},"LFAU05E01_IPS           AT%I352.4      :BOOL; (*F新风机组NJ-5AP(KT)81-初效滤网压差*)",null,"L01\\L01FAU05E01_IPS","F新风机组NJ-5AP(KT)81-初效滤网压差",12820]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","F新风机组NJ-5AP(KT)81-低温断路开关",{"$nulls":16},"NJ-5AP(KT)81",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)81","05E01","低温断路开关","F新风机组-低温断路开关",{"$f":"VLOOKUP(AH13,[1]List!$D$3:$F$527,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05E01_AFS"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LFAU05E01_AFS AT%I352.5 :BOOL; (*F新风机组NJ-5AP(KT)81-低温断路开关*)"},"LFAU05E01_AFS           AT%I352.5      :BOOL; (*F新风机组NJ-5AP(KT)81-低温断路开关*)",null,"L01\\L01FAU05E01_AFS","F新风机组NJ-5AP(KT)81-低温断路开关",12821]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","F新风机组NJ-5AP(KT)81-新风阀开状态",{"$nulls":16},"NJ-5AP(KT)81",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)81","05E01","新风阀开状态","F新风机组-新风阀开状态",{"$f":"VLOOKUP(AH14,[1]List!$D$3:$F$527,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05E01_FDOB"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LFAU05E01_FDOB AT%I352.6 :BOOL; (*F新风机组NJ-5AP(KT)81-新风阀开状态*)"},"LFAU05E01_FDOB          AT%I352.6      :BOOL; (*F新风机组NJ-5AP(KT)81-新风阀开状态*)",null,"L01\\L01FAU05E01_FDOB","F新风机组NJ-5AP(KT)81-新风阀开状态",12822]
[null,null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","F新风机组NJ-5AP(KT)81-新风阀关状态",{"$nulls":16},"NJ-5AP(KT)81",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)81","05E01","新风阀关状态","F新风机组-新风阀关状态",{"$f":"VLOOKUP(AH15,[1]List!$D$3:$F$527,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05E01_FDSB"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LFAU05E01_FDSB AT%I352.7 :BOOL; (*F新风机组NJ-5AP(KT)81-新风阀关状态*)"},"LFAU05E01_FDSB          AT%I352.7      :BOOL; (*F新风机组NJ-5AP(KT)81-新风阀关状态*)",null,"L01\\L01FAU05E01_FDSB","F新风机组NJ-5AP(KT)81-新风阀关状态",12823]
[{"$nulls":5},9,null,9,"C","排烟机NJ-5AP(YY)8-运行状态",{"$nulls":16},"NJ-5AP(YY)8",{"$f":"_xlfn.IFNA(VLOOKUP(AL16,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL16,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排烟机","NJ-5AP(YY)8","05E01","运行状态","排烟机-运行状态",{"$f":"VLOOKUP(AH16,[1]List!$D$3:$F$527,2,FALSE)&AJ16&\"_\"&VLOOKUP(AK16,[1]List!$I$2:$K$529,2,FALSE)","v":"ESF05E01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM16&\" \"&\"AT%I\"&B9*16+1&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J16&\"*)\",\" \")","v":"LESF05E01_R AT%I353.0 :BOOL; (*排烟机NJ-5AP(YY)8-运行状态*)"},"LESF05E01_R             AT%I353.0      :BOOL; (*排烟机NJ-5AP(YY)8-运行状态*)",null,"L01\\L01ESF05E01_R","排烟机NJ-5AP(YY)8-运行状态",12824]
[{"$nulls":5},10,null,10,"C","排烟机NJ-5AP(YY)8-故障状态",{"$nulls":16},"NJ-5AP(YY)8",{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排烟机","NJ-5AP(YY)8","05E01","故障状态","排烟机-故障状态",{"$f":"VLOOKUP(AH17,[1]List!$D$3:$F$527,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,[1]List!$I$2:$K$529,2,FALSE)","v":"ESF05E01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%I\"&B9*16+1&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LESF05E01_F AT%I353.1 :BOOL; (*排烟机NJ-5AP(YY)8-故障状态*)"},"LESF05E01_F             AT%I353.1      :BOOL; (*排烟机NJ-5AP(YY)8-故障状态*)",null,"L01\\L01ESF05E01_F","排烟机NJ-5AP(YY)8-故障状态",12825]
[{"$nulls":5},11,null,11,"C","排烟机NJ-5AP(YY)8-自动状态",{"$nulls":16},"NJ-5AP(YY)8",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排烟机","NJ-5AP(YY)8","05E01","自动状态","排烟机-自动状态",{"$f":"VLOOKUP(AH18,[1]List!$D$3:$F$527,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,[1]List!$I$2:$K$529,2,FALSE)","v":"ESF05E01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%I\"&B9*16+1&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LESF05E01_A AT%I353.2 :BOOL; (*排烟机NJ-5AP(YY)8-自动状态*)"},"LESF05E01_A             AT%I353.2      :BOOL; (*排烟机NJ-5AP(YY)8-自动状态*)",null,"L01\\L01ESF05E01_A","排烟机NJ-5AP(YY)8-自动状态",12826]
[{"$nulls":5},12,null,12,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH19,[1]List!$D$3:$F$527,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%I\"&B9*16+1&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN19,SEARCH(\"AT%\",AN19),,REPT(\" \",30-SEARCH(\"AT%\",AN19))),SEARCH(\":\",REPLACE(AN19,SEARCH(\"AT%\",AN19),,REPT(\" \",30-SEARCH(\"AT%\",AN19)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN19,SEARCH(\"AT%\",AN19),,REPT(\" \",25-SEARCH(\"AT%\",AN19)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",12827]
[{"$nulls":5},13,null,13,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH20,[1]List!$D$3:$F$527,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%I\"&B9*16+1&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",12828]
[{"$nulls":5},14,null,14,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH21,[1]List!$D$3:$F$527,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%I\"&B9*16+1&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",12829]
[{"$nulls":5},15,null,15,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH22,[1]List!$D$3:$F$527,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%I\"&B9*16+1&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",12830]
[".",{"$nulls":4},16,null,16,"C","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH23,[1]List!$D$3:$F$527,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%I\"&B9*16+1&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",12831]
[null,{"$f":"B29","v":"IOM 0801D"},{"$nulls":38},{"$f":"\"(* \"&B29&\"地址: \"&B26&\" *)\"","v":"(* IOM 0801D地址: 23 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH25&AA25&\"-\"&AK25","v":"F新风机组NJ-5AP(KT)81-启停控制"},{"$nulls":16},{"$f":"IF(AI25=\"\",\"\",AI25)","v":"NJ-5AP(KT)81"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL25,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)81","05E01","启停控制",{"$f":"AH25&\"-\"&AK25","v":"F新风机组-启停控制"},{"$f":"VLOOKUP(AH25,[1]List!$D$3:$F$527,2,FALSE)&AJ25&\"_\"&VLOOKUP(AK25,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05E01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM25&\" \"&\"AT%Q\"&B26*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J25&\"*)\",\" \")","v":"LFAU05E01_C AT%Q368.0 :BOOL; (*F新风机组NJ-5AP(KT)81-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25))),SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN25,SEARCH(\"AT%\",AN25),,REPT(\" \",25-SEARCH(\"AT%\",AN25)))))),\" \")","v":"LFAU05E01_C             AT%Q368.0      :BOOL; (*F新风机组NJ-5AP(KT)81-启停控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM25","v":"L01\\L01FAU05E01_C"},{"$f":"J25","v":"F新风机组NJ-5AP(KT)81-启停控制"},{"$f":"($B26*16*8+F25-1)","v":2944}]
[null,23,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","F新风机组NJ-5AP(KT)81-新风阀开控制",{"$nulls":16},"NJ-5AP(KT)81",{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)81","05E01","新风阀开控制","F新风机组-新风阀开控制",{"$f":"VLOOKUP(AH26,[1]List!$D$3:$F$527,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05E01_FDOC"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%Q\"&B26*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LFAU05E01_FDOC AT%Q368.1 :BOOL; (*F新风机组NJ-5AP(KT)81-新风阀开控制*)"},"LFAU05E01_FDOC          AT%Q368.1      :BOOL; (*F新风机组NJ-5AP(KT)81-新风阀开控制*)",null,"L01\\L01FAU05E01_FDOC","F新风机组NJ-5AP(KT)81-新风阀开控制",{"$f":"AS25+1","v":2945}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),3,1))","v":1},3,null,"3+","3-","F新风机组NJ-5AP(KT)81-新风阀关控制",{"$nulls":16},"NJ-5AP(KT)81",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)81","05E01","新风阀关控制","F新风机组-新风阀关控制",{"$f":"VLOOKUP(AH27,[1]List!$D$3:$F$527,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05E01_FDSC"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%Q\"&B26*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LFAU05E01_FDSC AT%Q368.2 :BOOL; (*F新风机组NJ-5AP(KT)81-新风阀关控制*)"},"LFAU05E01_FDSC          AT%Q368.2      :BOOL; (*F新风机组NJ-5AP(KT)81-新风阀关控制*)",null,"L01\\L01FAU05E01_FDSC","F新风机组NJ-5AP(KT)81-新风阀关控制",2946]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),2,1))","v":0},4,null,"4+","4-","排烟机NJ-5AP(YY)8-启停控制",{"$nulls":16},"NJ-5AP(YY)8",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"排烟机","NJ-5AP(YY)8","05E01","启停控制","排烟机-启停控制",{"$f":"VLOOKUP(AH28,[1]List!$D$3:$F$527,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,[1]List!$I$2:$K$529,2,FALSE)","v":"ESF05E01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%Q\"&B26*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LESF05E01_C AT%Q368.3 :BOOL; (*排烟机NJ-5AP(YY)8-启停控制*)"},"LESF05E01_C             AT%Q368.3      :BOOL; (*排烟机NJ-5AP(YY)8-启停控制*)",null,"L01\\L01ESF05E01_C","排烟机NJ-5AP(YY)8-启停控制",2947]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B26),REPT(0,5))),1,1))","v":1},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH29,[1]List!$D$3:$F$527,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%Q\"&B26*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2948]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL30,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL30,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH30,[1]List!$D$3:$F$527,2,FALSE)&AJ30&\"_\"&VLOOKUP(AK30,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM30&\" \"&\"AT%Q\"&B26*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J30&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN30,SEARCH(\"AT%\",AN30),,REPT(\" \",30-SEARCH(\"AT%\",AN30))),SEARCH(\":\",REPLACE(AN30,SEARCH(\"AT%\",AN30),,REPT(\" \",30-SEARCH(\"AT%\",AN30)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN30,SEARCH(\"AT%\",AN30),,REPT(\" \",25-SEARCH(\"AT%\",AN30)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",2949]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL31,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL31,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH31,[1]List!$D$3:$F$527,2,FALSE)&AJ31&\"_\"&VLOOKUP(AK31,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM31&\" \"&\"AT%Q\"&B26*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J31&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2950]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B28=20,1,IF(B28=50,10,IF(B28=125,11,IF(B28=250,100,IF(B28=500,101,IF(B28=800,110,IF(B28=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL32,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL32,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH32,[1]List!$D$3:$F$527,2,FALSE)&AJ32&\"_\"&VLOOKUP(AK32,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM32&\" \"&\"AT%Q\"&B26*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J32&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",2951]
[null,{"$f":"B38","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B38&\"地址: \"&B35&\" *)\"","v":"(* IOM 0401U地址: 24 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH34&AA34&\"-\"&AK34","v":"F新风机组NJ-5AP(KT)81-送风温度"},{"$nulls":16},{"$f":"IF(AI34=\"\",\"\",AI34)","v":"NJ-5AP(KT)81"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL34,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)81","05E01","送风温度",{"$f":"AH34&\"-\"&AK34","v":"F新风机组-送风温度"},{"$f":"VLOOKUP(AH34,[1]List!$D$3:$F$527,2,FALSE)&AJ34&\"_\"&VLOOKUP(AK34,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05E01_ST"},{"$f":"_xlfn.IFNA(\"L\"&AM34&\" \"&\"AT%I\"&B35*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J34&\"*)\",\" \")","v":"LFAU05E01_ST AT%I384.0 :INT; (*F新风机组NJ-5AP(KT)81-送风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34))),SEARCH(\":\",REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN34,SEARCH(\"AT%\",AN34),,REPT(\" \",25-SEARCH(\"AT%\",AN34)))))),\" \")","v":"LFAU05E01_ST            AT%I384.0      :INT; (*F新风机组NJ-5AP(KT)81-送风温度*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM34","v":"L01\\L01FAU05E01_ST"},{"$f":"J34","v":"F新风机组NJ-5AP(KT)81-送风温度"},{"$f":"30000+($B35*8+F34-1)","v":30192}]
[null,24,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),4,1))","v":0},2,null,2,"0V","F新风机组NJ-5AP(KT)81-水阀反馈",{"$nulls":16},"NJ-5AP(KT)81",{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)81","05E01","水阀反馈","F新风机组-水阀反馈",{"$f":"VLOOKUP(AH35,[1]List!$D$3:$F$527,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05E01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%I\"&B35*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LFAU05E01_WVB AT%I386.0 :INT; (*F新风机组NJ-5AP(KT)81-水阀反馈*)"},"LFAU05E01_WVB           AT%I386.0      :INT; (*F新风机组NJ-5AP(KT)81-水阀反馈*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM35","v":"L01\\L01FAU05E01_WVB"},"F新风机组NJ-5AP(KT)81-水阀反馈",{"$f":"AS34+1","v":30193}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),3,1))","v":0},3,null,3,"0V","F新风机组NJ-5AP(KT)81-变频器频率反馈",{"$nulls":16},"NJ-5AP(KT)81",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)81","05E01","变频器频率反馈","F新风机组-变频器频率反馈",{"$f":"VLOOKUP(AH36,[1]List!$D$3:$F$527,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05E01_VFB"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%I\"&B35*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LFAU05E01_VFB AT%I388.0 :INT; (*F新风机组NJ-5AP(KT)81-变频器频率反馈*)"},"LFAU05E01_VFB           AT%I388.0      :INT; (*F新风机组NJ-5AP(KT)81-变频器频率反馈*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM36","v":"L01\\L01FAU05E01_VFB"},"F新风机组NJ-5AP(KT)81-变频器频率反馈",30194]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),2,1))","v":1},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH37,[1]List!$D$3:$F$527,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%I\"&B35*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN37,SEARCH(\"AT%\",AN37),,REPT(\" \",30-SEARCH(\"AT%\",AN37))),SEARCH(\":\",REPLACE(AN37,SEARCH(\"AT%\",AN37),,REPT(\" \",30-SEARCH(\"AT%\",AN37)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN37,SEARCH(\"AT%\",AN37),,REPT(\" \",25-SEARCH(\"AT%\",AN37)))))),\" \")","v":" "},null,{"$f":"$B$2&\"\\\"&$B$2&AM37","v":{"$error":"#N/A"}},"-",30195]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B35),REPT(0,5))),1,1))","v":1}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B37=20,1,IF(B37=50,10,IF(B37=125,11,IF(B37=250,100,IF(B37=500,101,IF(B37=800,110,IF(B37=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B47","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B47&\"地址: \"&B44&\" *)\"","v":"(* IOM 0401A地址: 25 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH43&AA43&\"-\"&AK43","v":"F新风机组NJ-5AP(KT)81-水阀控制"},{"$nulls":16},{"$f":"IF(AI43=\"\",\"\",AI43)","v":"NJ-5AP(KT)81"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL43,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)81","05E01","水阀控制",{"$f":"AH43&\"-\"&AK43","v":"F新风机组-水阀控制"},{"$f":"VLOOKUP(AH43,[1]List!$D$3:$F$527,2,FALSE)&AJ43&\"_\"&VLOOKUP(AK43,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05E01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM43&\" \"&\"AT%Q\"&B44*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J43&\"*)\",\" \")","v":"LFAU05E01_WVC AT%Q400.0 :INT; (*F新风机组NJ-5AP(KT)81-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43))),SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN43,SEARCH(\"AT%\",AN43),,REPT(\" \",25-SEARCH(\"AT%\",AN43)))))),\" \")","v":"LFAU05E01_WVC           AT%Q400.0      :INT; (*F新风机组NJ-5AP(KT)81-水阀控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM43","v":"L01\\L01FAU05E01_WVC"},{"$f":"J43","v":"F新风机组NJ-5AP(KT)81-水阀控制"},{"$f":"40000+($B44*8+F43-1)","v":40200}]
[null,25,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),4,1))","v":0},2,null,3,4,"F新风机组NJ-5AP(KT)81-变频器频率控制",{"$nulls":16},"NJ-5AP(KT)81",{"$f":"_xlfn.IFNA(VLOOKUP(AL44,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL44,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)81","05E01","变频器频率控制","F新风机组-变频器频率控制",{"$f":"VLOOKUP(AH44,[1]List!$D$3:$F$527,2,FALSE)&AJ44&\"_\"&VLOOKUP(AK44,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05E01_VFC"},{"$f":"_xlfn.IFNA(\"L\"&AM44&\" \"&\"AT%Q\"&B44*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J44&\"*)\",\" \")","v":"LFAU05E01_VFC AT%Q402.0 :INT; (*F新风机组NJ-5AP(KT)81-变频器频率控制*)"},"LFAU05E01_VFC           AT%Q402.0      :INT; (*F新风机组NJ-5AP(KT)81-变频器频率控制*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM44","v":"L01\\L01FAU05E01_VFC"},"F新风机组NJ-5AP(KT)81-变频器频率控制",{"$f":"AS43+1","v":40201}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),3,1))","v":0},3,null,5,6,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL45,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL45,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH45,[1]List!$D$3:$F$527,2,FALSE)&AJ45&\"_\"&VLOOKUP(AK45,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM45&\" \"&\"AT%Q\"&B44*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J45&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM45","v":{"$error":"#N/A"}},"-",40202]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),2,1))","v":1},4,null,7,8,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL46,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL46,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH46,[1]List!$D$3:$F$527,2,FALSE)&AJ46&\"_\"&VLOOKUP(AK46,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM46&\" \"&\"AT%Q\"&B44*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J46&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN46,SEARCH(\"AT%\",AN46),,REPT(\" \",30-SEARCH(\"AT%\",AN46))),SEARCH(\":\",REPLACE(AN46,SEARCH(\"AT%\",AN46),,REPT(\" \",30-SEARCH(\"AT%\",AN46)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN46,SEARCH(\"AT%\",AN46),,REPT(\" \",25-SEARCH(\"AT%\",AN46)))))),\" \")","v":" "},null,{"$f":"$B$2&\"\\\"&$B$2&AM46","v":{"$error":"#N/A"}},"-",40203]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B44),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B46=20,1,IF(B46=50,10,IF(B46=125,11,IF(B46=250,100,IF(B46=500,101,IF(B46=800,110,IF(B46=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]

{"sheet":"L506","index":46,"n_rows":42,"n_cols":45,"rows_kept":42,"cut":false,"hidden":false,"merged":[[0,9,0,25],[3,1,3,28],[3,29,3,31],[3,32,3,40],[3,41,3,44],[4,27,4,28],[7,5,7,6],[7,9,7,25],[8,5,8,6],[8,9,8,25],[9,5,9,6],[9,9,9,25],[10,5,10,6],[10,9,10,25],[11,5,11,6],[11,9,11,25],[12,5,12,6],[12,9,12,25],[13,5,13,6],[13,9,13,25],[14,5,14,6],[14,9,14,25],[16,5,16,6],[16,9,16,25],[17,5,17,6],[17,9,17,25],[18,5,18,6],[18,9,18,25],[19,5,19,6],[19,9,19,25],[20,5,20,6],[20,9,20,25],[21,5,21,6],[21,9,21,25],[22,5,22,6],[22,9,22,25],[23,5,23,6],[23,9,23,25],[25,5,25,6],[25,9,25,25],[26,5,26,6],[26,9,26,25],[27,5,27,6],[27,9,27,25],[28,5,28,6],[28,9,28,25],[29,5,29,6],[29,9,29,25],[30,5,30,6],[30,9,30,25],[31,5,31,6],[31,9,31,25],[32,5,32,6],[32,9,32,25],[34,5,34,6],[34,9,34,25],[35,5,35,6],[35,9,35,25],[36,5,36,6],[36,9,36,25],[37,5,37,6],[37,9,37,25],[38,5,38,6],[38,9,38,25],[39,5,39,6],[39,9,39,25],[40,5,40,6],[40,9,40,25],[41,5,41,6],[41,9,41,25],[4,1,5,1],[11,1,14,1],[20,1,23,1],[29,1,32,1],[38,1,41,1],[4,26,5,26],[4,29,5,29],[4,30,5,30],[4,31,5,31],[4,32,5,32],[4,33,5,33],[4,34,5,34],[4,35,5,35],[4,36,5,36],[4,37,5,37],[4,38,5,38],[4,39,5,39],[4,40,5,40],[4,41,5,41],[4,42,5,42],[4,43,5,43],[4,44,5,44],[4,2,5,4],[4,5,5,6],[4,7,5,8],[4,9,5,25]]}
[null,4.5,1.5,1.5,1.5,1.5,1.5,1.75,1.75,35,{"$nulls":16},15,10,10]
[12,"L01",0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,null,"X","X","X","X"]
[12,null,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,{"$nulls":8},20]
[25,"DDC-X-X 现场实施段",{"$nulls":27},"调试记录段",null,null,"下位机声明段",{"$nulls":8},"上位机声明段"]
[20,"模块类型","拨码\n设置",null,null,"点位序号",null,"端子编号",null,"线缆功能.auto",{"$nulls":16},"设备编号.auto","前端接线备注.auto",null,"DBG","调试记录","调试备注","PRG","设备类型","设备编号","程序编号","点位功能","接线备注\n判断区","变量名.auto","编程变量声明.auto","编程变量声明(结构整理).auto","HMI","上位机组态.auto","上位机注释.auto","MODBUS偏置量.auto"]
[20,{"$nulls":26},"端子编号","线色备注"]
[null,"IOM.0801R D7",{"$nulls":38},{"$f":"\"(* \"&B12&\"地址: \"&B9&\" *)\"","v":"(* IOM 0801R地址: 26 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),5,1))","v":0},1,null,1,"C",{"$f":"AH8&AA8&\"-\"&AK8","v":"F新风机组NJ-5AP(KT)82-运行状态"},{"$nulls":16},{"$f":"IF(AI8=\"\",\"\",AI8)","v":"NJ-5AP(KT)82"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL8,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)82","05F01","运行状态",{"$f":"AH8&\"-\"&AK8","v":"F新风机组-运行状态"},{"$f":"VLOOKUP(AH8,[1]List!$D$3:$F$527,2,FALSE)&AJ8&\"_\"&VLOOKUP(AK8,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05F01_R"},{"$f":"_xlfn.IFNA(\"L\"&AM8&\" \"&\"AT%I\"&B9*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J8&\"*)\",\" \")","v":"LFAU05F01_R AT%I416.0 :BOOL; (*F新风机组NJ-5AP(KT)82-运行状态*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8))),SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN8,SEARCH(\"AT%\",AN8),,REPT(\" \",25-SEARCH(\"AT%\",AN8)))))),\" \")","v":"LFAU05F01_R             AT%I416.0      :BOOL; (*F新风机组NJ-5AP(KT)82-运行状态*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM8","v":"L01\\L01FAU05F01_R"},{"$f":"J8","v":"F新风机组NJ-5AP(KT)82-运行状态"},{"$f":"10000+($B9*16*8+F8-1)","v":13328}]
[null,26,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),4,1))","v":1},2,null,2,"C","F新风机组NJ-5AP(KT)82-故障状态",{"$nulls":16},"NJ-5AP(KT)82",{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL9,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)82","05F01","故障状态","F新风机组-故障状态",{"$f":"VLOOKUP(AH9,[1]List!$D$3:$F$527,2,FALSE)&AJ9&\"_\"&VLOOKUP(AK9,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05F01_F"},{"$f":"_xlfn.IFNA(\"L\"&AM9&\" \"&\"AT%I\"&B9*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J9&\"*)\",\" \")","v":"LFAU05F01_F AT%I416.1 :BOOL; (*F新风机组NJ-5AP(KT)82-故障状态*)"},"LFAU05F01_F             AT%I416.1      :BOOL; (*F新风机组NJ-5AP(KT)82-故障状态*)",null,"L01\\L01FAU05F01_F","F新风机组NJ-5AP(KT)82-故障状态",{"$f":"AS8+1","v":13329}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),3,1))","v":0},3,null,3,"C","F新风机组NJ-5AP(KT)82-自动状态",{"$nulls":16},"NJ-5AP(KT)82",{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL10,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)82","05F01","自动状态","F新风机组-自动状态",{"$f":"VLOOKUP(AH10,[1]List!$D$3:$F$527,2,FALSE)&AJ10&\"_\"&VLOOKUP(AK10,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05F01_A"},{"$f":"_xlfn.IFNA(\"L\"&AM10&\" \"&\"AT%I\"&B9*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J10&\"*)\",\" \")","v":"LFAU05F01_A AT%I416.2 :BOOL; (*F新风机组NJ-5AP(KT)82-自动状态*)"},"LFAU05F01_A             AT%I416.2      :BOOL; (*F新风机组NJ-5AP(KT)82-自动状态*)",null,"L01\\L01FAU05F01_A","F新风机组NJ-5AP(KT)82-自动状态",13330]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),2,1))","v":1},4,null,4,"C","F新风机组NJ-5AP(KT)82-风机压差",{"$nulls":16},"NJ-5AP(KT)82",{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL11,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)82","05F01","风机压差","F新风机组-风机压差",{"$f":"VLOOKUP(AH11,[1]List!$D$3:$F$527,2,FALSE)&AJ11&\"_\"&VLOOKUP(AK11,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05F01_FPS"},{"$f":"_xlfn.IFNA(\"L\"&AM11&\" \"&\"AT%I\"&B9*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J11&\"*)\",\" \")","v":"LFAU05F01_FPS AT%I416.3 :BOOL; (*F新风机组NJ-5AP(KT)82-风机压差*)"},"LFAU05F01_FPS           AT%I416.3      :BOOL; (*F新风机组NJ-5AP(KT)82-风机压差*)",null,"L01\\L01FAU05F01_FPS","F新风机组NJ-5AP(KT)82-风机压差",13331]
[null,"IOM 0801R",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B9),REPT(0,5))),1,1))","v":1},5,null,5,"C","F新风机组NJ-5AP(KT)82-初效滤网压差",{"$nulls":16},"NJ-5AP(KT)82",{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL12,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)82","05F01","初效滤网压差","F新风机组-初效滤网压差",{"$f":"VLOOKUP(AH12,[1]List!$D$3:$F$527,2,FALSE)&AJ12&\"_\"&VLOOKUP(AK12,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05F01_IPS"},{"$f":"_xlfn.IFNA(\"L\"&AM12&\" \"&\"AT%I\"&B9*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J12&\"*)\",\" \")","v":"LFAU05F01_IPS AT%I416.4 :BOOL; (*F新风机组NJ-5AP(KT)82-初效滤网压差*)"},"LFAU05F01_IPS           AT%I416.4      :BOOL; (*F新风机组NJ-5AP(KT)82-初效滤网压差*)",null,"L01\\L01FAU05F01_IPS","F新风机组NJ-5AP(KT)82-初效滤网压差",13332]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,6,"C","F新风机组NJ-5AP(KT)82-低温断路开关",{"$nulls":16},"NJ-5AP(KT)82",{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL13,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)82","05F01","低温断路开关","F新风机组-低温断路开关",{"$f":"VLOOKUP(AH13,[1]List!$D$3:$F$527,2,FALSE)&AJ13&\"_\"&VLOOKUP(AK13,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05F01_AFS"},{"$f":"_xlfn.IFNA(\"L\"&AM13&\" \"&\"AT%I\"&B9*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J13&\"*)\",\" \")","v":"LFAU05F01_AFS AT%I416.5 :BOOL; (*F新风机组NJ-5AP(KT)82-低温断路开关*)"},"LFAU05F01_AFS           AT%I416.5      :BOOL; (*F新风机组NJ-5AP(KT)82-低温断路开关*)",null,"L01\\L01FAU05F01_AFS","F新风机组NJ-5AP(KT)82-低温断路开关",13333]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,7,"C","F新风机组NJ-5AP(KT)82-新风阀开状态",{"$nulls":16},"NJ-5AP(KT)82",{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL14,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)82","05F01","新风阀开状态","F新风机组-新风阀开状态",{"$f":"VLOOKUP(AH14,[1]List!$D$3:$F$527,2,FALSE)&AJ14&\"_\"&VLOOKUP(AK14,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05F01_FDOB"},{"$f":"_xlfn.IFNA(\"L\"&AM14&\" \"&\"AT%I\"&B9*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J14&\"*)\",\" \")","v":"LFAU05F01_FDOB AT%I416.6 :BOOL; (*F新风机组NJ-5AP(KT)82-新风阀开状态*)"},"LFAU05F01_FDOB          AT%I416.6      :BOOL; (*F新风机组NJ-5AP(KT)82-新风阀开状态*)",null,"L01\\L01FAU05F01_FDOB","F新风机组NJ-5AP(KT)82-新风阀开状态",13334]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B11=20,1,IF(B11=50,10,IF(B11=125,11,IF(B11=250,100,IF(B11=500,101,IF(B11=800,110,IF(B11=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,8,"C","F新风机组NJ-5AP(KT)82-新风阀关状态",{"$nulls":16},"NJ-5AP(KT)82",{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL15,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)82","05F01","新风阀关状态","F新风机组-新风阀关状态",{"$f":"VLOOKUP(AH15,[1]List!$D$3:$F$527,2,FALSE)&AJ15&\"_\"&VLOOKUP(AK15,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05F01_FDSB"},{"$f":"_xlfn.IFNA(\"L\"&AM15&\" \"&\"AT%I\"&B9*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J15&\"*)\",\" \")","v":"LFAU05F01_FDSB AT%I416.7 :BOOL; (*F新风机组NJ-5AP(KT)82-新风阀关状态*)"},"LFAU05F01_FDSB          AT%I416.7      :BOOL; (*F新风机组NJ-5AP(KT)82-新风阀关状态*)",null,"L01\\L01FAU05F01_FDSB","F新风机组NJ-5AP(KT)82-新风阀关状态",13335]
[null,{"$f":"B21","v":"IOM 0801D"},{"$nulls":38},{"$f":"\"(* \"&B21&\"地址: \"&B18&\" *)\"","v":"(* IOM 0801D地址: 27 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),5,1))","v":1},1,null,"1+","1-",{"$f":"AH17&AA17&\"-\"&AK17","v":"F新风机组NJ-5AP(KT)82-启停控制"},{"$nulls":16},{"$f":"IF(AI17=\"\",\"\",AI17)","v":"NJ-5AP(KT)82"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL17,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)82","05F01","启停控制",{"$f":"AH17&\"-\"&AK17","v":"F新风机组-启停控制"},{"$f":"VLOOKUP(AH17,[1]List!$D$3:$F$527,2,FALSE)&AJ17&\"_\"&VLOOKUP(AK17,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05F01_C"},{"$f":"_xlfn.IFNA(\"L\"&AM17&\" \"&\"AT%Q\"&B18*16&\".0\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J17&\"*)\",\" \")","v":"LFAU05F01_C AT%Q432.0 :BOOL; (*F新风机组NJ-5AP(KT)82-启停控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",25-SEARCH(\"AT%\",AN17))),SEARCH(\":\",REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",25-SEARCH(\"AT%\",AN17)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN17,SEARCH(\"AT%\",AN17),,REPT(\" \",25-SEARCH(\"AT%\",AN17)))))),\" \")","v":"LFAU05F01_C             AT%Q432.0      :BOOL; (*F新风机组NJ-5AP(KT)82-启停控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM17","v":"L01\\L01FAU05F01_C"},{"$f":"J17","v":"F新风机组NJ-5AP(KT)82-启停控制"},{"$f":"($B18*16*8+F17-1)","v":3456}]
[null,27,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),4,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),4,1))","v":1},2,null,"2+","2-","F新风机组NJ-5AP(KT)82-新风阀开控制",{"$nulls":16},"NJ-5AP(KT)82",{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL18,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)82","05F01","新风阀开控制","F新风机组-新风阀开控制",{"$f":"VLOOKUP(AH18,[1]List!$D$3:$F$527,2,FALSE)&AJ18&\"_\"&VLOOKUP(AK18,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05F01_FDOC"},{"$f":"_xlfn.IFNA(\"L\"&AM18&\" \"&\"AT%Q\"&B18*16&\".1\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J18&\"*)\",\" \")","v":"LFAU05F01_FDOC AT%Q432.1 :BOOL; (*F新风机组NJ-5AP(KT)82-新风阀开控制*)"},"LFAU05F01_FDOC          AT%Q432.1      :BOOL; (*F新风机组NJ-5AP(KT)82-新风阀开控制*)",null,"L01\\L01FAU05F01_FDOC","F新风机组NJ-5AP(KT)82-新风阀开控制",{"$f":"AS17+1","v":3457}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),3,1))","v":0},3,null,"3+","3-","F新风机组NJ-5AP(KT)82-新风阀关控制",{"$nulls":16},"NJ-5AP(KT)82",{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL19,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)82","05F01","新风阀关控制","F新风机组-新风阀关控制",{"$f":"VLOOKUP(AH19,[1]List!$D$3:$F$527,2,FALSE)&AJ19&\"_\"&VLOOKUP(AK19,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05F01_FDSC"},{"$f":"_xlfn.IFNA(\"L\"&AM19&\" \"&\"AT%Q\"&B18*16&\".2\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J19&\"*)\",\" \")","v":"LFAU05F01_FDSC AT%Q432.2 :BOOL; (*F新风机组NJ-5AP(KT)82-新风阀关控制*)"},"LFAU05F01_FDSC          AT%Q432.2      :BOOL; (*F新风机组NJ-5AP(KT)82-新风阀关控制*)",null,"L01\\L01FAU05F01_FDSC","F新风机组NJ-5AP(KT)82-新风阀关控制",3458]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),2,1))","v":1},4,null,"4+","4-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL20,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH20,[1]List!$D$3:$F$527,2,FALSE)&AJ20&\"_\"&VLOOKUP(AK20,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM20&\" \"&\"AT%Q\"&B18*16&\".3\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J20&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",3459]
[null,"IOM 0801D",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B18),REPT(0,5))),1,1))","v":1},5,null,"5+","5-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL21,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH21,[1]List!$D$3:$F$527,2,FALSE)&AJ21&\"_\"&VLOOKUP(AK21,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM21&\" \"&\"AT%Q\"&B18*16&\".4\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J21&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN21,SEARCH(\"AT%\",AN21),,REPT(\" \",30-SEARCH(\"AT%\",AN21))),SEARCH(\":\",REPLACE(AN21,SEARCH(\"AT%\",AN21),,REPT(\" \",30-SEARCH(\"AT%\",AN21)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN21,SEARCH(\"AT%\",AN21),,REPT(\" \",25-SEARCH(\"AT%\",AN21)))))),\" \")","v":" "},null,{"$error":"#N/A"},"-",3460]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),3,1))","v":0},6,null,"6+","6-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL22,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH22,[1]List!$D$3:$F$527,2,FALSE)&AJ22&\"_\"&VLOOKUP(AK22,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM22&\" \"&\"AT%Q\"&B18*16&\".5\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J22&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",3461]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),2,1))","v":1},7,null,"7+","7-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL23,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH23,[1]List!$D$3:$F$527,2,FALSE)&AJ23&\"_\"&VLOOKUP(AK23,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM23&\" \"&\"AT%Q\"&B18*16&\".6\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J23&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",3462]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B20=20,1,IF(B20=50,10,IF(B20=125,11,IF(B20=250,100,IF(B20=500,101,IF(B20=800,110,IF(B20=1000,111,0))))))),REPT(0,3))),1,1))","v":0},8,null,"8+","8-","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL24,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL24,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH24,[1]List!$D$3:$F$527,2,FALSE)&AJ24&\"_\"&VLOOKUP(AK24,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM24&\" \"&\"AT%Q\"&B18*16&\".7\"&\" \"&\":BOOL;\"&\" \"&\"(*\"&J24&\"*)\",\" \")","v":" "}," ",null,{"$error":"#N/A"},"-",3463]
[null,{"$f":"B30","v":"IOM 0401U"},{"$nulls":38},{"$f":"\"(* \"&B30&\"地址: \"&B27&\" *)\"","v":"(* IOM 0401U地址: 28 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),5,1))","v":0},1,null,1,"0V",{"$f":"AH26&AA26&\"-\"&AK26","v":"F新风机组NJ-5AP(KT)82-送风温度"},{"$nulls":16},{"$f":"IF(AI26=\"\",\"\",AI26)","v":"NJ-5AP(KT)82"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL26,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)82","05F01","送风温度",{"$f":"AH26&\"-\"&AK26","v":"F新风机组-送风温度"},{"$f":"VLOOKUP(AH26,[1]List!$D$3:$F$527,2,FALSE)&AJ26&\"_\"&VLOOKUP(AK26,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05F01_ST"},{"$f":"_xlfn.IFNA(\"L\"&AM26&\" \"&\"AT%I\"&B27*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J26&\"*)\",\" \")","v":"LFAU05F01_ST AT%I448.0 :INT; (*F新风机组NJ-5AP(KT)82-送风温度*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26))),SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN26,SEARCH(\"AT%\",AN26),,REPT(\" \",25-SEARCH(\"AT%\",AN26)))))),\" \")","v":"LFAU05F01_ST            AT%I448.0      :INT; (*F新风机组NJ-5AP(KT)82-送风温度*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM26","v":"L01\\L01FAU05F01_ST"},{"$f":"J26","v":"F新风机组NJ-5AP(KT)82-送风温度"},{"$f":"30000+($B27*8+F26-1)","v":30224}]
[null,28,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),4,1))","v":0},2,null,2,"0V","F新风机组NJ-5AP(KT)82-水阀反馈",{"$nulls":16},"NJ-5AP(KT)82",{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL27,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)82","05F01","水阀反馈","F新风机组-水阀反馈",{"$f":"VLOOKUP(AH27,[1]List!$D$3:$F$527,2,FALSE)&AJ27&\"_\"&VLOOKUP(AK27,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05F01_WVB"},{"$f":"_xlfn.IFNA(\"L\"&AM27&\" \"&\"AT%I\"&B27*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J27&\"*)\",\" \")","v":"LFAU05F01_WVB AT%I450.0 :INT; (*F新风机组NJ-5AP(KT)82-水阀反馈*)"},"LFAU05F01_WVB           AT%I450.0      :INT; (*F新风机组NJ-5AP(KT)82-水阀反馈*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM27","v":"L01\\L01FAU05F01_WVB"},"F新风机组NJ-5AP(KT)82-水阀反馈",{"$f":"AS26+1","v":30225}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),3,1))","v":1},3,null,3,"0V","F新风机组NJ-5AP(KT)82-变频器频率反馈",{"$nulls":16},"NJ-5AP(KT)82",{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL28,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)82","05F01","变频器频率反馈","F新风机组-变频器频率反馈",{"$f":"VLOOKUP(AH28,[1]List!$D$3:$F$527,2,FALSE)&AJ28&\"_\"&VLOOKUP(AK28,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05F01_VFB"},{"$f":"_xlfn.IFNA(\"L\"&AM28&\" \"&\"AT%I\"&B27*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J28&\"*)\",\" \")","v":"LFAU05F01_VFB AT%I452.0 :INT; (*F新风机组NJ-5AP(KT)82-变频器频率反馈*)"},"LFAU05F01_VFB           AT%I452.0      :INT; (*F新风机组NJ-5AP(KT)82-变频器频率反馈*)",null,{"$f":"$B$2&\"\\\"&$B$2&AM28","v":"L01\\L01FAU05F01_VFB"},"F新风机组NJ-5AP(KT)82-变频器频率反馈",30226]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),2,1))","v":1},4,null,4,"0V","-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL29,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH29,[1]List!$D$3:$F$527,2,FALSE)&AJ29&\"_\"&VLOOKUP(AK29,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM29&\" \"&\"AT%I\"&B27*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J29&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM29","v":{"$error":"#N/A"}},"-",30227]
[null,"IOM 0401U",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B27),REPT(0,5))),1,1))","v":1}]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),3,1))","v":0}]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),2,1))","v":1}]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B29=20,1,IF(B29=50,10,IF(B29=125,11,IF(B29=250,100,IF(B29=500,101,IF(B29=800,110,IF(B29=1000,111,0))))))),REPT(0,3))),1,1))","v":0}]
[null,{"$f":"B39","v":"IOM 0401A"},{"$nulls":38},{"$f":"\"(* \"&B39&\"地址: \"&B36&\" *)\"","v":"(* IOM 0401A地址: 29 *)"}]
[null,"addr",1,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),5,1))","v":1},1,null,1,2,{"$f":"AH35&AA35&\"-\"&AK35","v":"F新风机组NJ-5AP(KT)82-水阀控制"},{"$nulls":16},{"$f":"IF(AI35=\"\",\"\",AI35)","v":"NJ-5AP(KT)82"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL35,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)82","05F01","水阀控制",{"$f":"AH35&\"-\"&AK35","v":"F新风机组-水阀控制"},{"$f":"VLOOKUP(AH35,[1]List!$D$3:$F$527,2,FALSE)&AJ35&\"_\"&VLOOKUP(AK35,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05F01_WVC"},{"$f":"_xlfn.IFNA(\"L\"&AM35&\" \"&\"AT%Q\"&B36*16&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J35&\"*)\",\" \")","v":"LFAU05F01_WVC AT%Q464.0 :INT; (*F新风机组NJ-5AP(KT)82-水阀控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35))),SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN35,SEARCH(\"AT%\",AN35),,REPT(\" \",25-SEARCH(\"AT%\",AN35)))))),\" \")","v":"LFAU05F01_WVC           AT%Q464.0      :INT; (*F新风机组NJ-5AP(KT)82-水阀控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM35","v":"L01\\L01FAU05F01_WVC"},{"$f":"J35","v":"F新风机组NJ-5AP(KT)82-水阀控制"},{"$f":"40000+($B36*8+F35-1)","v":40232}]
[null,29,2,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),4,1))","v":0},2,null,3,4,"F新风机组NJ-5AP(KT)82-变频器频率控制",{"$nulls":16},"NJ-5AP(KT)82",{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL36,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":4},"F新风机组","NJ-5AP(KT)82","05F01","变频器频率控制","F新风机组-变频器频率控制",{"$f":"VLOOKUP(AH36,[1]List!$D$3:$F$527,2,FALSE)&AJ36&\"_\"&VLOOKUP(AK36,[1]List!$I$2:$K$529,2,FALSE)","v":"FAU05F01_VFC"},{"$f":"_xlfn.IFNA(\"L\"&AM36&\" \"&\"AT%Q\"&B36*16+2&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J36&\"*)\",\" \")","v":"LFAU05F01_VFC AT%Q466.0 :INT; (*F新风机组NJ-5AP(KT)82-变频器频率控制*)"},{"$f":"IFERROR(REPLACE(REPLACE(AN36,SEARCH(\"AT%\",AN36),,REPT(\" \",25-SEARCH(\"AT%\",AN36))),SEARCH(\":\",REPLACE(AN36,SEARCH(\"AT%\",AN36),,REPT(\" \",25-SEARCH(\"AT%\",AN36)))),,REPT(\" \",40-SEARCH(\":\",REPLACE(AN36,SEARCH(\"AT%\",AN36),,REPT(\" \",25-SEARCH(\"AT%\",AN36)))))),\" \")","v":"LFAU05F01_VFC           AT%Q466.0      :INT; (*F新风机组NJ-5AP(KT)82-变频器频率控制*)"},null,{"$f":"$B$2&\"\\\"&$B$2&AM36","v":"L01\\L01FAU05F01_VFC"},"F新风机组NJ-5AP(KT)82-变频器频率控制",{"$f":"AS35+1","v":40233}]
[null,"kbs",3,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),3,1))","v":1},3,null,5,6,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL37,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH37,[1]List!$D$3:$F$527,2,FALSE)&AJ37&\"_\"&VLOOKUP(AK37,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM37&\" \"&\"AT%Q\"&B36*16+4&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J37&\"*)\",\" \")","v":" "},{"$f":"IFERROR(REPLACE(REPLACE(AN37,SEARCH(\"AT%\",AN37),,REPT(\" \",30-SEARCH(\"AT%\",AN37))),SEARCH(\":\",REPLACE(AN37,SEARCH(\"AT%\",AN37),,REPT(\" \",30-SEARCH(\"AT%\",AN37)))),,REPT(\" \",35-SEARCH(\":\",REPLACE(AN37,SEARCH(\"AT%\",AN37),,REPT(\" \",25-SEARCH(\"AT%\",AN37)))))),\" \")","v":" "},null,{"$f":"$B$2&\"\\\"&$B$2&AM37","v":{"$error":"#N/A"}},"-",40234]
[null,50,4,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),2,1))","v":1},4,null,7,8,"-",{"$nulls":16},"",{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[1]List!$M$3:$N$526,2,FALSE),\"-\")","v":"-"},{"$f":"_xlfn.IFNA(VLOOKUP(AL38,[1]List!$M$3:$O$526,3,FALSE),\"-\")","v":"-"},{"$nulls":8},"-",{"$f":"VLOOKUP(AH38,[1]List!$D$3:$F$527,2,FALSE)&AJ38&\"_\"&VLOOKUP(AK38,[1]List!$I$2:$K$529,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"_xlfn.IFNA(\"L\"&AM38&\" \"&\"AT%Q\"&B36*16+6&\".0\"&\" \"&\":INT;\"&\" \"&\"(*\"&J38&\"*)\",\" \")","v":" "}," ",null,{"$f":"$B$2&\"\\\"&$B$2&AM38","v":{"$error":"#N/A"}},"-",40235]
[null,"IOM 0401A",5,{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(DEC2BIN(B36),REPT(0,5))),1,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[null,null,6,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),3,1))","v":0},0,null,0,0,{"$nulls":28},"-"]
[null,null,7,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),2,1))","v":1},0,null,0,0,{"$nulls":28},"-"]
[".",null,8,{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},{"$f":"BIN2DEC(MID((TEXT(IF(B38=20,1,IF(B38=50,10,IF(B38=125,11,IF(B38=250,100,IF(B38=500,101,IF(B38=800,110,IF(B38=1000,111,0))))))),REPT(0,3))),1,1))","v":0},0,null,0,0,{"$nulls":28},"-"]